## 표지
H1-20C 구조계산서
| ▣ 구조형식 |  | : | 지중 1 련 암거
( 내공 : 2.5M ⅹ 2.5M )
| ▣ 토 피(FH) |  | = | 8.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 절점부 검토
[5 empty] | 22. | 사용성 검토
[5 empty] | 23. | 기초 지지력 검토
[5 empty] | 24. | 주철근 조립도

## 설계요약표
1. 설계 요약표
H1-20C (토피=8.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 8.0m
안정(지지력)검토 | Qmax = 220.377 kN/m²
단면 위치 | 내구성검토 |  | 단 면 검 토 | [7 empty] | 절 점 부 보 강
| 균열검토 |  | 휨 검 토 |  |  |  | 전 단 검 토
| 철근간격 mm | 최대간격 mm | 사용철근 | Mu kN.m | ΦMn kN.m | S.F | 사용철근 | Vu kN | ΦVn kN | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 455.749 | H16 - 4.0EA + H13 - 4.0EA | 128.901 | 221.459 | 1.72 | ∴ 전단보강 불필요 |  |  | O.K | 0.671 | 0.637 | H19 @250 - 4EA
상부슬래브 : 중앙부 | 125 | 358.472 | H19 - 4.0EA + H16 - 4.0EA | 161.624 | 257.941 | 1.6 | ∴ 전단보강 불필요 |  |  | O.K
상부슬래브 : 단지점부(우측) | 125 | 455.749 | H16 - 4.0EA + H13 - 4.0EA | 128.901 | 221.459 | 1.72 | ∴ 전단보강 불필요 |  |  | O.K | 0.671 | 0.637 | H19 @250 - 4EA
하부슬래브 : 단지점부(좌측) | 125 | 484.041 | H16 - 8.0EA | 125.412 | 223.868 | 1.79 | ∴ 전단보강 불필요 |  |  | O.K | 1.054 | 0.637 | H19 @250 - 4EA
하부슬래브 : 중앙부 | 125 | 307.823 | H16 - 8.0EA | 145.545 | 213.064 | 1.46 | ∴ 전단보강 불필요 |  |  | O.K
하부슬래브 : 단지점부(우측) | 125 | 484.041 | H16 - 8.0EA | 125.412 | 223.868 | 1.79 | ∴ 전단보강 불필요 |  |  | O.K | 1.054 | 0.637 | H19 @250 - 4EA
좌측벽체 : 상부 | 125 | 272.886 | H16 - 4.0EA + H13 - 4.0EA | 128.901 | 262.076 | 2.03 | ∴ 전단보강 불필요 |  |  | O.K
좌측벽체 : 중앙부 | 250 | 488.844 | H19 - 4.0EA | 51.92 | 282.73 | 5.45 | ∴ 전단보강 불필요 |  |  | O.K
좌측벽체 : 중앙부(부모멘트) | 250 | 576.49 | H16 - 4.0EA | 35.136 | 281.33 | 8.01 | ∴ 전단보강 불필요 |  |  | O.K
좌측벽체 : 하부 | 125 | 254.89 | H16 - 8.0EA | 125.412 | 212.669 | 1.7 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 상부 | 125 | 272.886 | H16 - 4.0EA + H13 - 4.0EA | 128.901 | 262.076 | 2.03 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 중앙부 | 250 | 488.844 | H19 - 4.0EA | 51.92 | 282.73 | 5.45 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 중앙부(부모멘트) | 250 | 576.49 | H16 - 4.0EA | 35.136 | 281.33 | 8.01 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 하부 | 125 | 254.89 | H16 - 8.0EA | 125.412 | 212.669 | 1.7 | ∴ 전단보강 불필요 |  |  | O.K

## 설계조건
2. 설계조건
1) 구조형식
- 지중 1 련 암거 ( 내공 : 2.5M ⅹ 2.5M, 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 10 |  | kN/m² |  | (∵ 토피 : | 8 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.500 × 1.000 = 0.500 |  |  |  | 0.01042 |  | 1~9,15~20
| 2 | 0.350 × 1.000 = 0.350 |  |  |  | 0.00357 |  | 10~14,21~25
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.175 | 0.25 | 17 |  | 2.42 |  | 3.25
| 2 |  | 0.35 | 0.25 | 18 |  | 1.6 |  | 3.25
| 3 |  | 0.745 | 0.25 | 19 |  | 0.78 |  | 3.25
| 4 |  | 0.78 | 0.25 | 20 |  | 0.35 |  | 3.25
| 5 |  | 1.315 | 0.25 | 21 |  | 0.175 |  | 3.25
| 6 |  | 1.885 | 0.25 | 22 |  | 0.175 |  | 3
| 7 |  | 2.42 | 0.25 | 23 |  | 0.175 |  | 2.72
| 8 |  | 2.455 | 0.25 | 24 |  | 0.175 |  | 0.78
| 9 |  | 2.85 | 0.25 | 25 |  | 0.175 |  | 0.5
| 10 |  | 3.025 | 0.25 | 26 |  | 0.175 |  | -0.25
| 11 |  | 3.025 | 0.5 | 27 |  | 0.745 |  | -0.25
| 12 |  | 3.025 | 0.78 | 28 |  | 1.315 |  | -0.25
| 13 |  | 3.025 | 2.72 | 29 |  | 1.885 |  | -0.25
| 14 |  | 3.025 | 3 | 30 |  | 2.455 |  | -0.25
| 15 |  | 3.025 | 3.25 | 31 |  | 3.025 |  | -0.25
| 16 |  | 2.85 | 3.25

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.500 × 1.000 = 0.500 |  |  |  | 0.01042 |  | 1~9,20~28
| 2 | 0.350 × 1.000 = 0.350 |  |  |  | 0.00357 |  | 10~19,29~38
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.175 | 0.25 | 33 |  | 0.175 |  | 2.25
| 2 |  | 0.35 | 0.25 | 34 |  | 0.175 |  | 1.75
| 3 |  | 0.745 | 0.25 | 35 |  | 0.175 |  | 1.25
| 4 |  | 0.78 | 0.25 | 36 |  | 0.175 |  | 0.78
| 5 |  | 1.315 | 0.25 | 37 |  | 0.175 |  | 0.75
| 6 |  | 1.885 | 0.25 | 38 |  | 0.175 |  | 0.5
| 7 |  | 2.42 | 0.25 | 39 |  | 0.175 |  | -0.25
| 8 |  | 2.455 | 0.25 | 40 |  | 0.745 |  | -0.25
| 9 |  | 2.85 | 0.25 | 41 |  | 1.315 |  | -0.25
| 10 |  | 3.025 | 0.25 | 42 |  | 1.885 |  | -0.25
| 11 |  | 3.025 | 0.5 | 43 |  | 2.455 |  | -0.25
| 12 |  | 3.025 | 0.75 | 44 |  | 3.025 |  | -0.25
| 13 |  | 3.025 | 0.78 | 45 |  | 3.525 |  | 0.25
| 14 |  | 3.025 | 1.25 | 46 |  | 3.525 |  | 0.75
| 15 |  | 3.025 | 1.75 | 47 |  | 3.525 |  | 1.25
| 16 |  | 3.025 | 2.25 | 48 |  | 3.525 |  | 1.75
| 17 |  | 3.025 | 2.72 | 49 |  | 3.525 |  | 2.25
| 18 |  | 3.025 | 2.75 | 50 |  | 3.525 |  | 2.75
| 19 |  | 3.025 | 3 | 51 |  | 3.525 |  | 3.25
| 20 |  | 3.025 | 3.25 | 52 |  | 3.025 |  | 3.75
| 21 |  | 2.85 | 3.25 | 53 |  | 2.455 |  | 3.75
| 22 |  | 2.455 | 3.25 | 54 |  | 1.885 |  | 3.75
| 23 |  | 2.42 | 3.25 | 55 |  | 1.315 |  | 3.75
| 24 |  | 1.885 | 3.25 | 56 |  | 0.745 |  | 3.75
| 25 |  | 1.315 | 3.25 | 57 |  | 0.175 |  | 3.75
| 26 |  | 0.78 | 3.25 | 58 |  | -0.325 |  | 3.25
| 27 |  | 0.745 | 3.25 | 59 |  | -0.325 |  | 2.75
| 28 |  | 0.35 | 3.25 | 60 |  | -0.325 |  | 2.25
| 29 |  | 0.175 | 3.25 | 61 |  | -0.325 |  | 1.75
| 30 |  | 0.175 | 3 | 62 |  | -0.325 |  | 1.25
| 31 |  | 0.175 | 2.75 | 63 |  | -0.325 |  | 0.75
| 32 |  | 0.175 | 2.72 | 64 |  | -0.325 |  | 0.25

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 3.200 × 3.200 ) |  |  | = | 3.2 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 3.200 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 23719.553 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.350/2 + 0.570/2) = 10911 kN/m |  |  |  |  | 1,10
| Kv2 |  |  | Kvⅹ(0.570/2 + 0.570/2) = 13520 kN/m |  |  |  |  | 3,5~6,8
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 3.000m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 3.200 × 3.200 ) |  |  |  |  | = | 3.2 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 3.200 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 59672.07 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 59672.070 |  |  |  |  | = | 19890.69 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 3.200 × 3.200 ) |  |  |  |  | = | 3.2 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 3.200 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 59672.07 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 59672.070 |  |  |  |  | = | 19890.69 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 3.500 × 3.500 ) |  |  |  |  | = | 3.5 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 3.500 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 55793.36 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 55793.360 |  |  |  |  | = | 18597.79 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.570/2 + 0.350/2) = 27449 kN/m | [8 empty] | 20,29
|  | Ksb1 |  |  | Ksbⅹ(0.570/2 + 0.350/2) = 9150 kN/m
|  | Kv2 |  |  | Kvⅹ(0.570/2 + 0.570/2) = 34013 kN/m | [8 empty] | 22,24~25,27
|  | Ksb2 |  |  | Ksbⅹ(0.570/2 + 0.570/2) = 11338 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(0.500/2 + 0.500/2) = 27897 kN/m | [8 empty] | 1,10,12,14~16,18,20,29,31,33~35,37
|  | Kss1 |  |  | Kssⅹ(0.500/2 + 0.500/2) = 9299 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.350/2 + 0.570/2) = 27449 kN/m | [8 empty] | 1,10
|  | Ksb1 |  |  | Ksbⅹ(0.350/2 + 0.570/2) = 9150 kN/m
|  | Kv2 |  |  | Kvⅹ(0.570/2 + 0.570/2) = 34013 kN/m | [8 empty] | 3,5~6,8
|  | Ksb2 |  |  | Ksbⅹ(0.570/2 + 0.570/2) = 11338 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 8.00 × 19.00 |  |  |  |  | = | 152 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 152 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 상부 슬래브에 작용하는 하중 (Wl1) - 토피 4m 이상
|  |  | - Wl1 |  | = | 10.000 kN/m²
② 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (8.250 × 19.000) × 0.500 | [9 empty] | = | 78.375 | kN/m²
|  | - Wh2 |  | = | 78.375 + 0.250 × 19.000 × 0.500 | [9 empty] | = | 80.75 | kN/m²
|  | - Wh3 |  | = | 80.750 + 0.280 × 19.000 × 0.500 | [9 empty] | = | 83.41 | kN/m²
|  | - Wh4 |  | = | 83.410 + 1.940 × 19.000 × 0.500 | [9 empty] | = | 101.84 | kN/m²
|  | - Wh5 |  | = | 101.840 + 0.280 × 19.000 × 0.500 | [9 empty] | = | 104.5 | kN/m²
|  | - Wh6 |  | = | 104.500 + 0.250 × 19.000 × 0.500 | [9 empty] | = | 106.875 | kN/m²
5) 암거내부수압
- Win = 20.000 kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 11 |  | 197.3 |  |  |  | 19 |  |  | 0.223
|  | 계 | [11 empty] | 0.223
Tg = 1.25 Tg' = 1.25 × 0.223 = 0.279 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.279 / 2π × 2.617 = 0.116 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 8.25 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 11.25 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.116 × 0.279 × cos(π× 8.250 / (2 × 30.000)) = 0.005956
U(Zb) = 2 / π²× 0.116 × 0.279 × cos(π× 11.250 / (2 × 30.000)) = 0.005453
Po = Ksb,top × (U(Zu) - U(Zb))
= 19890.690 × (0.005956 - 0.005453) = 10.005 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 8.25 |  | 55793.36 |  |  |  | 0.005956 |  |  |  |  | 0.000503 |  | 28.064
|  | 8.5 |  | 55793.36 |  |  |  | 0.005919 |  |  |  |  | 0.000466 |  | 26
|  | 8.75 |  | 55793.36 |  |  |  | 0.005882 |  |  |  |  | 0.000429 |  | 23.935
|  | 8.78 |  | 55793.36 |  |  |  | 0.005877 |  |  |  |  | 0.000424 |  | 23.656
|  | 9.25 |  | 55793.36 |  |  |  | 0.005804 |  |  |  |  | 0.000351 |  | 19.584
|  | 9.75 |  | 55793.36 |  |  |  | 0.005722 |  |  |  |  | 0.000269 |  | 15.008
|  | 10.25 |  | 55793.36 |  |  |  | 0.005636 |  |  |  |  | 0.000183 |  | 10.21
|  | 10.72 |  | 55793.36 |  |  |  | 0.005552 |  |  |  |  | 9.9e-05 |  | 5.524
|  | 10.75 |  | 55793.36 |  |  |  | 0.005547 |  |  |  |  | 9.4e-05 |  | 5.245
|  | 11 |  | 55793.36 |  |  |  | 0.0055 |  |  |  |  | 4.7e-05 |  | 2.622
|  | 11.25 |  | 55793.36 |  |  |  | 0.005453 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000144 = 2.720 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000191 = 3.600 kN/m²
Vs = (Vu - Vb) / 2 = (2.720 + 3.600) / 2 = 3.160 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.500 × 24.500 × 0.160 × (1 - 0.015 × 8.250) = 1.717 kN/m²
② 하부슬래브
fb = 0.500 × 24.500 × 0.160 × (1 - 0.015 × 11.250) = 1.629 kN/m²
③ 측벽
f1 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 8.250) = 1.202 kN/m²
f2 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 8.500) = 1.197 kN/m²
f3 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 8.750) = 1.192 kN/m²
f4 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 8.780) = 1.191 kN/m²
f5 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 9.250) = 1.182 kN/m²
f6 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 9.750) = 1.171 kN/m²
f7 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 10.250) = 1.161 kN/m²
f8 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 10.720) = 1.151 kN/m²
f9 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 10.750) = 1.151 kN/m²
f10 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 11.000) = 1.146 kN/m²
f11 = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 11.250) = 1.140 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)
6) CASE6 - 암거내부수압

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 0.875, h = 8.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
2) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1
| 2 |  | 1 | 0.875 |  | 1 | 1
| 3 |  | 1 | 0.875 | 1 | 0.5 | 0.5
3) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | 22 J= 22, 23 SEC=2 NSEG=1 ANG=180
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 23 J= 23, 24 SEC=2 NSEG=4 ANG=180
24 J= 24, 25 SEC=2 NSEG=1 ANG=180
| JOINT | 25 J= 25, 1 SEC=2 NSEG=1 ANG=180
1 X= 0.175 Y= 0.000 Z= 0.250
| 2 X= 0.350 Y= 0.000 Z= 0.250 | NLLINK
| 3 X= 0.745 Y= 0.000 Z= 0.250 | 1 J=1,26 NLP=SP1 ANG=0
| 4 X= 0.780 Y= 0.000 Z= 0.250 | 2 J=3,27 NLP=SP2 ANG=0
| 5 X= 1.315 Y= 0.000 Z= 0.250 | 3 J=5,28 NLP=SP2 ANG=0
| 6 X= 1.885 Y= 0.000 Z= 0.250 | 4 J=6,29 NLP=SP2 ANG=0
| 7 X= 2.420 Y= 0.000 Z= 0.250 | 5 J=8,30 NLP=SP2 ANG=0
| 8 X= 2.455 Y= 0.000 Z= 0.250 | 6 J=10,31 NLP=SP1 ANG=0
9 X= 2.850 Y= 0.000 Z= 0.250
| 10 X= 3.025 Y= 0.000 Z= 0.250 | LOAD
| 11 X= 3.025 Y= 0.000 Z= 0.500 | NAME=SELFWGT SW=1
| 12 X= 3.025 Y= 0.000 Z= 0.780 | NAME=NWDEAD
| 13 X= 3.025 Y= 0.000 Z= 2.720 | TYPE=Distributed Span
| 14 X= 3.025 Y= 0.000 Z= 3.000 | ADD=15 RD=0,1 UZ=-152,-152
| 15 X= 3.025 Y= 0.000 Z= 3.250 | ADD=16 RD=0,1 UZ=-152,-152
| 16 X= 2.850 Y= 0.000 Z= 3.250 | ADD=17 RD=0,1 UZ=-152,-152
| 17 X= 2.420 Y= 0.000 Z= 3.250 | ADD=18 RD=0,1 UZ=-152,-152
| 18 X= 1.600 Y= 0.000 Z= 3.250 | ADD=19 RD=0,1 UZ=-152,-152
| 19 X= 0.780 Y= 0.000 Z= 3.250 | ADD=20 RD=0,1 UZ=-152,-152
| 20 X= 0.350 Y= 0.000 Z= 3.250 | NAME=LIVEFULL
| 21 X= 0.175 Y= 0.000 Z= 3.250 | TYPE=Distributed Span
| 22 X= 0.175 Y= 0.000 Z= 3.000 | ADD=15 RD=0,1 UZ=-10,-10
| 23 X= 0.175 Y= 0.000 Z= 2.720 | ADD=16 RD=0,1 UZ=-10,-10
| 24 X= 0.175 Y= 0.000 Z= 0.780 | ADD=17 RD=0,1 UZ=-10,-10
| 25 X= 0.175 Y= 0.000 Z= 0.500 | ADD=18 RD=0,1 UZ=-10,-10
| 26 X= 0.175 Y= 0.000 Z= -0.250 | ADD=19 RD=0,1 UZ=-10,-10
| 27 X= 0.745 Y= 0.000 Z= -0.250 | ADD=20 RD=0,1 UZ=-10,-10
| 28 X= 1.315 Y= 0.000 Z= -0.250 | NAME=HORLIVE
| 29 X= 1.885 Y= 0.000 Z= -0.250 | TYPE=Distributed Span
| 30 X= 2.455 Y= 0.000 Z= -0.250 | ADD=10 RD=0,1 UX=-5,-5
| 31 X= 3.025 Y= 0.000 Z= -0.250 | ADD=11 RD=0,1 UX=-5,-5
ADD=12 RD=0,1 UX=-5,-5
| RESTRAINT | ADD=13 RD=0,1 UX=-5,-5
| ADD=26 DOF=U1, U2, U3, R1, R2, R3 | ADD=14 RD=0,1 UX=-5,-5
| ADD=27 DOF=U1, U2, U3, R1, R2, R3 | ADD=21 RD=0,1 UX=5,5
| ADD=28 DOF=U1, U2, U3, R1, R2, R3 | ADD=22 RD=0,1 UX=5,5
| ADD=29 DOF=U1, U2, U3, R1, R2, R3 | ADD=23 RD=0,1 UX=5,5
| ADD=30 DOF=U1, U2, U3, R1, R2, R3 | ADD=24 RD=0,1 UX=5,5
| ADD=31 DOF=U1, U2, U3, R1, R2, R3 | ADD=25 RD=0,1 UX=5,5
NAME=NWSOFULL
| SPRING | TYPE=Distributed Span
| ADD=1 U1=1e+010 | ADD=10 RD=0,1 UX=-106.875,-104.5
ADD=11 RD=0,1 UX=-104.5,-101.84
| MATERIAL | ADD=12 RD=0,1 UX=-101.84,-83.41
| NAME=CONC IDES=C M=0.0001 W=24.5 | ADD=13 RD=0,1 UX=-83.41,-80.75
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | ADD=14 RD=0,1 UX=-80.75,-78.375
ADD=21 RD=0,1 UX=78.375,80.75
| NLPROP | ADD=22 RD=0,1 UX=80.75,83.41
| NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=23 RD=0,1 UX=83.41,101.84
| DOF=U1 KE=10911 CE=0.99999 K=10911 OPEN=0 | ADD=24 RD=0,1 UX=101.84,104.5
| NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=25 RD=0,1 UX=104.5,106.875
| DOF=U1 KE=13520.1 CE=0.99999 K=13520.1 OPEN=0 | NAME=INWATER
TYPE=Distributed Span
| FRAME SECTION | ADD=2 RD=0,1 UZ=-20,-20
| NAME=1 MAT=CONC SH=R T=0.5, 1 | ADD=3 RD=0,1 UZ=-20,-20
| NAME=2 MAT=CONC SH=R T=0.35, 1 | ADD=4 RD=0,1 UZ=-20,-20
ADD=5 RD=0,1 UZ=-20,-20
| FRAME | ADD=6 RD=0,1 UZ=-20,-20
| 1 J= 1, 2 SEC=1 NSEG=1 ANG=180 | ADD=7 RD=0,1 UZ=-20,-20
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | ADD=8 RD=0,1 UZ=-20,-20
3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 4 J= 4, 5 SEC=1 NSEG=2 ANG=180 | MODE
| 5 J= 5, 6 SEC=1 NSEG=2 ANG=180 | TYPE=RITZ N=50
| 6 J= 6, 7 SEC=1 NSEG=2 ANG=180 | LOAD=SELFWGT
| 7 J= 7, 8 SEC=1 NSEG=1 ANG=180 | LOAD=NWDEAD
| 8 J= 8, 9 SEC=1 NSEG=1 ANG=180 | LOAD=LIVEFULL
| 9 J= 9, 10 SEC=1 NSEG=1 ANG=180 | LOAD=HORLIVE
| 10 J= 10, 11 SEC=2 NSEG=1 ANG=0 | LOAD=NWSOFULL
| 11 J= 11, 12 SEC=2 NSEG=1 ANG=0 | LOAD=INWATER
| 12 J= 12, 13 SEC=2 NSEG=4 ANG=0 | NLLINK=*
13 J= 13, 14 SEC=2 NSEG=1 ANG=0
| 14 J= 14, 15 SEC=2 NSEG=1 ANG=0 | HISTORY
| 15 J= 15, 16 SEC=1 NSEG=1 ANG=0 | NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| 16 J= 16, 17 SEC=1 NSEG=1 ANG=0 | LOAD=SELFWGT SF=1.2 AT=1
| 17 J= 17, 18 SEC=1 NSEG=2 ANG=0 | LOAD=NWDEAD SF=1.4 AT=1
| 18 J= 18, 19 SEC=1 NSEG=2 ANG=0 | LOAD=LIVEFULL SF=1.6 AT=1
| 19 J= 19, 20 SEC=1 NSEG=1 ANG=0 | LOAD=HORLIVE SF=1.6 AT=1
| 20 J= 20, 21 SEC=1 NSEG=1 ANG=0 | LOAD=NWSOFULL SF=1.6 AT=1
| 21 J= 21, 22 SEC=2 NSEG=1 ANG=180 | NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
LOAD=INWATER SF=1 AT=1
NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
LOAD=INWATER SF=1 AT=1
NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=0.5 AT=1
LOAD=NWSOFULL SF=0.5 AT=1
LOAD=INWATER SF=1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
HIST=HIST3 SF=1
NAME=SERVICE TYPE=ENVE
HIST=HIST4 SF=1
HIST=HIST5 SF=1
HIST=HIST6 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | ADD=52 DOF=U1, U2, U3, R1, R2, R3
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | ADD=53 DOF=U1, U2, U3, R1, R2, R3
ADD=54 DOF=U1, U2, U3, R1, R2, R3
| JOINT | ADD=55 DOF=U1, U2, U3, R1, R2, R3
| 1 X= 0.175 Y= 0.000 Z= 0.250 | ADD=56 DOF=U1, U2, U3, R1, R2, R3
| 2 X= 0.350 Y= 0.000 Z= 0.250 | ADD=57 DOF=U1, U2, U3, R1, R2, R3
| 3 X= 0.745 Y= 0.000 Z= 0.250 | ADD=58 DOF=U1, U2, U3, R1, R2, R3
| 4 X= 0.780 Y= 0.000 Z= 0.250 | ADD=59 DOF=U1, U2, U3, R1, R2, R3
| 5 X= 1.315 Y= 0.000 Z= 0.250 | ADD=60 DOF=U1, U2, U3, R1, R2, R3
| 6 X= 1.885 Y= 0.000 Z= 0.250 | ADD=61 DOF=U1, U2, U3, R1, R2, R3
| 7 X= 2.420 Y= 0.000 Z= 0.250 | ADD=62 DOF=U1, U2, U3, R1, R2, R3
| 8 X= 2.455 Y= 0.000 Z= 0.250 | ADD=63 DOF=U1, U2, U3, R1, R2, R3
| 9 X= 2.850 Y= 0.000 Z= 0.250 | ADD=64 DOF=U1, U2, U3, R1, R2, R3
10 X= 3.025 Y= 0.000 Z= 0.250
| 11 X= 3.025 Y= 0.000 Z= 0.500 | SPRING
| 12 X= 3.025 Y= 0.000 Z= 0.750 | ADD=1 U1=9149.72 U3=9298.9
| 13 X= 3.025 Y= 0.000 Z= 0.780 | ADD=3 U1=11337.7
| 14 X= 3.025 Y= 0.000 Z= 1.250 | ADD=5 U1=11337.7
| 15 X= 3.025 Y= 0.000 Z= 1.750 | ADD=6 U1=11337.7
| 16 X= 3.025 Y= 0.000 Z= 2.250 | ADD=8 U1=11337.7
| 17 X= 3.025 Y= 0.000 Z= 2.720 | ADD=10 U1=9149.72 U3=9298.9
| 18 X= 3.025 Y= 0.000 Z= 2.750 | ADD=12 U3=9298.9
| 19 X= 3.025 Y= 0.000 Z= 3.000 | ADD=14 U3=9298.9
| 20 X= 3.025 Y= 0.000 Z= 3.250 | ADD=15 U3=9298.9
| 21 X= 2.850 Y= 0.000 Z= 3.250 | ADD=16 U3=9298.9
| 22 X= 2.455 Y= 0.000 Z= 3.250 | ADD=18 U3=9298.9
| 23 X= 2.420 Y= 0.000 Z= 3.250 | ADD=20 U1=9149.72 U3=9298.9
| 24 X= 1.885 Y= 0.000 Z= 3.250 | ADD=22 U1=11337.7
| 25 X= 1.315 Y= 0.000 Z= 3.250 | ADD=24 U1=11337.7
| 26 X= 0.780 Y= 0.000 Z= 3.250 | ADD=25 U1=11337.7
| 27 X= 0.745 Y= 0.000 Z= 3.250 | ADD=27 U1=11337.7
| 28 X= 0.350 Y= 0.000 Z= 3.250 | ADD=29 U1=9149.72 U3=9298.9
| 29 X= 0.175 Y= 0.000 Z= 3.250 | ADD=31 U3=9298.9
| 30 X= 0.175 Y= 0.000 Z= 3.000 | ADD=33 U3=9298.9
| 31 X= 0.175 Y= 0.000 Z= 2.750 | ADD=34 U3=9298.9
| 32 X= 0.175 Y= 0.000 Z= 2.720 | ADD=35 U3=9298.9
| 33 X= 0.175 Y= 0.000 Z= 2.250 | ADD=37 U3=9298.9
34 X= 0.175 Y= 0.000 Z= 1.750
| 35 X= 0.175 Y= 0.000 Z= 1.250 | MATERIAL
| 36 X= 0.175 Y= 0.000 Z= 0.780 | NAME=CONC IDES=C M=0.0001 W=24.5
| 37 X= 0.175 Y= 0.000 Z= 0.750 | T=0 E=2.7e+007 U=0.17 A=9.99e-006
38 X= 0.175 Y= 0.000 Z= 0.500
| 39 X= 0.175 Y= 0.000 Z= -0.250 | NLPROP
| 40 X= 0.745 Y= 0.000 Z= -0.250 | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 41 X= 1.315 Y= 0.000 Z= -0.250 | DOF=U1 KE=27449.2 CE=0.99999 K=27449.2 OPEN=0
| 42 X= 1.885 Y= 0.000 Z= -0.250 | NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 43 X= 2.455 Y= 0.000 Z= -0.250 | DOF=U1 KE=34013.1 CE=0.99999 K=34013.1 OPEN=0
| 44 X= 3.025 Y= 0.000 Z= -0.250 | NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 45 X= 3.525 Y= 0.000 Z= 0.250 | DOF=U1 KE=27896.7 CE=0.99999 K=27896.7 OPEN=0
46 X= 3.525 Y= 0.000 Z= 0.750
| 47 X= 3.525 Y= 0.000 Z= 1.250 | FRAME SECTION
| 48 X= 3.525 Y= 0.000 Z= 1.750 | NAME=1 MAT=CONC SH=R T=0.5, 1
| 49 X= 3.525 Y= 0.000 Z= 2.250 | NAME=2 MAT=CONC SH=R T=0.35, 1
50 X= 3.525 Y= 0.000 Z= 2.750
| 51 X= 3.525 Y= 0.000 Z= 3.250 | FRAME
| 52 X= 3.025 Y= 0.000 Z= 3.750 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 53 X= 2.455 Y= 0.000 Z= 3.750 | 2 J= 2, 3 SEC=1 NSEG=1 ANG=180
| 54 X= 1.885 Y= 0.000 Z= 3.750 | 3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 55 X= 1.315 Y= 0.000 Z= 3.750 | 4 J= 4, 5 SEC=1 NSEG=2 ANG=180
| 56 X= 0.745 Y= 0.000 Z= 3.750 | 5 J= 5, 6 SEC=1 NSEG=2 ANG=180
| 57 X= 0.175 Y= 0.000 Z= 3.750 | 6 J= 6, 7 SEC=1 NSEG=2 ANG=180
| 58 X= -0.325 Y= 0.000 Z= 3.250 | 7 J= 7, 8 SEC=1 NSEG=1 ANG=180
| 59 X= -0.325 Y= 0.000 Z= 2.750 | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| 60 X= -0.325 Y= 0.000 Z= 2.250 | 9 J= 9, 10 SEC=1 NSEG=1 ANG=180
| 61 X= -0.325 Y= 0.000 Z= 1.750 | 10 J= 10, 11 SEC=2 NSEG=1 ANG=0
| 62 X= -0.325 Y= 0.000 Z= 1.250 | 11 J= 11, 12 SEC=2 NSEG=1 ANG=0
| 63 X= -0.325 Y= 0.000 Z= 0.750 | 12 J= 12, 13 SEC=2 NSEG=1 ANG=0
| 64 X= -0.325 Y= 0.000 Z= 0.250 | 13 J= 13, 14 SEC=2 NSEG=1 ANG=0
14 J= 14, 15 SEC=2 NSEG=1 ANG=0
| RESTRAINT | 15 J= 15, 16 SEC=2 NSEG=1 ANG=0
| ADD=39 DOF=U1, U2, U3, R1, R2, R3 | 16 J= 16, 17 SEC=2 NSEG=1 ANG=0
| ADD=40 DOF=U1, U2, U3, R1, R2, R3 | 17 J= 17, 18 SEC=2 NSEG=1 ANG=0
| ADD=41 DOF=U1, U2, U3, R1, R2, R3 | 18 J= 18, 19 SEC=2 NSEG=1 ANG=0
| ADD=42 DOF=U1, U2, U3, R1, R2, R3 | 19 J= 19, 20 SEC=2 NSEG=1 ANG=0
| ADD=43 DOF=U1, U2, U3, R1, R2, R3 | 20 J= 20, 21 SEC=1 NSEG=1 ANG=0
| ADD=44 DOF=U1, U2, U3, R1, R2, R3 | 21 J= 21, 22 SEC=1 NSEG=1 ANG=0
| ADD=45 DOF=U1, U2, U3, R1, R2, R3 | 22 J= 22, 23 SEC=1 NSEG=1 ANG=0
| ADD=46 DOF=U1, U2, U3, R1, R2, R3 | 23 J= 23, 24 SEC=1 NSEG=2 ANG=0
| ADD=47 DOF=U1, U2, U3, R1, R2, R3 | 24 J= 24, 25 SEC=1 NSEG=2 ANG=0
| ADD=48 DOF=U1, U2, U3, R1, R2, R3 | 25 J= 25, 26 SEC=1 NSEG=2 ANG=0
| ADD=49 DOF=U1, U2, U3, R1, R2, R3 | 26 J= 26, 27 SEC=1 NSEG=1 ANG=0
| ADD=50 DOF=U1, U2, U3, R1, R2, R3 | 27 J= 27, 28 SEC=1 NSEG=1 ANG=0
| ADD=51 DOF=U1, U2, U3, R1, R2, R3 | 28 J= 28, 29 SEC=1 NSEG=1 ANG=0
| 29 J= 29, 30 SEC=2 NSEG=1 ANG=180 | ADD=29 RD=0,1 UX=28.0641,25.9997
| 30 J= 30, 31 SEC=2 NSEG=1 ANG=180 | ADD=30 RD=0,1 UX=25.9997,23.9354
| 31 J= 31, 32 SEC=2 NSEG=1 ANG=180 | ADD=31 RD=0,1 UX=23.9354,23.6564
| 32 J= 32, 33 SEC=2 NSEG=1 ANG=180 | ADD=32 RD=0,1 UX=23.6564,19.5835
| 33 J= 33, 34 SEC=2 NSEG=1 ANG=180 | ADD=33 RD=0,1 UX=19.5835,15.0084
| 34 J= 34, 35 SEC=2 NSEG=1 ANG=180 | ADD=34 RD=0,1 UX=15.0084,10.2102
| 35 J= 35, 36 SEC=2 NSEG=1 ANG=180 | ADD=35 RD=0,1 UX=10.2102,5.5235
| 36 J= 36, 37 SEC=2 NSEG=1 ANG=180 | ADD=36 RD=0,1 UX=5.5235,5.2446
| 37 J= 37, 38 SEC=2 NSEG=1 ANG=180 | ADD=37 RD=0,1 UX=5.2446,2.6223
| 38 J= 38, 1 SEC=2 NSEG=1 ANG=180 | ADD=38 RD=0,1 UX=2.6223,0
NAME=SEPRINSH
| NLLINK | TYPE=Distributed Span
| 1 J=1,39 NLP=SP1 ANG=0 | ADD=1 RD=0,1 UX=-3.6,-3.6
| 2 J=3,40 NLP=SP2 ANG=0 | ADD=2 RD=0,1 UX=-3.6,-3.6
| 3 J=5,41 NLP=SP2 ANG=0 | ADD=3 RD=0,1 UX=-3.6,-3.6
| 4 J=6,42 NLP=SP2 ANG=0 | ADD=4 RD=0,1 UX=-3.6,-3.6
| 5 J=8,43 NLP=SP2 ANG=0 | ADD=5 RD=0,1 UX=-3.6,-3.6
| 6 J=10,44 NLP=SP1 ANG=0 | ADD=6 RD=0,1 UX=-3.6,-3.6
| 7 J=10,45 NLP=SP3 ANG=180 | ADD=7 RD=0,1 UX=-3.6,-3.6
| 8 J=12,46 NLP=SP3 ANG=180 | ADD=8 RD=0,1 UX=-3.6,-3.6
| 9 J=14,47 NLP=SP3 ANG=180 | ADD=9 RD=0,1 UX=-3.6,-3.6
| 10 J=15,48 NLP=SP3 ANG=180 | ADD=10 RD=0,1 UZ=3.16,3.16
| 11 J=16,49 NLP=SP3 ANG=180 | ADD=11 RD=0,1 UZ=3.16,3.16
| 12 J=18,50 NLP=SP3 ANG=180 | ADD=12 RD=0,1 UZ=3.16,3.16
| 13 J=20,51 NLP=SP3 ANG=180 | ADD=13 RD=0,1 UZ=3.16,3.16
| 14 J=20,52 NLP=SP1 ANG=0 | ADD=14 RD=0,1 UZ=3.16,3.16
| 15 J=22,53 NLP=SP2 ANG=0 | ADD=15 RD=0,1 UZ=3.16,3.16
| 16 J=24,54 NLP=SP2 ANG=0 | ADD=16 RD=0,1 UZ=3.16,3.16
| 17 J=25,55 NLP=SP2 ANG=0 | ADD=17 RD=0,1 UZ=3.16,3.16
| 18 J=27,56 NLP=SP2 ANG=0 | ADD=18 RD=0,1 UZ=3.16,3.16
| 19 J=29,57 NLP=SP1 ANG=0 | ADD=19 RD=0,1 UZ=3.16,3.16
| 20 J=29,58 NLP=SP3 ANG=180 | ADD=20 RD=0,1 UX=2.72,2.72
| 21 J=31,59 NLP=SP3 ANG=180 | ADD=21 RD=0,1 UX=2.72,2.72
| 22 J=33,60 NLP=SP3 ANG=180 | ADD=22 RD=0,1 UX=2.72,2.72
| 23 J=34,61 NLP=SP3 ANG=180 | ADD=23 RD=0,1 UX=2.72,2.72
| 24 J=35,62 NLP=SP3 ANG=180 | ADD=24 RD=0,1 UX=2.72,2.72
| 25 J=37,63 NLP=SP3 ANG=180 | ADD=25 RD=0,1 UX=2.72,2.72
| 26 J=1,64 NLP=SP3 ANG=180 | ADD=26 RD=0,1 UX=2.72,2.72
ADD=27 RD=0,1 UX=2.72,2.72
| LOAD | ADD=28 RD=0,1 UX=2.72,2.72
| NAME=SELFWGT SW=1 | ADD=29 RD=0,1 UZ=-3.16,-3.16
| NAME=NWDEAD | ADD=30 RD=0,1 UZ=-3.16,-3.16
| TYPE=Distributed Span | ADD=31 RD=0,1 UZ=-3.16,-3.16
| ADD=20 RD=0,1 UZ=-152,-152 | ADD=32 RD=0,1 UZ=-3.16,-3.16
| ADD=21 RD=0,1 UZ=-152,-152 | ADD=33 RD=0,1 UZ=-3.16,-3.16
| ADD=22 RD=0,1 UZ=-152,-152 | ADD=34 RD=0,1 UZ=-3.16,-3.16
| ADD=23 RD=0,1 UZ=-152,-152 | ADD=35 RD=0,1 UZ=-3.16,-3.16
| ADD=24 RD=0,1 UZ=-152,-152 | ADD=36 RD=0,1 UZ=-3.16,-3.16
| ADD=25 RD=0,1 UZ=-152,-152 | ADD=37 RD=0,1 UZ=-3.16,-3.16
| ADD=26 RD=0,1 UZ=-152,-152 | ADD=38 RD=0,1 UZ=-3.16,-3.16
| ADD=27 RD=0,1 UZ=-152,-152 | NAME=SEINER
| ADD=28 RD=0,1 UZ=-152,-152 | TYPE=Distributed Span
| NAME=LIVEFULL | ADD=1 RD=0,1 UX=1.62925,1.62925
| TYPE=Distributed Span | ADD=2 RD=0,1 UX=1.62925,1.62925
| ADD=20 RD=0,1 UZ=-10,-10 | ADD=3 RD=0,1 UX=1.62925,1.62925
| ADD=21 RD=0,1 UZ=-10,-10 | ADD=4 RD=0,1 UX=1.62925,1.62925
| ADD=22 RD=0,1 UZ=-10,-10 | ADD=5 RD=0,1 UX=1.62925,1.62925
| ADD=23 RD=0,1 UZ=-10,-10 | ADD=6 RD=0,1 UX=1.62925,1.62925
| ADD=24 RD=0,1 UZ=-10,-10 | ADD=7 RD=0,1 UX=1.62925,1.62925
| ADD=25 RD=0,1 UZ=-10,-10 | ADD=8 RD=0,1 UX=1.62925,1.62925
| ADD=26 RD=0,1 UZ=-10,-10 | ADD=9 RD=0,1 UX=1.62925,1.62925
| ADD=27 RD=0,1 UZ=-10,-10 | ADD=10 RD=0,1 UX=1.14048,1.14562
| ADD=28 RD=0,1 UZ=-10,-10 | ADD=11 RD=0,1 UX=1.14562,1.15077
| NAME=SEUPSLAB | ADD=12 RD=0,1 UX=1.15077,1.15138
| TYPE=Distributed Span | ADD=13 RD=0,1 UX=1.15138,1.16105
| ADD=20 RD=0,1 UX=10.005,10.005 | ADD=14 RD=0,1 UX=1.16105,1.17135
| ADD=21 RD=0,1 UX=10.005,10.005 | ADD=15 RD=0,1 UX=1.17135,1.18164
| ADD=22 RD=0,1 UX=10.005,10.005 | ADD=16 RD=0,1 UX=1.18164,1.19131
| ADD=23 RD=0,1 UX=10.005,10.005 | ADD=17 RD=0,1 UX=1.19131,1.19193
| ADD=24 RD=0,1 UX=10.005,10.005 | ADD=18 RD=0,1 UX=1.19193,1.19707
| ADD=25 RD=0,1 UX=10.005,10.005 | ADD=19 RD=0,1 UX=1.19707,1.20222
| ADD=26 RD=0,1 UX=10.005,10.005 | ADD=20 RD=0,1 UX=1.71745,1.71745
| ADD=27 RD=0,1 UX=10.005,10.005 | ADD=21 RD=0,1 UX=1.71745,1.71745
| ADD=28 RD=0,1 UX=10.005,10.005 | ADD=22 RD=0,1 UX=1.71745,1.71745
| NAME=SEWALL | ADD=23 RD=0,1 UX=1.71745,1.71745
| TYPE=Distributed Span | ADD=24 RD=0,1 UX=1.71745,1.71745
| ADD=10 RD=0,1 UX=0,2.6223 | ADD=25 RD=0,1 UX=1.71745,1.71745
| ADD=11 RD=0,1 UX=2.6223,5.2446 | ADD=26 RD=0,1 UX=1.71745,1.71745
| ADD=12 RD=0,1 UX=5.2446,5.5235 | ADD=27 RD=0,1 UX=1.71745,1.71745
| ADD=13 RD=0,1 UX=5.5235,10.2102 | ADD=28 RD=0,1 UX=1.71745,1.71745
| ADD=14 RD=0,1 UX=10.2102,15.0084 | ADD=29 RD=0,1 UX=1.20222,1.19707
| ADD=15 RD=0,1 UX=15.0084,19.5835 | ADD=30 RD=0,1 UX=1.19707,1.19193
| ADD=16 RD=0,1 UX=19.5835,23.6564 | ADD=31 RD=0,1 UX=1.19193,1.19131
| ADD=17 RD=0,1 UX=23.6564,23.9354 | ADD=32 RD=0,1 UX=1.19131,1.18164
| ADD=18 RD=0,1 UX=23.9354,25.9997 | ADD=33 RD=0,1 UX=1.18164,1.17135
| ADD=19 RD=0,1 UX=25.9997,28.0641 | ADD=34 RD=0,1 UX=1.17135,1.16105
ADD=35 RD=0,1 UX=1.16105,1.15138
ADD=36 RD=0,1 UX=1.15138,1.15077
ADD=37 RD=0,1 UX=1.15077,1.14562
ADD=38 RD=0,1 UX=1.14562,1.14048
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=SEUPSLAB
LOAD=SEWALL
LOAD=SEPRINSH
LOAD=SEINER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=1 AT=1
LOAD=SEWALL SF=1 AT=1
LOAD=SEPRINSH SF=1 AT=1
LOAD=SEINER SF=1 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=-1 AT=1
LOAD=SEWALL SF=-1 AT=1
LOAD=SEPRINSH SF=-1 AT=1
LOAD=SEINER SF=-1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 17 | ULTIMATE MAX | 1 | 0 | 0.006616 | 161.6241
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 17 | ULTIMATE MIN | 0 | -224.163 | -199.67 | 0
| 1 | ULTIMATE MIN | 0 | -244.5372 | -261.5871 | -125.4125 | 17 | ULTIMATE MIN | 0.5 | -224.163 | -99.835 | 0
| 1 | ULTIMATE MIN | 1 | -244.5372 | -264.1596 | -80.1028 | 17 | ULTIMATE MIN | 1 | -224.163 | 0 | 0
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 18 | ULTIMATE MAX | 0 | 0 | 0 | 161.6241
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 70.7335 | 18 | ULTIMATE MAX | 0.5 | 0 | 99.835 | 141.1579
| 2 | ULTIMATE MIN | 0 | -244.5372 | -264.1596 | -80.1028 | 18 | ULTIMATE MAX | 1 | 0 | 199.67 | 79.7594
| 2 | ULTIMATE MIN | 1 | -244.5372 | -269.9661 | 0 | 18 | ULTIMATE MIN | 0 | -224.163 | -0.006665 | 0
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 70.7335 | 18 | ULTIMATE MIN | 0.5 | -224.163 | 0 | 0
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 75.1895 | 18 | ULTIMATE MIN | 1 | -224.163 | 0 | 0
| 3 | ULTIMATE MIN | 0 | -244.5372 | -127.9024 | 0 | 19 | ULTIMATE MAX | 0 | 0 | 199.67 | 79.7594
| 3 | ULTIMATE MIN | 1 | -244.5372 | -128.4169 | 0 | 19 | ULTIMATE MAX | 1 | 0 | 304.375 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 75.1895 | 19 | ULTIMATE MIN | 0 | -224.163 | 0 | 0
| 4 | ULTIMATE MAX | 0.5 | 0 | 0 | 109.8415 | 19 | ULTIMATE MIN | 1 | -224.163 | 0 | -73.3134
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 145.5454 | 20 | ULTIMATE MAX | 0 | 0 | 304.375 | 0
| 4 | ULTIMATE MIN | 0 | -244.5372 | -128.4169 | 0 | 20 | ULTIMATE MAX | 1 | 0 | 346.9875 | 0
| 4 | ULTIMATE MIN | 0.5 | -244.5372 | -132.3492 | 0 | 20 | ULTIMATE MIN | 0 | -224.163 | 0 | -73.3134
| 4 | ULTIMATE MIN | 1 | -244.5372 | -136.2814 | 0 | 20 | ULTIMATE MIN | 1 | -224.163 | 0 | -128.9008
| 5 | ULTIMATE MAX | 0 | 0 | 4.1895 | 145.5454 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 0.5 | 0 | 0 | 144.9484 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 1 | 0 | 0 | 145.5454 | 21 | ULTIMATE MIN | 0 | -346.9875 | -224.163 | -128.9008
| 5 | ULTIMATE MIN | 0 | -244.5372 | 0 | 0 | 21 | ULTIMATE MIN | 1 | -349.56 | -190.338 | -77.0935
| 5 | ULTIMATE MIN | 0.5 | -244.5372 | -0.000104 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MIN | 1 | -244.5372 | -4.1896 | 0 | 22 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 6 | ULTIMATE MAX | 0 | 0 | 136.2814 | 145.5454 | 22 | ULTIMATE MIN | 0 | -349.56 | -190.338 | -77.0935
| 6 | ULTIMATE MAX | 0.5 | 0 | 132.3492 | 109.8415 | 22 | ULTIMATE MIN | 1 | -352.4412 | -151.3262 | -35.1363
| 6 | ULTIMATE MAX | 1 | 0 | 128.4169 | 75.1895 | 23 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 6 | ULTIMATE MIN | 0 | -244.5372 | 0 | 0 | 23 | ULTIMATE MAX | 0.25 | 0 | 0 | 30.4606
| 6 | ULTIMATE MIN | 0.5 | -244.5372 | 0 | 0 | 23 | ULTIMATE MAX | 0.5 | 0 | 0 | 51.9202
| 6 | ULTIMATE MIN | 1 | -244.5372 | 0 | 0 | 23 | ULTIMATE MAX | 0.75 | 0 | 70.6819 | 36.6377
| 7 | ULTIMATE MAX | 0 | 0 | 128.4169 | 75.1895 | 23 | ULTIMATE MAX | 1 | 0 | 151.8021 | 0
| 7 | ULTIMATE MAX | 1 | 0 | 127.9024 | 70.7335 | 23 | ULTIMATE MIN | 0 | -352.4412 | -151.3272 | -35.1363
| 7 | ULTIMATE MIN | 0 | -244.5372 | 0 | 0 | 23 | ULTIMATE MIN | 0.25 | -357.4318 | -80.9333 | -6.3339
| 7 | ULTIMATE MIN | 1 | -244.5372 | 0 | 0 | 23 | ULTIMATE MIN | 0.5 | -362.4225 | -6.964 | 0
| 8 | ULTIMATE MAX | 0 | 0 | 269.9661 | 70.7335 | 23 | ULTIMATE MIN | 0.75 | -367.4131 | 0 | -2.1082
| 8 | ULTIMATE MAX | 1 | 0 | 264.1596 | 0 | 23 | ULTIMATE MIN | 1 | -372.4038 | 0 | -28.419
| 8 | ULTIMATE MIN | 0 | -244.5372 | 0 | 0 | 24 | ULTIMATE MAX | 0 | 0 | 151.8021 | 0
| 8 | ULTIMATE MIN | 1 | -244.5372 | 0 | -80.1028 | 24 | ULTIMATE MAX | 1 | 0 | 200.2622 | 0
| 9 | ULTIMATE MAX | 0 | 0 | 264.1596 | 0 | 24 | ULTIMATE MIN | 0 | -372.4038 | 0 | -28.419
| 9 | ULTIMATE MAX | 1 | 0 | 261.5871 | 0 | 24 | ULTIMATE MIN | 1 | -375.285 | 0 | -69.8323
| 9 | ULTIMATE MIN | 0 | -244.5372 | 0 | -80.1028 | 25 | ULTIMATE MAX | 0 | 0 | 200.2622 | 0
| 9 | ULTIMATE MIN | 1 | -244.5372 | 0 | -125.4125 | 25 | ULTIMATE MAX | 1 | 0 | 244.5372 | 0
| 10 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 25 | ULTIMATE MIN | 0 | -375.285 | 0 | -69.8323
| 10 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 25 | ULTIMATE MIN | 1 | -377.8575 | 0 | -125.4125
| 10 | ULTIMATE MIN | 0 | -377.8575 | -244.5372 | -125.4125
| 10 | ULTIMATE MIN | 1 | -375.285 | -200.2622 | -69.8323
| 11 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 11 | ULTIMATE MIN | 0 | -375.285 | -200.2622 | -69.8323
| 11 | ULTIMATE MIN | 1 | -372.4038 | -151.8021 | -28.419
| 12 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 12 | ULTIMATE MAX | 0.25 | 0 | 0 | 36.6377
| 12 | ULTIMATE MAX | 0.5 | 0 | 6.9641 | 51.9202
| 12 | ULTIMATE MAX | 0.75 | 0 | 80.9334 | 30.4605
| 12 | ULTIMATE MAX | 1 | 0 | 151.3273 | 0
| 12 | ULTIMATE MIN | 0 | -372.4038 | -151.8021 | -28.419
| 12 | ULTIMATE MIN | 0.25 | -367.4131 | -70.6819 | -2.1082
| 12 | ULTIMATE MIN | 0.5 | -362.4225 | 0 | 0
| 12 | ULTIMATE MIN | 0.75 | -357.4318 | 0 | -6.3339
| 12 | ULTIMATE MIN | 1 | -352.4412 | 0 | -35.1363
| 13 | ULTIMATE MAX | 0 | 0 | 151.3262 | 0
| 13 | ULTIMATE MAX | 1 | 0 | 190.338 | 0
| 13 | ULTIMATE MIN | 0 | -352.4412 | 0 | -35.1363
| 13 | ULTIMATE MIN | 1 | -349.56 | 0 | -77.0935
| 14 | ULTIMATE MAX | 0 | 0 | 190.338 | 0
| 14 | ULTIMATE MAX | 1 | 0 | 224.163 | 0
| 14 | ULTIMATE MIN | 0 | -349.56 | 0 | -77.0935
| 14 | ULTIMATE MIN | 1 | -346.9875 | 0 | -128.9008
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 15 | ULTIMATE MIN | 0 | -224.163 | -346.9875 | -128.9008
| 15 | ULTIMATE MIN | 1 | -224.163 | -304.375 | -73.3135
| 16 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 16 | ULTIMATE MAX | 1 | 0 | 0 | 79.7594
| 16 | ULTIMATE MIN | 0 | -224.163 | -304.375 | -73.3135
| 16 | ULTIMATE MIN | 1 | -224.163 | -199.67 | 0
| 17 | ULTIMATE MAX | 0 | 0 | 0 | 79.7594
| 17 | ULTIMATE MAX | 0.5 | 0 | 0 | 141.1579
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 17 | SERVICE MIN | 1 | -140.2161 | 0 | 0
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 18 | SERVICE MAX | 0 | 0 | 0 | 103.4847
| 1 | SERVICE MIN | 0 | -152.8316 | -162.7123 | -78.4918 | 18 | SERVICE MAX | 0.5 | 0 | 63.6525 | 90.4359
| 1 | SERVICE MIN | 1 | -152.8316 | -164.856 | -50.3096 | 18 | SERVICE MAX | 1 | 0 | 127.305 | 51.2896
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 18 | SERVICE MIN | 0 | -140.2161 | -0.004635 | 0
| 2 | SERVICE MAX | 1 | 0 | 0 | 45.7127 | 18 | SERVICE MIN | 0.5 | -140.2161 | 0 | 0
| 2 | SERVICE MIN | 0 | -152.8316 | -164.856 | -50.3096 | 18 | SERVICE MIN | 1 | -140.2161 | 0 | 0
| 2 | SERVICE MIN | 1 | -152.8316 | -177.5948 | 0 | 19 | SERVICE MAX | 0 | 0 | 127.305 | 51.2896
| 3 | SERVICE MAX | 0 | 0 | 0 | 45.7127 | 19 | SERVICE MAX | 1 | 0 | 194.0625 | 0
| 3 | SERVICE MAX | 1 | 0 | 0 | 48.3216 | 19 | SERVICE MIN | 0 | -140.2161 | 0 | 0
| 3 | SERVICE MIN | 0 | -152.8316 | -74.5008 | 0 | 19 | SERVICE MIN | 1 | -140.2161 | 0 | -45.4152
| 3 | SERVICE MIN | 1 | -152.8316 | -75.6295 | 0 | 20 | SERVICE MAX | 0 | 0 | 194.0625 | 0
| 4 | SERVICE MAX | 0 | 0 | 0 | 48.3216 | 20 | SERVICE MAX | 1 | 0 | 221.2312 | 0
| 4 | SERVICE MAX | 0.5 | 0 | 0 | 69.5654 | 20 | SERVICE MIN | 0 | -140.2161 | 0 | -45.4152
| 4 | SERVICE MAX | 1 | 0 | 0 | 93.1169 | 20 | SERVICE MIN | 1 | -140.2161 | 0 | -81.2028
| 4 | SERVICE MIN | 0 | -152.8316 | -75.6295 | 0 | 21 | SERVICE MAX | 0 | 0 | 0 | 0
| 4 | SERVICE MIN | 0.5 | -152.8316 | -84.2564 | 0 | 21 | SERVICE MAX | 1 | 0 | 0 | 0
| 4 | SERVICE MIN | 1 | -152.8316 | -92.8833 | 0 | 21 | SERVICE MIN | 0 | -221.2312 | -140.2161 | -81.2028
| 5 | SERVICE MAX | 0 | 0 | 9.1913 | 93.1169 | 21 | SERVICE MIN | 1 | -223.375 | -119.0755 | -48.7789
| 5 | SERVICE MAX | 0.5 | 0 | 0 | 91.8072 | 22 | SERVICE MAX | 0 | 0 | 0 | 0
| 5 | SERVICE MAX | 1 | 0 | 0 | 93.1169 | 22 | SERVICE MAX | 1 | 0 | 0 | 0
| 5 | SERVICE MIN | 0 | -152.8316 | 0 | 0 | 22 | SERVICE MIN | 0 | -223.375 | -119.0755 | -48.7789
| 5 | SERVICE MIN | 0.5 | -152.8316 | -6.5e-05 | 0 | 22 | SERVICE MIN | 1 | -225.776 | -94.6931 | -22.5062
| 5 | SERVICE MIN | 1 | -152.8316 | -9.1913 | 0 | 23 | SERVICE MAX | 0 | 0 | 0 | 0
| 6 | SERVICE MAX | 0 | 0 | 92.8833 | 93.1169 | 23 | SERVICE MAX | 0.25 | 0 | 0 | 18.1303
| 6 | SERVICE MAX | 0.5 | 0 | 84.2564 | 69.5654 | 23 | SERVICE MAX | 0.5 | 0 | 0 | 31.5143
| 6 | SERVICE MAX | 1 | 0 | 75.6295 | 48.3216 | 23 | SERVICE MAX | 0.75 | 0 | 44.172 | 21.9344
| 6 | SERVICE MIN | 0 | -152.8316 | 0 | 0 | 23 | SERVICE MAX | 1 | 0 | 94.8721 | 0
| 6 | SERVICE MIN | 0.5 | -152.8316 | 0 | 0 | 23 | SERVICE MIN | 0 | -225.776 | -94.694 | -22.5062
| 6 | SERVICE MIN | 1 | -152.8316 | 0 | 0 | 23 | SERVICE MIN | 0.25 | -229.9349 | -50.6978 | -4.4189
| 7 | SERVICE MAX | 0 | 0 | 75.6295 | 48.3216 | 23 | SERVICE MIN | 0.5 | -234.0938 | -4.467 | 0
| 7 | SERVICE MAX | 1 | 0 | 74.5008 | 45.7127 | 23 | SERVICE MIN | 0.75 | -238.2526 | 0 | -1.6062
| 7 | SERVICE MIN | 0 | -152.8316 | 0 | 0 | 23 | SERVICE MIN | 1 | -242.4115 | 0 | -17.9647
| 7 | SERVICE MIN | 1 | -152.8316 | 0 | 0 | 24 | SERVICE MAX | 0 | 0 | 94.8721 | 0
| 8 | SERVICE MAX | 0 | 0 | 177.5948 | 45.7127 | 24 | SERVICE MAX | 1 | 0 | 125.1597 | 0
| 8 | SERVICE MAX | 1 | 0 | 164.856 | 0 | 24 | SERVICE MIN | 0 | -242.4115 | 0 | -17.9647
| 8 | SERVICE MIN | 0 | -152.8316 | 0 | 0 | 24 | SERVICE MIN | 1 | -244.8125 | 0 | -43.7985
| 8 | SERVICE MIN | 1 | -152.8316 | 0 | -50.3096 | 25 | SERVICE MAX | 0 | 0 | 125.1597 | 0
| 9 | SERVICE MAX | 0 | 0 | 164.856 | 0 | 25 | SERVICE MAX | 1 | 0 | 152.8316 | 0
| 9 | SERVICE MAX | 1 | 0 | 162.7123 | 0 | 25 | SERVICE MIN | 0 | -244.8125 | 0 | -43.7985
| 9 | SERVICE MIN | 0 | -152.8316 | 0 | -50.3096 | 25 | SERVICE MIN | 1 | -246.9563 | 0 | -78.4918
| 9 | SERVICE MIN | 1 | -152.8316 | 0 | -78.4918
| 10 | SERVICE MAX | 0 | 0 | 0 | 0
| 10 | SERVICE MAX | 1 | 0 | 0 | 0
| 10 | SERVICE MIN | 0 | -246.9563 | -152.8316 | -78.4918
| 10 | SERVICE MIN | 1 | -244.8125 | -125.1597 | -43.7985
| 11 | SERVICE MAX | 0 | 0 | 0 | 0
| 11 | SERVICE MAX | 1 | 0 | 0 | 0
| 11 | SERVICE MIN | 0 | -244.8125 | -125.1597 | -43.7985
| 11 | SERVICE MIN | 1 | -242.4115 | -94.8721 | -17.9647
| 12 | SERVICE MAX | 0 | 0 | 0 | 0
| 12 | SERVICE MAX | 0.25 | 0 | 0 | 21.9344
| 12 | SERVICE MAX | 0.5 | 0 | 4.4671 | 31.5143
| 12 | SERVICE MAX | 0.75 | 0 | 50.6979 | 18.1303
| 12 | SERVICE MAX | 1 | 0 | 94.694 | 0
| 12 | SERVICE MIN | 0 | -242.4115 | -94.8721 | -17.9647
| 12 | SERVICE MIN | 0.25 | -238.2526 | -44.172 | -1.6062
| 12 | SERVICE MIN | 0.5 | -234.0938 | 0 | 0
| 12 | SERVICE MIN | 0.75 | -229.9349 | 0 | -4.4189
| 12 | SERVICE MIN | 1 | -225.776 | 0 | -22.5062
| 13 | SERVICE MAX | 0 | 0 | 94.6931 | 0
| 13 | SERVICE MAX | 1 | 0 | 119.0755 | 0
| 13 | SERVICE MIN | 0 | -225.776 | 0 | -22.5062
| 13 | SERVICE MIN | 1 | -223.375 | 0 | -48.7789
| 14 | SERVICE MAX | 0 | 0 | 119.0755 | 0
| 14 | SERVICE MAX | 1 | 0 | 140.2161 | 0
| 14 | SERVICE MIN | 0 | -223.375 | 0 | -48.7789
| 14 | SERVICE MIN | 1 | -221.2312 | 0 | -81.2028
| 15 | SERVICE MAX | 0 | 0 | 0 | 0
| 15 | SERVICE MAX | 1 | 0 | 0 | 0
| 15 | SERVICE MIN | 0 | -140.2161 | -221.2312 | -81.2028
| 15 | SERVICE MIN | 1 | -140.2161 | -194.0625 | -45.4152
| 16 | SERVICE MAX | 0 | 0 | 0 | 0
| 16 | SERVICE MAX | 1 | 0 | 0 | 51.2896
| 16 | SERVICE MIN | 0 | -140.2161 | -194.0625 | -45.4152
| 16 | SERVICE MIN | 1 | -140.2161 | -127.305 | 0
| 17 | SERVICE MAX | 0 | 0 | 0 | 51.2896
| 17 | SERVICE MAX | 0.5 | 0 | 0 | 90.4359
| 17 | SERVICE MAX | 1 | 0 | 0.004605 | 103.4847
| 17 | SERVICE MIN | 0 | -140.2161 | -127.305 | 0
| 17 | SERVICE MIN | 0.5 | -140.2161 | -63.6525 | 0

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 19 | ULTIMATE MAX | 0 | 0 | 30.342 | 0
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 13.9602 | 19 | ULTIMATE MAX | 1 | 0 | 32.1124 | 0
| 1 | ULTIMATE MIN | 0 | -14.0364 | -96.3104 | -26.5401 | 19 | ULTIMATE MIN | 0 | -212.3778 | 0 | -42.9813
| 1 | ULTIMATE MIN | 1 | -13.6915 | -98.4542 | -9.4982 | 19 | ULTIMATE MIN | 1 | -211.0241 | 0 | -49.6954
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 13.9602 | 20 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 47.0282 | 20 | ULTIMATE MAX | 1 | 0 | 0 | 4.6414
| 2 | ULTIMATE MIN | 0 | -13.6915 | -98.4542 | -9.4982 | 20 | ULTIMATE MIN | 0 | -43.4136 | -227.9604 | -49.6954
| 2 | ULTIMATE MIN | 1 | -12.9131 | -103.2929 | 0 | 20 | ULTIMATE MIN | 1 | -40.8862 | -200.7916 | -12.1796
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 47.0282 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 4.6414
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 48.1282 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 66.5272
| 3 | ULTIMATE MIN | 0 | -11.2304 | -50.5121 | 0 | 21 | ULTIMATE MIN | 0 | -40.8862 | -200.7916 | -12.1796
| 3 | ULTIMATE MIN | 1 | -11.1614 | -50.9408 | 0 | 21 | ULTIMATE MIN | 1 | -35.3049 | -139.4679 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 48.1282 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 66.5272
| 4 | ULTIMATE MAX | 0.5 | 0 | 0 | 57.0311 | 22 | ULTIMATE MAX | 1 | 0 | 0 | 70.8425
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 66.8106 | 22 | ULTIMATE MIN | 0 | -41.3607 | -139.4675 | 0
| 4 | ULTIMATE MIN | 0 | -11.1614 | -50.9408 | 0 | 22 | ULTIMATE MIN | 1 | -40.8552 | -134.0338 | 0
| 4 | ULTIMATE MIN | 0.5 | -10.6343 | -54.2177 | 0 | 23 | ULTIMATE MAX | 0 | 0 | 0 | 70.8425
| 4 | ULTIMATE MIN | 1 | -10.1071 | -57.4946 | 0 | 23 | ULTIMATE MAX | 0.5 | 0 | 0 | 97.5423
| 5 | ULTIMATE MAX | 0 | 0 | 13.4594 | 66.8106 | 23 | ULTIMATE MAX | 1 | 0 | 0 | 113.133
| 5 | ULTIMATE MAX | 0.5 | 0 | 9.9681 | 63.4722 | 23 | ULTIMATE MIN | 0 | -40.8552 | -134.0338 | 0
| 5 | ULTIMATE MAX | 1 | 0 | 6.4769 | 66.8106 | 23 | ULTIMATE MIN | 0.5 | -36.9918 | -92.5044 | 0
| 5 | ULTIMATE MIN | 0 | -8.4295 | -6.4769 | 0 | 23 | ULTIMATE MIN | 1 | -37.3073 | -50.975 | 0
| 5 | ULTIMATE MIN | 0.5 | -7.8679 | -9.9681 | 0 | 24 | ULTIMATE MAX | 0 | 0 | 0 | 113.133
| 5 | ULTIMATE MIN | 1 | -8.4295 | -13.4594 | 0 | 24 | ULTIMATE MAX | 0.5 | 0 | 6.7284 | 117.5205
| 6 | ULTIMATE MAX | 0 | 0 | 57.4946 | 66.8106 | 24 | ULTIMATE MAX | 1 | 0 | 50.9746 | 113.133
| 6 | ULTIMATE MAX | 0.5 | 0 | 54.2177 | 57.0311 | 24 | ULTIMATE MIN | 0 | -39.3256 | -50.9746 | 0
| 6 | ULTIMATE MAX | 1 | 0 | 50.9408 | 48.1282 | 24 | ULTIMATE MIN | 0.5 | -35.2095 | -6.7284 | 0
| 6 | ULTIMATE MIN | 0 | -10.1071 | 0 | 0 | 24 | ULTIMATE MIN | 1 | -39.3256 | 0 | 0
| 6 | ULTIMATE MIN | 0.5 | -10.6343 | 0 | 0 | 25 | ULTIMATE MAX | 0 | 0 | 50.975 | 113.133
| 6 | ULTIMATE MIN | 1 | -11.1614 | 0 | 0 | 25 | ULTIMATE MAX | 0.5 | 0 | 92.5044 | 97.5423
| 7 | ULTIMATE MAX | 0 | 0 | 50.9408 | 48.1282 | 25 | ULTIMATE MAX | 1 | 0 | 134.0338 | 70.8425
| 7 | ULTIMATE MAX | 1 | 0 | 50.5121 | 47.0282 | 25 | ULTIMATE MIN | 0 | -37.3073 | 0 | 0
| 7 | ULTIMATE MIN | 0 | -11.1614 | 0 | 0 | 25 | ULTIMATE MIN | 0.5 | -36.9918 | 0 | 0
| 7 | ULTIMATE MIN | 1 | -11.2304 | 0 | 0 | 25 | ULTIMATE MIN | 1 | -40.8552 | 0 | 0
| 8 | ULTIMATE MAX | 0 | 0 | 103.2929 | 47.0282 | 26 | ULTIMATE MAX | 0 | 0 | 134.0338 | 70.8425
| 8 | ULTIMATE MAX | 1 | 0 | 98.4542 | 13.9602 | 26 | ULTIMATE MAX | 1 | 0 | 139.4675 | 66.5272
| 8 | ULTIMATE MIN | 0 | -12.9131 | 0 | 0 | 26 | ULTIMATE MIN | 0 | -40.8552 | 0 | 0
| 8 | ULTIMATE MIN | 1 | -13.6915 | 0 | -9.4982 | 26 | ULTIMATE MIN | 1 | -41.3607 | 0 | 0
| 9 | ULTIMATE MAX | 0 | 0 | 98.4542 | 13.9602 | 27 | ULTIMATE MAX | 0 | 0 | 139.4679 | 66.5272
| 9 | ULTIMATE MAX | 1 | 0 | 96.3104 | 0 | 27 | ULTIMATE MAX | 1 | 0 | 200.7916 | 4.6414
| 9 | ULTIMATE MIN | 0 | -13.6915 | 0 | -9.4982 | 27 | ULTIMATE MIN | 0 | -35.3049 | 0 | 0
| 9 | ULTIMATE MIN | 1 | -14.0364 | 0 | -26.5401 | 27 | ULTIMATE MIN | 1 | -40.8862 | 0 | -12.1796
| 10 | ULTIMATE MAX | 0 | 0 | 3.7437 | 0 | 28 | ULTIMATE MAX | 0 | 0 | 200.7916 | 4.6414
| 10 | ULTIMATE MAX | 1 | 0 | 3.1301 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 227.9604 | 0
| 10 | ULTIMATE MIN | 0 | -156.5294 | -15.3995 | -26.5401 | 28 | ULTIMATE MIN | 0 | -40.8862 | 0 | -12.1796
| 10 | ULTIMATE MIN | 1 | -153.5956 | -14.786 | -22.7532 | 28 | ULTIMATE MIN | 1 | -43.4136 | 0 | -49.6954
| 11 | ULTIMATE MAX | 0 | 0 | 3.1302 | 0 | 29 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MAX | 1 | 0 | 1.8598 | 0 | 29 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 11 | ULTIMATE MIN | 0 | -153.5956 | -14.786 | -22.7532 | 29 | ULTIMATE MIN | 0 | -211.0241 | -32.1124 | -49.6954
| 11 | ULTIMATE MIN | 1 | -150.6619 | -13.5156 | -19.2019 | 29 | ULTIMATE MIN | 1 | -212.3778 | -30.342 | -42.9813
| 12 | ULTIMATE MAX | 0 | 0 | 9.613 | 0 | 30 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 12 | ULTIMATE MAX | 1 | 0 | 9.417 | 0 | 30 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 12 | ULTIMATE MIN | 0 | -165.9755 | -13.5156 | -19.2019 | 30 | ULTIMATE MIN | 0 | -212.3778 | -30.342 | -42.9813
| 12 | ULTIMATE MIN | 1 | -165.6235 | -13.3195 | -18.7993 | 30 | ULTIMATE MIN | 1 | -213.7316 | -36.8825 | -34.5675
| 13 | ULTIMATE MAX | 0 | 0 | 9.4171 | 0 | 31 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 13 | ULTIMATE MAX | 1 | 0 | 5.1762 | 0 | 31 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 13 | ULTIMATE MIN | 0 | -165.6235 | -13.3195 | -18.7993 | 31 | ULTIMATE MIN | 0 | -196.8995 | -19.7562 | -34.5675
| 13 | ULTIMATE MIN | 1 | -160.108 | -9.0787 | -13.4494 | 31 | ULTIMATE MIN | 1 | -197.0619 | -20.5058 | -33.9635
| 14 | ULTIMATE MAX | 0 | 0 | 16.4409 | 0 | 32 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 14 | ULTIMATE MAX | 1 | 0 | 9.5532 | 0 | 32 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 14 | ULTIMATE MIN | 0 | -175.5019 | -9.0787 | -13.4494 | 32 | ULTIMATE MIN | 0 | -197.0619 | -20.5058 | -33.9635
| 14 | ULTIMATE MIN | 1 | -169.6344 | -2.1909 | -11.9893 | 32 | ULTIMATE MIN | 1 | -199.607 | -31.2248 | -21.7317
| 15 | ULTIMATE MAX | 0 | 0 | 23.9117 | 0 | 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 14.6755 | 0 | 33 | ULTIMATE MAX | 1 | 0 | 2.1909 | 0
| 15 | ULTIMATE MIN | 0 | -185.5799 | -2.1909 | -11.9893 | 33 | ULTIMATE MIN | 0 | -182.8724 | -14.6755 | -21.7317
| 15 | ULTIMATE MIN | 1 | -182.8724 | 0 | -21.7317 | 33 | ULTIMATE MIN | 1 | -185.5799 | -23.9117 | -11.9893
| 16 | ULTIMATE MAX | 0 | 0 | 31.2248 | 0 | 34 | ULTIMATE MAX | 0 | 0 | 2.1909 | 0
| 16 | ULTIMATE MAX | 1 | 0 | 20.5058 | 0 | 34 | ULTIMATE MAX | 1 | 0 | 9.0787 | 0
| 16 | ULTIMATE MIN | 0 | -199.607 | 0 | -21.7317 | 34 | ULTIMATE MIN | 0 | -169.6344 | -9.5532 | -11.9893
| 16 | ULTIMATE MIN | 1 | -197.0619 | 0 | -33.9635 | 34 | ULTIMATE MIN | 1 | -175.5019 | -16.4409 | -13.4494
| 17 | ULTIMATE MAX | 0 | 0 | 20.5058 | 0 | 35 | ULTIMATE MAX | 0 | 0 | 9.0787 | 0
| 17 | ULTIMATE MAX | 1 | 0 | 19.7562 | 0 | 35 | ULTIMATE MAX | 1 | 0 | 13.3195 | 0
| 17 | ULTIMATE MIN | 0 | -197.0619 | 0 | -33.9635 | 35 | ULTIMATE MIN | 0 | -160.108 | -5.1762 | -13.4494
| 17 | ULTIMATE MIN | 1 | -196.8995 | 0 | -34.5675 | 35 | ULTIMATE MIN | 1 | -165.6235 | -9.4171 | -18.7993
| 18 | ULTIMATE MAX | 0 | 0 | 36.8825 | 0 | 36 | ULTIMATE MAX | 0 | 0 | 13.3195 | 0
| 18 | ULTIMATE MAX | 1 | 0 | 30.342 | 0 | 36 | ULTIMATE MAX | 1 | 0 | 13.5156 | 0
| 18 | ULTIMATE MIN | 0 | -213.7316 | 0 | -34.5675 | 36 | ULTIMATE MIN | 0 | -165.6235 | -9.417 | -18.7993
| 18 | ULTIMATE MIN | 1 | -212.3778 | 0 | -42.9813 | 36 | ULTIMATE MIN | 1 | -165.9755 | -9.613 | -19.2019
| FRAME | LOAD | DIST | P | V2 | M3
| 37 | ULTIMATE MAX | 0 | 0 | 13.5156 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 14.786 | 0
| 37 | ULTIMATE MIN | 0 | -150.6619 | -1.8598 | -19.2019
| 37 | ULTIMATE MIN | 1 | -153.5956 | -3.1302 | -22.7532
| 38 | ULTIMATE MAX | 0 | 0 | 14.786 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 15.3995 | 0
| 38 | ULTIMATE MIN | 0 | -153.5956 | -3.1301 | -22.7532
| 38 | ULTIMATE MIN | 1 | -156.5294 | -3.7437 | -26.5401

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 128.901 | 199.67 | 224.163 | 81.203 | 1000 | 583.333
|  | 중앙부 | 161.624 | - | 224.163 | 103.485 | 1000 | 500
|  | 단지점부(우측) | 128.901 | 199.67 | 224.163 | 81.203 | 1000 | 583.333
| 하부슬래브 | 단지점부(좌측) | 125.412 | 128.417 | 244.537 | 78.492 | 1000 | 500
|  | 중앙부 | 145.545 | - | 244.537 | 93.117 | 1000 | 500
|  | 단지점부(우측) | 125.412 | 128.417 | 244.537 | 78.492 | 1000 | 500
| 좌측벽체 | 상부 | 128.901 | 151.327 | 346.988 | 81.203 | 1000 | 433.333
|  | 중앙부 | 51.92 | - | 362.423 | 31.514 | 1000 | 350
|  | 중앙부(부모멘트) | -35.136 | - | 362.423 | -22.506 | 1000 | 350 | 부모멘트
|  | 하부 | 125.412 | 151.802 | 377.858 | 78.492 | 1000 | 350
| 우측벽체 | 상부 | 128.901 | 151.327 | 346.988 | 81.203 | 1000 | 433.333
|  | 중앙부 | 51.92 | - | 362.423 | 31.514 | 1000 | 350
|  | 중앙부(부모멘트) | -35.136 | - | 362.423 | -22.506 | 1000 | 350 | 부모멘트
|  | 하부 | 125.412 | 151.802 | 377.858 | 78.492 | 1000 | 350

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 49.695 | 134.034 | 43.414 | 1000 | 583.333
|  | 중앙부 | 117.52 | - | 35.209 | 1000 | 500
|  | 단지점부(우측) | 49.695 | 134.034 | 43.414 | 1000 | 583.333
| 하부슬래브 | 단지점부(좌측) | 26.54 | 50.941 | 14.036 | 1000 | 500
|  | 중앙부 | 66.811 | - | 10.107 | 1000 | 500
|  | 단지점부(우측) | 26.54 | 50.941 | 14.036 | 1000 | 500
| 좌측벽체 | 상부 | 49.695 | 20.506 | 211.024 | 1000 | 433.333
|  | 중앙부 | 0 | - | 196.899 | 1000 | 350
|  | 중앙부(부모멘트) | -34.567 | - | 196.899 | 1000 | 350 | 부모멘트
|  | 하부 | 26.54 | 13.32 | 156.529 | 1000 | 350
| 우측벽체 | 상부 | 49.695 | 20.506 | 211.024 | 1000 | 433.333
|  | 중앙부 | 0 | - | 165.976 | 1000 | 350
|  | 중앙부(부모멘트) | -34.567 | - | 165.976 | 1000 | 350 | 부모멘트
|  | 하부 | 26.54 | 13.32 | 156.529 | 1000 | 350

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 513.333 | 128.901 | 221.459 |  | 749.268 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.718
상부슬래브 : 중앙부 |  |  |  | 1000 |  | 410 | 161.624 | 257.941 |  | 1193.487 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.596
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 513.333 | 128.901 | 221.459 |  | 749.268 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.718
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 430 | 125.412 | 223.868 |  | 875.282 | H16 - 8.0EA |  |  | 1588.8 | 1.785
하부슬래브 : 중앙부 |  |  |  | 1000 |  | 410 | 145.545 | 213.064 |  | 1071.54 | H16 - 8.0EA |  |  | 1588.8 | 1.464
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 430 | 125.412 | 223.868 |  | 875.282 | H16 - 8.0EA |  |  | 1588.8 | 1.785
좌측벽체 : 상부 |  |  |  | 1000 |  | 363.333 | 128.901 | 262.076 |  | - | H16 - 4.0EA + H13 - 4.0EA |  |  | - | 2.033
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 260 | 51.92 | 282.73 |  | - | H19 - 4.0EA |  |  | - | 5.445
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 280 | 35.136 | 281.33 |  | - | H16 - 4.0EA |  |  | - | 8.007
좌측벽체 : 하부 |  |  |  | 1000 |  | 280 | 125.412 | 212.669 |  | - | H16 - 8.0EA |  |  | - | 1.696
우측벽체 : 상부 |  |  |  | 1000 |  | 363.333 | 128.901 | 262.076 |  | - | H16 - 4.0EA + H13 - 4.0EA |  |  | - | 2.033
우측벽체 : 중앙부 |  |  |  | 1000 |  | 260 | 51.92 | 282.73 |  | - | H19 - 4.0EA |  |  | - | 5.445
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 280 | 35.136 | 281.33 |  | - | H16 - 4.0EA |  |  | - | 8.007
우측벽체 : 하부 |  |  |  | 1000 |  | 280 | 125.412 | 212.669 |  | - | H16 - 8.0EA |  |  | - | 1.696
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 263.32 |  | 199.67 | 263.32 | - |  | - | - | - |  | - | O.K
상부슬래브 : 중앙부 |  |  |  | 251.073 |  | - | 251.073 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 263.32 |  | 199.67 | 263.32 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 263.32 |  | 128.417 | 263.32 | - |  | - | - | - |  | - | O.K
하부슬래브 : 중앙부 |  |  |  | 251.073 |  | - | 251.073 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 263.32 |  | 128.417 | 263.32 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 183.606 |  | 151.327 | 183.606 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 170.993 |  | - | 170.993 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 184.687 |  | 151.802 | 184.687 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 183.606 |  | 151.327 | 183.606 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 170.993 |  | - | 170.993 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 184.687 |  | 151.802 | 184.687 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 583.333 |  | 513.333 |  | 70 |  | 128.901 |  | 199.67
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (513.33 - 30.016) / 30.016 = 0.0483
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 749.268 mm²
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00253
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (513.33 - a/2) = 221.459 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 128.901 kN.m) ∴ O.K [안전률 1.718]
＊ 전단에 대한 검토 (d = 430.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 430.00 = 263.320 kN
≥ Vu (= 199.670 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 500 |  | 410 |  | 90 |  | 161.624 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (410.00 - 44.761) / 44.761 = 0.0245
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1193.487 mm²
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00473
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (410.00 - a/2) = 257.941 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 161.624 kN.m) ∴ O.K [안전률 1.596]
＊ 전단에 대한 검토 (d = 410.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 410.00 = 251.073 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 583.333 |  | 513.333 |  | 70 |  | 128.901 |  | 199.67
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (513.33 - 30.016) / 30.016 = 0.0483
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 749.268 mm²
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00253
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (513.33 - a/2) = 221.459 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 128.901 kN.m) ∴ O.K [안전률 1.718]
＊ 전단에 대한 검토 (d = 430.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 430.00 = 263.320 kN
≥ Vu (= 199.670 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 500 |  | 430 |  | 70 |  | 125.412 |  | 128.417
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (430.00 - 36.651) / 36.651 = 0.0322
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 875.282 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00369
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (430.00 - a/2) = 223.868 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 125.412 kN.m) ∴ O.K [안전률 1.785]
＊ 전단에 대한 검토 (d = 430.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 430.00 = 263.320 kN
≥ Vu (= 128.417 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 500 |  | 410 |  | 90 |  | 145.545 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (410.00 - 36.651) / 36.651 = 0.0306
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1071.540 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00388
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (410.00 - a/2) = 213.064 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 145.545 kN.m) ∴ O.K [안전률 1.464]
＊ 전단에 대한 검토 (d = 410.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 410.00 = 251.073 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 500 |  | 430 |  | 70 |  | 125.412 |  | 128.417
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (430.00 - 36.651) / 36.651 = 0.0322
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 875.282 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00369
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (430.00 - a/2) = 223.868 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 125.412 kN.m) ∴ O.K [안전률 1.785]
＊ 전단에 대한 검토 (d = 430.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 430.00 = 263.320 kN
≥ Vu (= 128.417 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 433.333 |  | 363.333 |  | 346.988 |  | 128.901 |  | 151.327 |  | 371.486
＊ 철근비 검토
As = 1301.200 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA + H13- 4.0EA , d1 = 70.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0056) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 433.3 x 1000.0 = 8840000.0 N
Cs = As x fy = 520480.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (8840000.0 x 216.67 + 520480.0 x 70.000 + 458400.0 x 343.333) / 9818880.0
= 214.806 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 218.000 mm, ab = k1 x cb = 185.300 mm
fs' = 600 x (218.000 - 90.000) / 218.000 (≤fy) = 352.294 MPa
Cc = 0.85 x 24.0 x 185.300 x 1000.000 = 3780.120 kN
Cs = As' x (fs' - 0.85 x fck) = 380.350 kN
Ts = As x fs = 520.480 kN
Pb = 3780.120 + 380.350 - 520.480 = 3639.990 kN
Mb = 3780.120 x (363.333 - 185.300/2) + 380.350 x (363.333 - 90.00)
- 3639.990 x (214.806 - 70.000)
= 600.087 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 164.859 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 81.766 mm, a = k1 x c = 69.501 mm 를 사용.
fs = 600 x (363.333 - 81.766) / 81.766 (≤fy) = 400.000 MPa
fs' = 600 x ( 81.766 - 90.000) / 81.766 (≤fy) = 17.546 MPa
Cc = 0.85 x 24.0 x 69.501 x 1000.000 = 1417.824 kN
Cs = As' x (fs' - 0.85 x fck) = -3.271 kN
Ts = As x fs = 520.480 kN
Pn = 1417.824 + -3.271 - 520.480 = 900.615 kN
Mn' = 1417.824 x (363.333 - 69.501/2) + -3.271 x (363.333 - 90.00)
= 464.978 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0011 ＜ 0.0100 (e' = e + Xp - dc = 516.291 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 70.00 = 280.000 mm
c = 600.00 / (600.00+400.00) x 280.000 = 168.000 mm, a = k1 x c = 142.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (280.00-168.00) / 168.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7815.166 kN ≥ Pn = 900.615 kN
ΦPn = 0.78 x 900.615 = 705.481 kN ≥ Pu = 346.988 kN ∴ O.K
ΦMn = ΦPn x 0.371 = 262.076 kN.m ≥ Mu = 128.901 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 280.00 = 183.606 kN
≥ Vu (= 151.327 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 350 |  | 260 |  | 362.423 |  | 51.92 |  | 0 |  | 143.259
＊ 철근비 검토
As = 1146.000 mm² (인장중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0055) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 350.0 x 1000.0 = 7140000.0 N
Cs = As x fy = 458400.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (7140000.0 x 175.00 + 458400.0 x 90.000 + 317760.0 x 280.000) / 7916160.0
= 174.293 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 156.000 mm, ab = k1 x cb = 132.600 mm
fs' = 600 x (156.000 - 70.000) / 156.000 (≤fy) = 330.769 MPa
Cc = 0.85 x 24.0 x 132.600 x 1000.000 = 2705.040 kN
Cs = As' x (fs' - 0.85 x fck) = 246.557 kN
Ts = As x fs = 458.400 kN
Pb = 2705.040 + 246.557 - 458.400 = 2493.197 kN
Mb = 2705.040 x (260.000 - 132.600/2) + 246.557 x (260.000 - 70.00)
- 2493.197 x (174.293 - 90.000)
= 360.654 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 144.655 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 157.009 mm, a = k1 x c = 133.458 mm 를 사용.
fs = 600 x (260.000 - 157.009) / 157.009 (≤fy) = 393.572 MPa
fs' = 600 x (157.009 - 70.000) / 157.009 (≤fy) = 332.500 MPa
Cc = 0.85 x 24.0 x 133.458 x 1000.000 = 2722.541 kN
Cs = As' x (fs' - 0.85 x fck) = 247.932 kN
Ts = As x fs = 451.033 kN
Pn = 2722.541 + 247.932 - 451.033 = 2519.440 kN
Mn' = 2722.541 x (260.000 - 133.458/2) + 247.932 x (260.000 - 70.00)
= 573.295 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0026 ＜ 0.0100 (e' = e + Xp - dc = 227.551 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 90.00 = 260.000 mm
c = 600.00 / (600.00+400.00) x 260.000 = 156.000 mm, a = k1 x c = 132.600 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (260.00-156.00) / 156.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6301.261 kN ≥ Pn = 2519.440 kN
ΦPn = 0.78 x 2519.440 = 1973.561 kN ≥ Pu = 362.423 kN ∴ O.K
ΦMn = ΦPn x 0.143 = 282.730 kN.m ≥ Mu = 51.920 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 260.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 260.00 = 170.993 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 350 |  | 280 |  | 362.423 |  | 35.136 |  | 0 |  | 96.949
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0055) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 350.0 x 1000.0 = 7140000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (7140000.0 x 175.00 + 317760.0 x 70.000 + 458400.0 x 260.000) / 7916160.0
= 175.707 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 168.000 mm, ab = k1 x cb = 142.800 mm
fs' = 600 x (168.000 - 90.000) / 168.000 (≤fy) = 278.571 MPa
Cc = 0.85 x 24.0 x 142.800 x 1000.000 = 2913.120 kN
Cs = As' x (fs' - 0.85 x fck) = 295.864 kN
Ts = As x fs = 317.760 kN
Pb = 2913.120 + 295.864 - 317.760 = 2891.224 kN
Mb = 2913.120 x (280.000 - 142.800/2) + 295.864 x (280.000 - 90.00)
- 2891.224 x (175.707 - 70.000)
= 358.268 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 123.915 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 203.267 mm, a = k1 x c = 172.777 mm 를 사용.
fs = 600 x (280.000 - 203.267) / 203.267 (≤fy) = 226.501 MPa
fs' = 600 x (203.267 - 90.000) / 203.267 (≤fy) = 334.339 MPa
Cc = 0.85 x 24.0 x 172.777 x 1000.000 = 3524.643 kN
Cs = As' x (fs' - 0.85 x fck) = 359.774 kN
Ts = As x fs = 179.932 kN
Pn = 3524.643 + 359.774 - 179.932 = 3704.485 kN
Mn' = 3524.643 x (280.000 - 172.777/2) + 359.774 x (280.000 - 90.00)
= 750.769 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0091 ＜ 0.0100 (e' = e + Xp - dc = 202.656 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 70.00 = 280.000 mm
c = 600.00 / (600.00+400.00) x 280.000 = 168.000 mm, a = k1 x c = 142.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (280.00-168.00) / 168.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6301.261 kN ≥ Pn = 3704.485 kN
ΦPn = 0.78 x 3704.485 = 2901.846 kN ≥ Pu = 362.423 kN ∴ O.K
ΦMn = ΦPn x 0.097 = 281.330 kN.m ≥ Mu = 35.136 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 280.00 = 184.146 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 350 |  | 280 |  | 377.858 |  | 125.412 |  | 151.802 |  | 331.904
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0078) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 350.0 x 1000.0 = 7140000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (7140000.0 x 175.00 + 635520.0 x 70.000 + 458400.0 x 260.000) / 8233920.0
= 171.628 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 168.000 mm, ab = k1 x cb = 142.800 mm
fs' = 600 x (168.000 - 90.000) / 168.000 (≤fy) = 278.571 MPa
Cc = 0.85 x 24.0 x 142.800 x 1000.000 = 2913.120 kN
Cs = As' x (fs' - 0.85 x fck) = 295.864 kN
Ts = As x fs = 635.520 kN
Pb = 2913.120 + 295.864 - 635.520 = 2573.464 kN
Mb = 2913.120 x (280.000 - 142.800/2) + 295.864 x (280.000 - 90.00)
- 2573.464 x (171.628 - 70.000)
= 402.355 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 156.348 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 83.740 mm, a = k1 x c = 71.179 mm 를 사용.
fs = 600 x (280.000 - 83.740) / 83.740 (≤fy) = 400.000 MPa
fs' = 600 x ( 83.740 - 90.000) / 83.740 (≤fy) = 19.137 MPa
Cc = 0.85 x 24.0 x 71.179 x 1000.000 = 1452.056 kN
Cs = As' x (fs' - 0.85 x fck) = -1.447 kN
Ts = As x fs = 635.520 kN
Pn = 1452.056 + -1.447 - 635.520 = 817.983 kN
Mn' = 1452.056 x (280.000 - 71.179/2) + -1.447 x (280.000 - 90.00)
= 354.623 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0009 ＜ 0.0100 (e' = e + Xp - dc = 433.532 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 70.00 = 280.000 mm
c = 600.00 / (600.00+400.00) x 280.000 = 168.000 mm, a = k1 x c = 142.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (280.00-168.00) / 168.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6542.504 kN ≥ Pn = 817.983 kN
ΦPn = 0.78 x 817.983 = 640.753 kN ≥ Pu = 377.858 kN ∴ O.K
ΦMn = ΦPn x 0.332 = 212.669 kN.m ≥ Mu = 125.412 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 280.00 = 184.687 kN
≥ Vu (= 151.802 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 433.333 |  | 363.333 |  | 346.988 |  | 128.901 |  | 151.327 |  | 371.486
＊ 철근비 검토
As = 1301.200 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA + H13- 4.0EA , d1 = 70.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0056) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 433.3 x 1000.0 = 8840000.0 N
Cs = As x fy = 520480.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (8840000.0 x 216.67 + 520480.0 x 70.000 + 458400.0 x 343.333) / 9818880.0
= 214.806 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 218.000 mm, ab = k1 x cb = 185.300 mm
fs' = 600 x (218.000 - 90.000) / 218.000 (≤fy) = 352.294 MPa
Cc = 0.85 x 24.0 x 185.300 x 1000.000 = 3780.120 kN
Cs = As' x (fs' - 0.85 x fck) = 380.350 kN
Ts = As x fs = 520.480 kN
Pb = 3780.120 + 380.350 - 520.480 = 3639.990 kN
Mb = 3780.120 x (363.333 - 185.300/2) + 380.350 x (363.333 - 90.00)
- 3639.990 x (214.806 - 70.000)
= 600.087 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 164.859 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 81.766 mm, a = k1 x c = 69.501 mm 를 사용.
fs = 600 x (363.333 - 81.766) / 81.766 (≤fy) = 400.000 MPa
fs' = 600 x ( 81.766 - 90.000) / 81.766 (≤fy) = 17.546 MPa
Cc = 0.85 x 24.0 x 69.501 x 1000.000 = 1417.824 kN
Cs = As' x (fs' - 0.85 x fck) = -3.271 kN
Ts = As x fs = 520.480 kN
Pn = 1417.824 + -3.271 - 520.480 = 900.615 kN
Mn' = 1417.824 x (363.333 - 69.501/2) + -3.271 x (363.333 - 90.00)
= 464.978 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0011 ＜ 0.0100 (e' = e + Xp - dc = 516.291 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 70.00 = 280.000 mm
c = 600.00 / (600.00+400.00) x 280.000 = 168.000 mm, a = k1 x c = 142.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (280.00-168.00) / 168.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7815.166 kN ≥ Pn = 900.615 kN
ΦPn = 0.78 x 900.615 = 705.481 kN ≥ Pu = 346.988 kN ∴ O.K
ΦMn = ΦPn x 0.371 = 262.076 kN.m ≥ Mu = 128.901 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 280.00 = 183.606 kN
≥ Vu (= 151.327 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 350 |  | 260 |  | 362.423 |  | 51.92 |  | 0 |  | 143.259
＊ 철근비 검토
As = 1146.000 mm² (인장중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0055) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 350.0 x 1000.0 = 7140000.0 N
Cs = As x fy = 458400.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (7140000.0 x 175.00 + 458400.0 x 90.000 + 317760.0 x 280.000) / 7916160.0
= 174.293 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 156.000 mm, ab = k1 x cb = 132.600 mm
fs' = 600 x (156.000 - 70.000) / 156.000 (≤fy) = 330.769 MPa
Cc = 0.85 x 24.0 x 132.600 x 1000.000 = 2705.040 kN
Cs = As' x (fs' - 0.85 x fck) = 246.557 kN
Ts = As x fs = 458.400 kN
Pb = 2705.040 + 246.557 - 458.400 = 2493.197 kN
Mb = 2705.040 x (260.000 - 132.600/2) + 246.557 x (260.000 - 70.00)
- 2493.197 x (174.293 - 90.000)
= 360.654 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 144.655 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 157.009 mm, a = k1 x c = 133.458 mm 를 사용.
fs = 600 x (260.000 - 157.009) / 157.009 (≤fy) = 393.572 MPa
fs' = 600 x (157.009 - 70.000) / 157.009 (≤fy) = 332.500 MPa
Cc = 0.85 x 24.0 x 133.458 x 1000.000 = 2722.541 kN
Cs = As' x (fs' - 0.85 x fck) = 247.932 kN
Ts = As x fs = 451.033 kN
Pn = 2722.541 + 247.932 - 451.033 = 2519.440 kN
Mn' = 2722.541 x (260.000 - 133.458/2) + 247.932 x (260.000 - 70.00)
= 573.295 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0026 ＜ 0.0100 (e' = e + Xp - dc = 227.551 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 90.00 = 260.000 mm
c = 600.00 / (600.00+400.00) x 260.000 = 156.000 mm, a = k1 x c = 132.600 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (260.00-156.00) / 156.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6301.261 kN ≥ Pn = 2519.440 kN
ΦPn = 0.78 x 2519.440 = 1973.561 kN ≥ Pu = 362.423 kN ∴ O.K
ΦMn = ΦPn x 0.143 = 282.730 kN.m ≥ Mu = 51.920 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 260.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 260.00 = 170.993 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 350 |  | 280 |  | 362.423 |  | 35.136 |  | 0 |  | 96.949
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0055) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 350.0 x 1000.0 = 7140000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (7140000.0 x 175.00 + 317760.0 x 70.000 + 458400.0 x 260.000) / 7916160.0
= 175.707 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 168.000 mm, ab = k1 x cb = 142.800 mm
fs' = 600 x (168.000 - 90.000) / 168.000 (≤fy) = 278.571 MPa
Cc = 0.85 x 24.0 x 142.800 x 1000.000 = 2913.120 kN
Cs = As' x (fs' - 0.85 x fck) = 295.864 kN
Ts = As x fs = 317.760 kN
Pb = 2913.120 + 295.864 - 317.760 = 2891.224 kN
Mb = 2913.120 x (280.000 - 142.800/2) + 295.864 x (280.000 - 90.00)
- 2891.224 x (175.707 - 70.000)
= 358.268 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 123.915 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 203.267 mm, a = k1 x c = 172.777 mm 를 사용.
fs = 600 x (280.000 - 203.267) / 203.267 (≤fy) = 226.501 MPa
fs' = 600 x (203.267 - 90.000) / 203.267 (≤fy) = 334.339 MPa
Cc = 0.85 x 24.0 x 172.777 x 1000.000 = 3524.643 kN
Cs = As' x (fs' - 0.85 x fck) = 359.774 kN
Ts = As x fs = 179.932 kN
Pn = 3524.643 + 359.774 - 179.932 = 3704.485 kN
Mn' = 3524.643 x (280.000 - 172.777/2) + 359.774 x (280.000 - 90.00)
= 750.769 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0091 ＜ 0.0100 (e' = e + Xp - dc = 202.656 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 70.00 = 280.000 mm
c = 600.00 / (600.00+400.00) x 280.000 = 168.000 mm, a = k1 x c = 142.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (280.00-168.00) / 168.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6301.261 kN ≥ Pn = 3704.485 kN
ΦPn = 0.78 x 3704.485 = 2901.846 kN ≥ Pu = 362.423 kN ∴ O.K
ΦMn = ΦPn x 0.097 = 281.330 kN.m ≥ Mu = 35.136 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 280.00 = 184.146 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 350 |  | 280 |  | 377.858 |  | 125.412 |  | 151.802 |  | 331.904
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0078) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 350.0 x 1000.0 = 7140000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (7140000.0 x 175.00 + 635520.0 x 70.000 + 458400.0 x 260.000) / 8233920.0
= 171.628 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 168.000 mm, ab = k1 x cb = 142.800 mm
fs' = 600 x (168.000 - 90.000) / 168.000 (≤fy) = 278.571 MPa
Cc = 0.85 x 24.0 x 142.800 x 1000.000 = 2913.120 kN
Cs = As' x (fs' - 0.85 x fck) = 295.864 kN
Ts = As x fs = 635.520 kN
Pb = 2913.120 + 295.864 - 635.520 = 2573.464 kN
Mb = 2913.120 x (280.000 - 142.800/2) + 295.864 x (280.000 - 90.00)
- 2573.464 x (171.628 - 70.000)
= 402.355 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 156.348 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 83.740 mm, a = k1 x c = 71.179 mm 를 사용.
fs = 600 x (280.000 - 83.740) / 83.740 (≤fy) = 400.000 MPa
fs' = 600 x ( 83.740 - 90.000) / 83.740 (≤fy) = 19.137 MPa
Cc = 0.85 x 24.0 x 71.179 x 1000.000 = 1452.056 kN
Cs = As' x (fs' - 0.85 x fck) = -1.447 kN
Ts = As x fs = 635.520 kN
Pn = 1452.056 + -1.447 - 635.520 = 817.983 kN
Mn' = 1452.056 x (280.000 - 71.179/2) + -1.447 x (280.000 - 90.00)
= 354.623 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0009 ＜ 0.0100 (e' = e + Xp - dc = 433.532 mm)
＊ 강도감소계수(Φ) 산정
dt = 350.00 - 70.00 = 280.000 mm
c = 600.00 / (600.00+400.00) x 280.000 = 168.000 mm, a = k1 x c = 142.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (280.00-168.00) / 168.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6542.504 kN ≥ Pn = 817.983 kN
ΦPn = 0.78 x 817.983 = 640.753 kN ≥ Pu = 377.858 kN ∴ O.K
ΦMn = ΦPn x 0.332 = 212.669 kN.m ≥ Mu = 125.412 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 280.00 = 184.687 kN
≥ Vu (= 151.802 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 500 |  | × | 0.002 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
2) 상부슬래브 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 500 |  | × | 0.002 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 388.080 ----------> O.K !!!
3) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 500 |  | × | 0.002 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
4) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 500 |  | × | 0.002 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
5) 하부슬래브 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 500 |  | × | 0.002 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
6) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 500 |  | × | 0.002 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
7) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
8) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 229.200 ----------> O.K !!!
9) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 229.200 ----------> O.K !!!
10) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
11) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
12) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 229.200 ----------> O.K !!!
13) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 229.200 ----------> O.K !!!
14) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.0025 |  | = | 875 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 875.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!

## 절점부 검토
21. 절점부 검토
1) 절점 21
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 81.203 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 81.203 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 777.817 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 81.20 × 10^6 |  |  | = | 0.671 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 777.817²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 81.20 × 10^6 |  |  | = | 1159.980 mm²
|  |  |  | R × fsa |  |  | 777.817 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1159.980 mm² - 506.800 mm²
[5 empty] | = | 653.180 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @250 - 4EA
∴ Total As = 1146.000 mm² > Req'd As (= 653.180 mm²) -------------> O.K !!!
2) 절점 1
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 78.492 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 78.492 kN.m
R = √(T1² + T2²) = 610.328 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 78.49 × 10^6 |  |  | = | 1.054 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 610.328²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 78.49 × 10^6 |  |  | = | 1428.956 mm²
|  |  |  | R × fsa |  |  | 610.328 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1428.956 mm² - 794.400 mm²
[5 empty] | = | 634.556 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @250 - 4EA
∴ Total As = 1146.000 mm² > Req'd As (= 634.556 mm²) -------------> O.K !!!
3) 절점 15
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 81.203 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 81.203 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 777.817 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 81.20 × 10^6 |  |  | = | 0.671 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 777.817²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 81.20 × 10^6 |  |  | = | 1159.980 mm²
|  |  |  | R × fsa |  |  | 777.817 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1159.980 mm² - 506.800 mm²
[5 empty] | = | 653.180 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @250 - 4EA
∴ Total As = 1146.000 mm² > Req'd As (= 653.180 mm²) -------------> O.K !!!
4) 절점 10
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 78.492 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 78.492 kN.m
R = √(T1² + T2²) = 610.328 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 78.49 × 10^6 |  |  | = | 1.054 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 610.328²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 78.49 × 10^6 |  |  | = | 1428.956 mm²
|  |  |  | R × fsa |  |  | 610.328 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1428.956 mm² - 794.400 mm²
[5 empty] | = | 634.556 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @250 - 4EA
∴ Total As = 1146.000 mm² > Req'd As (= 634.556 mm²) -------------> O.K !!!

## 사용성 검토
22. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 513.333 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 455.749 | O.K |  | 3.646
2 | 상부슬래브 : 중앙부 |  | 410 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 358.472 | O.K |  | 2.868
3 | 상부슬래브 : 단지점부(우측) |  | 513.333 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 455.749 | O.K |  | 3.646
4 | 하부슬래브 : 단지점부(좌측) |  | 430 |  | H16 - 8.0EA |  |  | 125 | 484.041 | O.K |  | 3.872
5 | 하부슬래브 : 중앙부 |  | 410 |  | H16 - 8.0EA |  |  | 125 | 307.823 | O.K |  | 2.463
6 | 하부슬래브 : 단지점부(우측) |  | 430 |  | H16 - 8.0EA |  |  | 125 | 484.041 | O.K |  | 3.872
7 | 좌측벽체 : 상부 |  | 363.333 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 272.886 | O.K |  | 2.183
8 | 좌측벽체 : 중앙부 |  | 260 |  | H19 - 4.0EA |  |  | 250 | 488.844 | O.K |  | 1.955
9 | 좌측벽체 : 중앙부(부모멘트) |  | 280 |  | H16 - 4.0EA |  |  | 250 | 576.49 | O.K |  | 2.306
10 | 좌측벽체 : 하부 |  | 280 |  | H16 - 8.0EA |  |  | 125 | 254.89 | O.K |  | 2.039
11 | 우측벽체 : 상부 |  | 363.333 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 272.886 | O.K |  | 2.183
12 | 우측벽체 : 중앙부 |  | 260 |  | H19 - 4.0EA |  |  | 250 | 488.844 | O.K |  | 1.955
13 | 우측벽체 : 중앙부(부모멘트) |  | 280 |  | H16 - 4.0EA |  |  | 250 | 576.49 | O.K |  | 2.306
14 | 우측벽체 : 하부 |  | 280 |  | H16 - 8.0EA |  |  | 125 | 254.89 | O.K |  | 2.039
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 81.203 x 1000000 / [1301.200 x (513.333 - 88.022/3)]
= 128.940 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x513.3/(7x1301.200)]
= 88.022 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 128.94) - 2.5 x 62.00 = 455.75 mm
300 x (210 / fs) = 300 x (210 / 128.94) = 488.60 mm
Sa는 작은 값인 455.75 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 455.75 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 103.485 x 1000000 / [1940.400 x (410.000 - 92.824/3)]
= 140.695 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x410.0/(7x1940.400)]
= 92.824 mm
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 140.69) - 2.5 x 80.50 = 358.47 mm
300 x (210 / fs) = 300 x (210 / 140.69) = 447.78 mm
Sa는 작은 값인 358.47 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 358.47 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 81.203 x 1000000 / [1301.200 x (513.333 - 88.022/3)]
= 128.940 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x513.3/(7x1301.200)]
= 88.022 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 128.94) - 2.5 x 62.00 = 455.75 mm
300 x (210 / fs) = 300 x (210 / 128.94) = 488.60 mm
Sa는 작은 값인 455.75 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 455.75 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 78.492 x 1000000 / [1588.800 x (430.000 - 87.307/3)]
= 123.232 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x430.0/(7x1588.800)]
= 87.307 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 123.23) - 2.5 x 62.00 = 484.04 mm
300 x (210 / fs) = 300 x (210 / 123.23) = 511.23 mm
Sa는 작은 값인 484.04 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 484.04 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 93.117 x 1000000 / [1588.800 x (410.000 - 85.021/3)]
= 153.562 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x410.0/(7x1588.800)]
= 85.021 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 153.56) - 2.5 x 82.00 = 307.82 mm
300 x (210 / fs) = 300 x (210 / 153.56) = 410.26 mm
Sa는 작은 값인 307.82 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 307.82 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 78.492 x 1000000 / [1588.800 x (430.000 - 87.307/3)]
= 123.232 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x430.0/(7x1588.800)]
= 87.307 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 123.23) - 2.5 x 62.00 = 484.04 mm
300 x (210 / fs) = 300 x (210 / 123.23) = 511.23 mm
Sa는 작은 값인 484.04 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 484.04 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 81.203 x 1000000 / [1301.200 x (363.333 - 72.756/3)]
= 184.044 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x363.3/(7x1301.200)]
= 72.756 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 184.04) - 2.5 x 62.00 = 272.89 mm
300 x (210 / fs) = 300 x (210 / 184.04) = 342.31 mm
Sa는 작은 값인 272.89 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 272.89 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 31.514 x 1000000 / [1146.000 x (260.000 - 57.061/3)]
= 114.115 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1146.000/1000.0 + 7x1146.000/1000.0 x √[(1 + 2x1000.0x260.0/(7x1146.000)]
= 57.061 mm
Use As = 1146.000 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA (= 1146.000 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 114.11) - 2.5 x 80.50 = 488.84 mm
300 x (210 / fs) = 300 x (210 / 114.11) = 552.07 mm
Sa는 작은 값인 488.84 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 488.84 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 22.506 x 1000000 / [794.400 x (280.000 - 50.519/3)]
= 107.657 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x280.0/(7x794.400)]
= 50.519 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 107.66) - 2.5 x 62.00 = 576.49 mm
300 x (210 / fs) = 300 x (210 / 107.66) = 585.19 mm
Sa는 작은 값인 576.49 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 576.49 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 78.492 x 1000000 / [1588.800 x (280.000 - 68.576/3)]
= 192.125 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x280.0/(7x1588.800)]
= 68.576 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 192.12) - 2.5 x 62.00 = 254.89 mm
300 x (210 / fs) = 300 x (210 / 192.12) = 327.91 mm
Sa는 작은 값인 254.89 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 254.89 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 81.203 x 1000000 / [1301.200 x (363.333 - 72.756/3)]
= 184.044 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x363.3/(7x1301.200)]
= 72.756 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 184.04) - 2.5 x 62.00 = 272.89 mm
300 x (210 / fs) = 300 x (210 / 184.04) = 342.31 mm
Sa는 작은 값인 272.89 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 272.89 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 31.514 x 1000000 / [1146.000 x (260.000 - 57.061/3)]
= 114.115 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1146.000/1000.0 + 7x1146.000/1000.0 x √[(1 + 2x1000.0x260.0/(7x1146.000)]
= 57.061 mm
Use As = 1146.000 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA (= 1146.000 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 114.11) - 2.5 x 80.50 = 488.84 mm
300 x (210 / fs) = 300 x (210 / 114.11) = 552.08 mm
Sa는 작은 값인 488.84 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 488.84 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 22.506 x 1000000 / [794.400 x (280.000 - 50.519/3)]
= 107.657 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x280.0/(7x794.400)]
= 50.519 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 107.66) - 2.5 x 62.00 = 576.49 mm
300 x (210 / fs) = 300 x (210 / 107.66) = 585.19 mm
Sa는 작은 값인 576.49 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 576.49 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 78.492 x 1000000 / [1588.800 x (280.000 - 68.576/3)]
= 192.125 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x280.0/(7x1588.800)]
= 68.576 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 192.12) - 2.5 x 62.00 = 254.89 mm
300 x (210 / fs) = 300 x (210 / 192.12) = 327.91 mm
Sa는 작은 값인 254.89 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 254.89 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 2.850 m
- fy = 400 MPa
- 부재두께(T) = 0.50 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 2.850 / 28
T = 0.102 m < 0.500 m -----------> O.K

## 기초 지지력 검토
23. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  | = | 122.806 |  | / | 3.2 |  | = | 38.377 |  | kN/m²
|  |  | - 상부연직하중 |  |  | = | 152 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  | 10 |  | kN/m²
3) 내부 수압
|  |  | - 암거내부수압 |  |  | = | 20 |  | kN/m²
4) 최대 지반 반력
|  |  | Qmax | = | 38.377 |  | + | 152 |  | + | 10 |  | + | 20
|  |  |  | = | 220.377 |  | kN/m²

## 주철근 조립도
24. 주철근 조립도