## 표지
H1-7A 구조계산서
| ▣ 구조형식 |  | : | 지중 1 련 암거1
( 내공 : 2M ⅹ 2M )
| ▣ 토 피(FH) |  | = | 3.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 절점부 검토
[5 empty] | 22. | 사용성 검토
[5 empty] | 23. | 기초 지지력 검토
[5 empty] | 24. | 주철근 조립도

## 설계요약표
1. 설계 요약표
H1-7A (토피=3.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 3.0m
안정(지지력)검토 | Qmax = 110.739 kN/m²
단면 위치 | 내구성검토 |  | 단 면 검 토 | [7 empty] | 절 점 부 보 강
| 균열검토 |  | 휨 검 토 |  |  |  | 전 단 검 토
| 철근간격 mm | 최대간격 mm | 사용철근 | Mu kN.m | ΦMn kN.m | S.F | 사용철근 | Vu kN | ΦVn kN | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 664.961 | H13 - 8.0EA | 41.815 | 98.814 | 2.36 | ∴ 전단보강 불필요 |  |  | O.K | 0.416 | 0.637
상부슬래브 : 중앙부 | 125 | 356.183 | H13 - 8.0EA | 42.705 | 68.946 | 1.61 | ∴ 전단보강 불필요 |  |  | O.K
상부슬래브 : 단지점부(우측) | 125 | 664.961 | H13 - 8.0EA | 41.815 | 98.814 | 2.36 | ∴ 전단보강 불필요 |  |  | O.K | 0.416 | 0.637
하부슬래브 : 단지점부(좌측) | 125 | 527.478 | H13 - 8.0EA | 39.756 | 75.839 | 1.91 | ∴ 전단보강 불필요 |  |  | O.K | 0.689 | 0.637 | H13 @250 - 4EA
하부슬래브 : 중앙부 | 125 | 486.691 | H16 - 4.0EA + H13 - 4.0EA | 44.185 | 87.262 | 1.97 | ∴ 전단보강 불필요 |  |  | O.K
하부슬래브 : 단지점부(우측) | 125 | 527.478 | H13 - 8.0EA | 39.756 | 75.839 | 1.91 | ∴ 전단보강 불필요 |  |  | O.K | 0.689 | 0.637 | H13 @250 - 4EA
좌측벽체 : 상부 | 125 | 664.961 | H13 - 8.0EA | 41.815 | 185.291 | 4.43 | ∴ 전단보강 불필요 |  |  | O.K
좌측벽체 : 중앙부 | 250 | 921.92 | H13 - 4.0EA | 12.13 | 195.4 | 16.11 | ∴ 전단보강 불필요 |  |  | O.K
좌측벽체 : 중앙부(부모멘트) | 125 | 1013.967 | H13 - 8.0EA | 20.836 | 191.571 | 9.19 | ∴ 전단보강 불필요 |  |  | O.K
좌측벽체 : 하부 | 125 | 527.478 | H13 - 8.0EA | 39.756 | 142.048 | 3.57 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 상부 | 125 | 664.961 | H13 - 8.0EA | 41.815 | 185.291 | 4.43 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 중앙부 | 250 | 921.921 | H13 - 4.0EA | 12.13 | 195.4 | 16.11 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 중앙부(부모멘트) | 125 | 1013.967 | H13 - 8.0EA | 20.836 | 191.571 | 9.19 | ∴ 전단보강 불필요 |  |  | O.K
우측벽체 : 하부 | 125 | 527.478 | H13 - 8.0EA | 39.756 | 142.048 | 3.57 | ∴ 전단보강 불필요 |  |  | O.K

## 설계조건
2. 설계조건
1) 구조형식
- 지중 1 련 암거1 ( 내공 : 2M ⅹ 2M, 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 11.355 |  | kN/m² |  | (∵ 토피 : | 3 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 1~24
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.15 | 0.15 | 16 |  | 2.07 |  | 2.45
| 2 |  | 0.3 | 0.15 | 17 |  | 1.3 |  | 2.45
| 3 |  | 0.53 | 0.15 | 18 |  | 0.53 |  | 2.45
| 4 |  | 0.725 | 0.15 | 19 |  | 0.3 |  | 2.45
| 5 |  | 1.3 | 0.15 | 20 |  | 0.15 |  | 2.45
| 6 |  | 1.875 | 0.15 | 21 |  | 0.15 |  | 2.3
| 7 |  | 2.07 | 0.15 | 22 |  | 0.15 |  | 2.07
| 8 |  | 2.3 | 0.15 | 23 |  | 0.15 |  | 0.53
| 9 |  | 2.45 | 0.15 | 24 |  | 0.15 |  | 0.3
| 10 |  | 2.45 | 0.3 | 25 |  | 0.15 |  | -0.35
| 11 |  | 2.45 | 0.53 | 26 |  | 0.725 |  | -0.35
| 12 |  | 2.45 | 2.07 | 27 |  | 1.3 |  | -0.35
| 13 |  | 2.45 | 2.3 | 28 |  | 1.875 |  | -0.35
| 14 |  | 2.45 | 2.45 | 29 |  | 2.45 |  | -0.35
| 15 |  | 2.3 | 2.45

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 1~32
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.15 | 0.15 | 27 |  | 0.15 |  | 2.07
| 2 |  | 0.3 | 0.15 | 28 |  | 0.15 |  | 1.875
| 3 |  | 0.53 | 0.15 | 29 |  | 0.15 |  | 1.3
| 4 |  | 0.725 | 0.15 | 30 |  | 0.15 |  | 0.725
| 5 |  | 1.3 | 0.15 | 31 |  | 0.15 |  | 0.53
| 6 |  | 1.875 | 0.15 | 32 |  | 0.15 |  | 0.3
| 7 |  | 2.07 | 0.15 | 33 |  | 0.15 |  | -0.35
| 8 |  | 2.3 | 0.15 | 34 |  | 0.725 |  | -0.35
| 9 |  | 2.45 | 0.15 | 35 |  | 1.3 |  | -0.35
| 10 |  | 2.45 | 0.3 | 36 |  | 1.875 |  | -0.35
| 11 |  | 2.45 | 0.53 | 37 |  | 2.45 |  | -0.35
| 12 |  | 2.45 | 0.725 | 38 |  | 2.95 |  | 0.15
| 13 |  | 2.45 | 1.3 | 39 |  | 2.95 |  | 0.725
| 14 |  | 2.45 | 1.875 | 40 |  | 2.95 |  | 1.3
| 15 |  | 2.45 | 2.07 | 41 |  | 2.95 |  | 1.875
| 16 |  | 2.45 | 2.3 | 42 |  | 2.95 |  | 2.45
| 17 |  | 2.45 | 2.45 | 43 |  | 2.45 |  | 2.95
| 18 |  | 2.3 | 2.45 | 44 |  | 1.875 |  | 2.95
| 19 |  | 2.07 | 2.45 | 45 |  | 1.3 |  | 2.95
| 20 |  | 1.875 | 2.45 | 46 |  | 0.725 |  | 2.95
| 21 |  | 1.3 | 2.45 | 47 |  | 0.15 |  | 2.95
| 22 |  | 0.725 | 2.45 | 48 |  | -0.35 |  | 2.45
| 23 |  | 0.53 | 2.45 | 49 |  | -0.35 |  | 1.875
| 24 |  | 0.3 | 2.45 | 50 |  | -0.35 |  | 1.3
| 25 |  | 0.15 | 2.45 | 51 |  | -0.35 |  | 0.725
| 26 |  | 0.15 | 2.3 | 52 |  | -0.35 |  | 0.15

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 2.600 × 2.600 ) |  |  | = | 2.6 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 2.600 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 27716.537 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.300/2 + 0.575/2) = 12126 kN/m |  |  |  |  | 1,9
| Kv2 |  |  | Kvⅹ(0.575/2 + 0.575/2) = 15937 kN/m |  |  |  |  | 4~6
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 2.300m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 2.600 × 2.600 ) |  |  |  |  | = | 2.6 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 2.600 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 69727.42 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 69727.420 |  |  |  |  | = | 23242.47 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 2.600 × 2.600 ) |  |  |  |  | = | 2.6 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 2.600 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 69727.42 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 69727.420 |  |  |  |  | = | 23242.47 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 2.600 × 2.600 ) |  |  |  |  | = | 2.6 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 2.600 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 69727.42 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 69727.420 |  |  |  |  | = | 23242.47 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.575/2 + 0.300/2) = 30506 kN/m | [8 empty] | 17,25
|  | Ksb1 |  |  | Ksbⅹ(0.575/2 + 0.300/2) = 10169 kN/m
|  | Kv2 |  |  | Kvⅹ(0.575/2 + 0.575/2) = 40093 kN/m | [8 empty] | 20~22
|  | Ksb2 |  |  | Ksbⅹ(0.575/2 + 0.575/2) = 13364 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(0.575/2 + 0.300/2) = 30506 kN/m | [8 empty] | 1,9,17,25
|  | Kss1 |  |  | Kssⅹ(0.575/2 + 0.300/2) = 10169 kN/m
|  | Kh2 |  |  | Khⅹ(0.575/2 + 0.575/2) = 40093 kN/m | [8 empty] | 12~14,28~30
|  | Kss2 |  |  | Kssⅹ(0.575/2 + 0.575/2) = 13364 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.300/2 + 0.575/2) = 30506 kN/m | [8 empty] | 1,9
|  | Ksb1 |  |  | Ksbⅹ(0.300/2 + 0.575/2) = 10169 kN/m
|  | Kv2 |  |  | Kvⅹ(0.575/2 + 0.575/2) = 40093 kN/m | [8 empty] | 4~6
|  | Ksb2 |  |  | Ksbⅹ(0.575/2 + 0.575/2) = 13364 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 3.00 × 19.00 |  |  |  |  | = | 57 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 57 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 충격계수
|  | 토피두께 D(m) |  |  |  | 0.15 ≤ D ≤ 1 |  |  | 1 < D ≤ 2 |  |  | 2 < D ≤ 3 | 3 < D
|  | 충격계수 i |  |  |  | 0.3 |  |  | 0.2 |  |  | 0.1 | 0
i = 0.1 ( 토피 D = 3.00 m )
② 상부 슬래브에 작용하는 하중 (Wl1)
- Pr = 96.0 kN/m
- Wl1 = Pr × ( 1 + i ) /(1.5 × W1) = 96.0 × ( 1 + 0.1 ) / 9.3 = 11.355 kN/m²
③ 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (3.150 × 19.000) × 0.500 | [9 empty] | = | 29.925 | kN/m²
|  | - Wh2 |  | = | 29.925 + 0.150 × 19.000 × 0.500 | [9 empty] | = | 31.35 | kN/m²
|  | - Wh3 |  | = | 31.350 + 0.230 × 19.000 × 0.500 | [9 empty] | = | 33.535 | kN/m²
|  | - Wh4 |  | = | 33.535 + 1.540 × 19.000 × 0.500 | [9 empty] | = | 48.165 | kN/m²
|  | - Wh5 |  | = | 48.165 + 0.230 × 19.000 × 0.500 | [9 empty] | = | 50.35 | kN/m²
|  | - Wh6 |  | = | 50.350 + 0.150 × 19.000 × 0.500 | [9 empty] | = | 51.775 | kN/m²
5) 암거1내부수압
- Win = 16.000 kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 5.3 |  | 197.3 |  |  |  | 19 |  |  | 0.107
|  | 계 | [11 empty] | 0.107
Tg = 1.25 Tg' = 1.25 × 0.107 = 0.134 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.134 / 2π × 2.617 = 0.056 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 3.15 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 5.45 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.056 × 0.134 × cos(π× 3.150 / (2 × 30.000)) = 0.001500
U(Zb) = 2 / π²× 0.056 × 0.134 × cos(π× 5.450 / (2 × 30.000)) = 0.001459
Po = Ksb,top × (U(Zu) - U(Zb))
= 23242.470 × (0.001500 - 0.001459) = 0.953 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 3.15 |  | 69727.42 |  |  |  | 0.0015 |  |  |  |  | 4.1e-05 |  | 2.859
|  | 3.3 |  | 69727.42 |  |  |  | 0.001498 |  |  |  |  | 3.9e-05 |  | 2.719
|  | 3.53 |  | 69727.42 |  |  |  | 0.001495 |  |  |  |  | 3.6e-05 |  | 2.51
|  | 3.725 |  | 69727.42 |  |  |  | 0.001492 |  |  |  |  | 3.3e-05 |  | 2.301
|  | 4.3 |  | 69727.42 |  |  |  | 0.001482 |  |  |  |  | 2.3e-05 |  | 1.604
|  | 4.875 |  | 69727.42 |  |  |  | 0.001471 |  |  |  |  | 1.2e-05 |  | 0.837
|  | 5.07 |  | 69727.42 |  |  |  | 0.001467 |  |  |  |  | 8e-06 |  | 0.558
|  | 5.3 |  | 69727.42 |  |  |  | 0.001462 |  |  |  |  | 3e-06 |  | 0.209
|  | 5.45 |  | 69727.42 |  |  |  | 0.001459 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000013 = 0.250 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000022 = 0.420 kN/m²
Vs = (Vu - Vb) / 2 = (0.250 + 0.420) / 2 = 0.340 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.150) = 1.120 kN/m²
② 하부슬래브
fb = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.450) = 1.080 kN/m²
③ 측벽
f1 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.150) = 1.120 kN/m²
f2 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.300) = 1.118 kN/m²
f3 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.530) = 1.114 kN/m²
f4 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.725) = 1.110 kN/m²
f5 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 4.300) = 1.100 kN/m²
f6 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 4.875) = 1.090 kN/m²
f7 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.070) = 1.087 kN/m²
f8 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.300) = 1.083 kN/m²
f9 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.450) = 1.080 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)
6) CASE6 - 암거내부수압

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 0.975, h = 3.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.56 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.56 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.56 | 1.6 | 0.8 | 0.8
2) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.975 | 1 | 1 | 1
| 2 |  | 1 | 0.975 |  | 1 | 1
| 3 |  | 1 | 0.975 | 1 | 0.5 | 0.5
3) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.975 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | NLLINK
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 1 J=1,25 NLP=SP1 ANG=0
2 J=4,26 NLP=SP2 ANG=0
| JOINT | 3 J=5,27 NLP=SP2 ANG=0
| 1 X= 0.150 Y= 0.000 Z= 0.150 | 4 J=6,28 NLP=SP2 ANG=0
| 2 X= 0.300 Y= 0.000 Z= 0.150 | 5 J=9,29 NLP=SP1 ANG=0
3 X= 0.530 Y= 0.000 Z= 0.150
| 4 X= 0.725 Y= 0.000 Z= 0.150 | LOAD
| 5 X= 1.300 Y= 0.000 Z= 0.150 | NAME=SELFWGT SW=1
| 6 X= 1.875 Y= 0.000 Z= 0.150 | NAME=NWDEAD
| 7 X= 2.070 Y= 0.000 Z= 0.150 | TYPE=Distributed Span
| 8 X= 2.300 Y= 0.000 Z= 0.150 | ADD=14 RD=0,1 UZ=-57,-57
| 9 X= 2.450 Y= 0.000 Z= 0.150 | ADD=15 RD=0,1 UZ=-57,-57
| 10 X= 2.450 Y= 0.000 Z= 0.300 | ADD=16 RD=0,1 UZ=-57,-57
| 11 X= 2.450 Y= 0.000 Z= 0.530 | ADD=17 RD=0,1 UZ=-57,-57
| 12 X= 2.450 Y= 0.000 Z= 2.070 | ADD=18 RD=0,1 UZ=-57,-57
| 13 X= 2.450 Y= 0.000 Z= 2.300 | ADD=19 RD=0,1 UZ=-57,-57
| 14 X= 2.450 Y= 0.000 Z= 2.450 | NAME=LIVEFULL
| 15 X= 2.300 Y= 0.000 Z= 2.450 | TYPE=Distributed Span
| 16 X= 2.070 Y= 0.000 Z= 2.450 | ADD=14 RD=0,1 UZ=-11.3548,-11.3548
| 17 X= 1.300 Y= 0.000 Z= 2.450 | ADD=15 RD=0,1 UZ=-11.3548,-11.3548
| 18 X= 0.530 Y= 0.000 Z= 2.450 | ADD=16 RD=0,1 UZ=-11.3548,-11.3548
| 19 X= 0.300 Y= 0.000 Z= 2.450 | ADD=17 RD=0,1 UZ=-11.3548,-11.3548
| 20 X= 0.150 Y= 0.000 Z= 2.450 | ADD=18 RD=0,1 UZ=-11.3548,-11.3548
| 21 X= 0.150 Y= 0.000 Z= 2.300 | ADD=19 RD=0,1 UZ=-11.3548,-11.3548
| 22 X= 0.150 Y= 0.000 Z= 2.070 | NAME=HORLIVE
| 23 X= 0.150 Y= 0.000 Z= 0.530 | TYPE=Distributed Span
| 24 X= 0.150 Y= 0.000 Z= 0.300 | ADD=9 RD=0,1 UX=-5,-5
| 25 X= 0.150 Y= 0.000 Z= -0.350 | ADD=10 RD=0,1 UX=-5,-5
| 26 X= 0.725 Y= 0.000 Z= -0.350 | ADD=11 RD=0,1 UX=-5,-5
| 27 X= 1.300 Y= 0.000 Z= -0.350 | ADD=12 RD=0,1 UX=-5,-5
| 28 X= 1.875 Y= 0.000 Z= -0.350 | ADD=13 RD=0,1 UX=-5,-5
| 29 X= 2.450 Y= 0.000 Z= -0.350 | ADD=20 RD=0,1 UX=5,5
ADD=21 RD=0,1 UX=5,5
| RESTRAINT | ADD=22 RD=0,1 UX=5,5
| ADD=25 DOF=U1, U2, U3, R1, R2, R3 | ADD=23 RD=0,1 UX=5,5
| ADD=26 DOF=U1, U2, U3, R1, R2, R3 | ADD=24 RD=0,1 UX=5,5
| ADD=27 DOF=U1, U2, U3, R1, R2, R3 | NAME=NWSOFULL
| ADD=28 DOF=U1, U2, U3, R1, R2, R3 | TYPE=Distributed Span
| ADD=29 DOF=U1, U2, U3, R1, R2, R3 | ADD=9 RD=0,1 UX=-51.775,-50.35
ADD=10 RD=0,1 UX=-50.35,-48.165
| SPRING | ADD=11 RD=0,1 UX=-48.165,-33.535
| ADD=1 U1=1e+010 | ADD=12 RD=0,1 UX=-33.535,-31.35
ADD=13 RD=0,1 UX=-31.35,-29.925
| MATERIAL | ADD=20 RD=0,1 UX=29.925,31.35
| NAME=CONC IDES=C M=0.0001 W=24.5 | ADD=21 RD=0,1 UX=31.35,33.535
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | ADD=22 RD=0,1 UX=33.535,48.165
ADD=23 RD=0,1 UX=48.165,50.35
| NLPROP | ADD=24 RD=0,1 UX=50.35,51.775
| NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | NAME=INWATER
| DOF=U1 KE=12126 CE=0.99999 K=12126 OPEN=0 | TYPE=Distributed Span
| NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=2 RD=0,1 UZ=-16,-16
| DOF=U1 KE=15937 CE=0.99999 K=15937 OPEN=0 | ADD=3 RD=0,1 UZ=-16,-16
ADD=4 RD=0,1 UZ=-16,-16
| FRAME SECTION | ADD=5 RD=0,1 UZ=-16,-16
| NAME=1 MAT=CONC SH=R T=0.3, 1 | ADD=6 RD=0,1 UZ=-16,-16
ADD=7 RD=0,1 UZ=-16,-16
FRAME
| 1 J= 1, 2 SEC=1 NSEG=1 ANG=180 | MODE
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | TYPE=RITZ N=50
| 3 J= 3, 4 SEC=1 NSEG=1 ANG=180 | LOAD=SELFWGT
| 4 J= 4, 5 SEC=1 NSEG=2 ANG=180 | LOAD=NWDEAD
| 5 J= 5, 6 SEC=1 NSEG=2 ANG=180 | LOAD=LIVEFULL
| 6 J= 6, 7 SEC=1 NSEG=1 ANG=180 | LOAD=HORLIVE
| 7 J= 7, 8 SEC=1 NSEG=1 ANG=180 | LOAD=NWSOFULL
| 8 J= 8, 9 SEC=1 NSEG=1 ANG=180 | LOAD=INWATER
| 9 J= 9, 10 SEC=1 NSEG=1 ANG=0 | NLLINK=*
10 J= 10, 11 SEC=1 NSEG=1 ANG=0
| 11 J= 11, 12 SEC=1 NSEG=4 ANG=0 | HISTORY
| 12 J= 12, 13 SEC=1 NSEG=1 ANG=0 | NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| 13 J= 13, 14 SEC=1 NSEG=1 ANG=0 | LOAD=SELFWGT SF=1.2 AT=1
| 14 J= 14, 15 SEC=1 NSEG=1 ANG=0 | LOAD=NWDEAD SF=1.56 AT=1
| 15 J= 15, 16 SEC=1 NSEG=1 ANG=0 | LOAD=LIVEFULL SF=1.6 AT=1
| 16 J= 16, 17 SEC=1 NSEG=2 ANG=0 | LOAD=HORLIVE SF=1.6 AT=1
| 17 J= 17, 18 SEC=1 NSEG=2 ANG=0 | LOAD=NWSOFULL SF=1.6 AT=1
| 18 J= 18, 19 SEC=1 NSEG=1 ANG=0 | NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| 19 J= 19, 20 SEC=1 NSEG=1 ANG=0 | LOAD=SELFWGT SF=0.9 AT=1
| 20 J= 20, 21 SEC=1 NSEG=1 ANG=180 | LOAD=NWDEAD SF=1.56 AT=1
| 21 J= 21, 22 SEC=1 NSEG=1 ANG=180 | LOAD=HORLIVE SF=1.6 AT=1
| 22 J= 22, 23 SEC=1 NSEG=4 ANG=180 | LOAD=NWSOFULL SF=1.6 AT=1
| 23 J= 23, 24 SEC=1 NSEG=1 ANG=180 | NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| 24 J= 24, 1 SEC=1 NSEG=1 ANG=180 | LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.56 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.975 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
LOAD=INWATER SF=1 AT=1
NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.975 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
LOAD=INWATER SF=1 AT=1
NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.975 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=0.5 AT=1
LOAD=NWSOFULL SF=0.5 AT=1
LOAD=INWATER SF=1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
HIST=HIST3 SF=1
NAME=SERVICE TYPE=ENVE
HIST=HIST4 SF=1
HIST=HIST5 SF=1
HIST=HIST6 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | ADD=6 U1=13364.4
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | ADD=9 U1=10168.6 U3=10168.6
ADD=12 U3=13364.4
| JOINT | ADD=13 U3=13364.4
| 1 X= 0.150 Y= 0.000 Z= 0.150 | ADD=14 U3=13364.4
| 2 X= 0.300 Y= 0.000 Z= 0.150 | ADD=17 U1=10168.6 U3=10168.6
| 3 X= 0.530 Y= 0.000 Z= 0.150 | ADD=20 U1=13364.4
| 4 X= 0.725 Y= 0.000 Z= 0.150 | ADD=21 U1=13364.4
| 5 X= 1.300 Y= 0.000 Z= 0.150 | ADD=22 U1=13364.4
| 6 X= 1.875 Y= 0.000 Z= 0.150 | ADD=25 U1=10168.6 U3=10168.6
| 7 X= 2.070 Y= 0.000 Z= 0.150 | ADD=28 U3=13364.4
| 8 X= 2.300 Y= 0.000 Z= 0.150 | ADD=29 U3=13364.4
| 9 X= 2.450 Y= 0.000 Z= 0.150 | ADD=30 U3=13364.4
10 X= 2.450 Y= 0.000 Z= 0.300
| 11 X= 2.450 Y= 0.000 Z= 0.530 | MATERIAL
| 12 X= 2.450 Y= 0.000 Z= 0.725 | NAME=CONC IDES=C M=0.0001 W=24.5
| 13 X= 2.450 Y= 0.000 Z= 1.300 | T=0 E=2.7e+007 U=0.17 A=9.99e-006
14 X= 2.450 Y= 0.000 Z= 1.875
| 15 X= 2.450 Y= 0.000 Z= 2.070 | NLPROP
| 16 X= 2.450 Y= 0.000 Z= 2.300 | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 17 X= 2.450 Y= 0.000 Z= 2.450 | DOF=U1 KE=30505.7 CE=0.99999 K=30505.7 OPEN=0
| 18 X= 2.300 Y= 0.000 Z= 2.450 | NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 19 X= 2.070 Y= 0.000 Z= 2.450 | DOF=U1 KE=40093.3 CE=0.99999 K=40093.3 OPEN=0
20 X= 1.875 Y= 0.000 Z= 2.450
| 21 X= 1.300 Y= 0.000 Z= 2.450 | FRAME SECTION
| 22 X= 0.725 Y= 0.000 Z= 2.450 | NAME=1 MAT=CONC SH=R T=0.3, 1
23 X= 0.530 Y= 0.000 Z= 2.450
| 24 X= 0.300 Y= 0.000 Z= 2.450 | FRAME
| 25 X= 0.150 Y= 0.000 Z= 2.450 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 26 X= 0.150 Y= 0.000 Z= 2.300 | 2 J= 2, 3 SEC=1 NSEG=1 ANG=180
| 27 X= 0.150 Y= 0.000 Z= 2.070 | 3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 28 X= 0.150 Y= 0.000 Z= 1.875 | 4 J= 4, 5 SEC=1 NSEG=2 ANG=180
| 29 X= 0.150 Y= 0.000 Z= 1.300 | 5 J= 5, 6 SEC=1 NSEG=2 ANG=180
| 30 X= 0.150 Y= 0.000 Z= 0.725 | 6 J= 6, 7 SEC=1 NSEG=1 ANG=180
| 31 X= 0.150 Y= 0.000 Z= 0.530 | 7 J= 7, 8 SEC=1 NSEG=1 ANG=180
| 32 X= 0.150 Y= 0.000 Z= 0.300 | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| 33 X= 0.150 Y= 0.000 Z= -0.350 | 9 J= 9, 10 SEC=1 NSEG=1 ANG=0
| 34 X= 0.725 Y= 0.000 Z= -0.350 | 10 J= 10, 11 SEC=1 NSEG=1 ANG=0
| 35 X= 1.300 Y= 0.000 Z= -0.350 | 11 J= 11, 12 SEC=1 NSEG=1 ANG=0
| 36 X= 1.875 Y= 0.000 Z= -0.350 | 12 J= 12, 13 SEC=1 NSEG=2 ANG=0
| 37 X= 2.450 Y= 0.000 Z= -0.350 | 13 J= 13, 14 SEC=1 NSEG=2 ANG=0
| 38 X= 2.950 Y= 0.000 Z= 0.150 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=0
| 39 X= 2.950 Y= 0.000 Z= 0.725 | 15 J= 15, 16 SEC=1 NSEG=1 ANG=0
| 40 X= 2.950 Y= 0.000 Z= 1.300 | 16 J= 16, 17 SEC=1 NSEG=1 ANG=0
| 41 X= 2.950 Y= 0.000 Z= 1.875 | 17 J= 17, 18 SEC=1 NSEG=1 ANG=0
| 42 X= 2.950 Y= 0.000 Z= 2.450 | 18 J= 18, 19 SEC=1 NSEG=1 ANG=0
| 43 X= 2.450 Y= 0.000 Z= 2.950 | 19 J= 19, 20 SEC=1 NSEG=1 ANG=0
| 44 X= 1.875 Y= 0.000 Z= 2.950 | 20 J= 20, 21 SEC=1 NSEG=2 ANG=0
| 45 X= 1.300 Y= 0.000 Z= 2.950 | 21 J= 21, 22 SEC=1 NSEG=2 ANG=0
| 46 X= 0.725 Y= 0.000 Z= 2.950 | 22 J= 22, 23 SEC=1 NSEG=1 ANG=0
| 47 X= 0.150 Y= 0.000 Z= 2.950 | 23 J= 23, 24 SEC=1 NSEG=1 ANG=0
| 48 X= -0.350 Y= 0.000 Z= 2.450 | 24 J= 24, 25 SEC=1 NSEG=1 ANG=0
| 49 X= -0.350 Y= 0.000 Z= 1.875 | 25 J= 25, 26 SEC=1 NSEG=1 ANG=180
| 50 X= -0.350 Y= 0.000 Z= 1.300 | 26 J= 26, 27 SEC=1 NSEG=1 ANG=180
| 51 X= -0.350 Y= 0.000 Z= 0.725 | 27 J= 27, 28 SEC=1 NSEG=1 ANG=180
| 52 X= -0.350 Y= 0.000 Z= 0.150 | 28 J= 28, 29 SEC=1 NSEG=2 ANG=180
29 J= 29, 30 SEC=1 NSEG=2 ANG=180
| RESTRAINT | 30 J= 30, 31 SEC=1 NSEG=1 ANG=180
| ADD=33 DOF=U1, U2, U3, R1, R2, R3 | 31 J= 31, 32 SEC=1 NSEG=1 ANG=180
| ADD=34 DOF=U1, U2, U3, R1, R2, R3 | 32 J= 32, 1 SEC=1 NSEG=1 ANG=180
ADD=35 DOF=U1, U2, U3, R1, R2, R3
| ADD=36 DOF=U1, U2, U3, R1, R2, R3 | NLLINK
| ADD=37 DOF=U1, U2, U3, R1, R2, R3 | 1 J=1,33 NLP=SP1 ANG=0
| ADD=38 DOF=U1, U2, U3, R1, R2, R3 | 2 J=4,34 NLP=SP2 ANG=0
| ADD=39 DOF=U1, U2, U3, R1, R2, R3 | 3 J=5,35 NLP=SP2 ANG=0
| ADD=40 DOF=U1, U2, U3, R1, R2, R3 | 4 J=6,36 NLP=SP2 ANG=0
| ADD=41 DOF=U1, U2, U3, R1, R2, R3 | 5 J=9,37 NLP=SP1 ANG=0
| ADD=42 DOF=U1, U2, U3, R1, R2, R3 | 6 J=9,38 NLP=SP1 ANG=180
| ADD=43 DOF=U1, U2, U3, R1, R2, R3 | 7 J=12,39 NLP=SP2 ANG=180
| ADD=44 DOF=U1, U2, U3, R1, R2, R3 | 8 J=13,40 NLP=SP2 ANG=180
| ADD=45 DOF=U1, U2, U3, R1, R2, R3 | 9 J=14,41 NLP=SP2 ANG=180
| ADD=46 DOF=U1, U2, U3, R1, R2, R3 | 10 J=17,42 NLP=SP1 ANG=180
| ADD=47 DOF=U1, U2, U3, R1, R2, R3 | 11 J=17,43 NLP=SP1 ANG=0
| ADD=48 DOF=U1, U2, U3, R1, R2, R3 | 12 J=20,44 NLP=SP2 ANG=0
| ADD=49 DOF=U1, U2, U3, R1, R2, R3 | 13 J=21,45 NLP=SP2 ANG=0
| ADD=50 DOF=U1, U2, U3, R1, R2, R3 | 14 J=22,46 NLP=SP2 ANG=0
| ADD=51 DOF=U1, U2, U3, R1, R2, R3 | 15 J=25,47 NLP=SP1 ANG=0
| ADD=52 DOF=U1, U2, U3, R1, R2, R3 | 16 J=25,48 NLP=SP1 ANG=180
17 J=28,49 NLP=SP2 ANG=180
| SPRING | 18 J=29,50 NLP=SP2 ANG=180
| ADD=1 U1=10168.6 U3=10168.6 | 19 J=30,51 NLP=SP2 ANG=180
| ADD=4 U1=13364.4 | 20 J=1,52 NLP=SP1 ANG=180
ADD=5 U1=13364.4
| LOAD | ADD=1 RD=0,1 UX=1.07986,1.07986
| NAME=SELFWGT SW=1 | ADD=2 RD=0,1 UX=1.07986,1.07986
| NAME=NWDEAD | ADD=3 RD=0,1 UX=1.07986,1.07986
| TYPE=Distributed Span | ADD=4 RD=0,1 UX=1.07986,1.07986
| ADD=17 RD=0,1 UZ=-57,-57 | ADD=5 RD=0,1 UX=1.07986,1.07986
| ADD=18 RD=0,1 UZ=-57,-57 | ADD=6 RD=0,1 UX=1.07986,1.07986
| ADD=19 RD=0,1 UZ=-57,-57 | ADD=7 RD=0,1 UX=1.07986,1.07986
| ADD=20 RD=0,1 UZ=-57,-57 | ADD=8 RD=0,1 UX=1.07986,1.07986
| ADD=21 RD=0,1 UZ=-57,-57 | ADD=9 RD=0,1 UX=1.07986,1.08251
| ADD=22 RD=0,1 UZ=-57,-57 | ADD=10 RD=0,1 UX=1.08251,1.08657
| ADD=23 RD=0,1 UZ=-57,-57 | ADD=11 RD=0,1 UX=1.08657,1.09001
| ADD=24 RD=0,1 UZ=-57,-57 | ADD=12 RD=0,1 UX=1.09001,1.10015
| NAME=LIVEFULL | ADD=13 RD=0,1 UX=1.10015,1.11029
| TYPE=Distributed Span | ADD=14 RD=0,1 UX=1.11029,1.11373
| ADD=17 RD=0,1 UZ=-11.3548,-11.3548 | ADD=15 RD=0,1 UX=1.11373,1.11779
| ADD=18 RD=0,1 UZ=-11.3548,-11.3548 | ADD=16 RD=0,1 UX=1.11779,1.12043
| ADD=19 RD=0,1 UZ=-11.3548,-11.3548 | ADD=17 RD=0,1 UX=1.12043,1.12043
| ADD=20 RD=0,1 UZ=-11.3548,-11.3548 | ADD=18 RD=0,1 UX=1.12043,1.12043
| ADD=21 RD=0,1 UZ=-11.3548,-11.3548 | ADD=19 RD=0,1 UX=1.12043,1.12043
| ADD=22 RD=0,1 UZ=-11.3548,-11.3548 | ADD=20 RD=0,1 UX=1.12043,1.12043
| ADD=23 RD=0,1 UZ=-11.3548,-11.3548 | ADD=21 RD=0,1 UX=1.12043,1.12043
| ADD=24 RD=0,1 UZ=-11.3548,-11.3548 | ADD=22 RD=0,1 UX=1.12043,1.12043
| NAME=SEUPSLAB | ADD=23 RD=0,1 UX=1.12043,1.12043
| TYPE=Distributed Span | ADD=24 RD=0,1 UX=1.12043,1.12043
| ADD=17 RD=0,1 UX=0.9529,0.9529 | ADD=25 RD=0,1 UX=1.12043,1.11779
| ADD=18 RD=0,1 UX=0.9529,0.9529 | ADD=26 RD=0,1 UX=1.11779,1.11373
| ADD=19 RD=0,1 UX=0.9529,0.9529 | ADD=27 RD=0,1 UX=1.11373,1.11029
| ADD=20 RD=0,1 UX=0.9529,0.9529 | ADD=28 RD=0,1 UX=1.11029,1.10015
| ADD=21 RD=0,1 UX=0.9529,0.9529 | ADD=29 RD=0,1 UX=1.10015,1.09001
| ADD=22 RD=0,1 UX=0.9529,0.9529 | ADD=30 RD=0,1 UX=1.09001,1.08657
| ADD=23 RD=0,1 UX=0.9529,0.9529 | ADD=31 RD=0,1 UX=1.08657,1.08251
| ADD=24 RD=0,1 UX=0.9529,0.9529 | ADD=32 RD=0,1 UX=1.08251,1.07986
NAME=SEWALL
| TYPE=Distributed Span | MODE
| ADD=9 RD=0,1 UX=0,0.2092 | TYPE=RITZ N=50
| ADD=10 RD=0,1 UX=0.2092,0.5578 | LOAD=SELFWGT
| ADD=11 RD=0,1 UX=0.5578,0.8367 | LOAD=NWDEAD
| ADD=12 RD=0,1 UX=0.8367,1.6037 | LOAD=LIVEFULL
| ADD=13 RD=0,1 UX=1.6037,2.301 | LOAD=SEUPSLAB
| ADD=14 RD=0,1 UX=2.301,2.5102 | LOAD=SEWALL
| ADD=15 RD=0,1 UX=2.5102,2.7194 | LOAD=SEPRINSH
| ADD=16 RD=0,1 UX=2.7194,2.8588 | LOAD=SEINER
| ADD=25 RD=0,1 UX=2.8588,2.7194 | NLLINK=*
ADD=26 RD=0,1 UX=2.7194,2.5102
| ADD=27 RD=0,1 UX=2.5102,2.301 | HISTORY
| ADD=28 RD=0,1 UX=2.301,1.6037 | NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=29 RD=0,1 UX=1.6037,0.8367 | LOAD=SELFWGT SF=1 AT=1
| ADD=30 RD=0,1 UX=0.8367,0.5578 | LOAD=NWDEAD SF=0.975 AT=1
| ADD=31 RD=0,1 UX=0.5578,0.2092 | LOAD=LIVEFULL SF=1 AT=1
| ADD=32 RD=0,1 UX=0.2092,0 | LOAD=SEUPSLAB SF=1 AT=1
| NAME=SEPRINSH | LOAD=SEWALL SF=1 AT=1
| TYPE=Distributed Span | LOAD=SEPRINSH SF=1 AT=1
| ADD=1 RD=0,1 UX=-0.42,-0.42 | LOAD=SEINER SF=1 AT=1
| ADD=2 RD=0,1 UX=-0.42,-0.42 | NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=3 RD=0,1 UX=-0.42,-0.42 | LOAD=SELFWGT SF=1 AT=1
| ADD=4 RD=0,1 UX=-0.42,-0.42 | LOAD=NWDEAD SF=0.975 AT=1
| ADD=5 RD=0,1 UX=-0.42,-0.42 | LOAD=LIVEFULL SF=1 AT=1
| ADD=6 RD=0,1 UX=-0.42,-0.42 | LOAD=SEUPSLAB SF=-1 AT=1
| ADD=7 RD=0,1 UX=-0.42,-0.42 | LOAD=SEWALL SF=-1 AT=1
| ADD=8 RD=0,1 UX=-0.42,-0.42 | LOAD=SEPRINSH SF=-1 AT=1
| ADD=9 RD=0,1 UZ=0.34,0.34 | LOAD=SEINER SF=-1 AT=1
ADD=10 RD=0,1 UZ=0.34,0.34
| ADD=11 RD=0,1 UZ=0.34,0.34 | COMBO
| ADD=12 RD=0,1 UZ=0.34,0.34 | NAME=ULTIMATE TYPE=ENVE
| ADD=13 RD=0,1 UZ=0.34,0.34 | HIST=HIST1 SF=1
| ADD=14 RD=0,1 UZ=0.34,0.34 | HIST=HIST2 SF=1
ADD=15 RD=0,1 UZ=0.34,0.34
| ADD=16 RD=0,1 UZ=0.34,0.34 | OUTPUT
| ADD=17 RD=0,1 UX=0.25,0.25 | ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
| ADD=18 RD=0,1 UX=0.25,0.25 | ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*
ADD=19 RD=0,1 UX=0.25,0.25
ADD=20 RD=0,1 UX=0.25,0.25
ADD=21 RD=0,1 UX=0.25,0.25
ADD=22 RD=0,1 UX=0.25,0.25
ADD=23 RD=0,1 UX=0.25,0.25
ADD=24 RD=0,1 UX=0.25,0.25
ADD=25 RD=0,1 UZ=-0.34,-0.34
ADD=26 RD=0,1 UZ=-0.34,-0.34
ADD=27 RD=0,1 UZ=-0.34,-0.34
ADD=28 RD=0,1 UZ=-0.34,-0.34
ADD=29 RD=0,1 UZ=-0.34,-0.34
ADD=30 RD=0,1 UZ=-0.34,-0.34
ADD=31 RD=0,1 UZ=-0.34,-0.34
ADD=32 RD=0,1 UZ=-0.34,-0.34
NAME=SEINER
TYPE=Distributed Span

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 17 | ULTIMATE MAX | 1 | 0 | 89.2489 | 8.3443
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 17 | ULTIMATE MIN | 0 | -78.5585 | -0.002296 | 0
| 1 | ULTIMATE MIN | 0 | -90.2791 | -96.962 | -39.7558 | 17 | ULTIMATE MIN | 0.5 | -78.5585 | 0 | 0
| 1 | ULTIMATE MIN | 1 | -90.2791 | -98.285 | -25.1123 | 17 | ULTIMATE MIN | 1 | -78.5585 | 0 | -2.4332
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 18 | ULTIMATE MAX | 0 | 0 | 89.2489 | 8.3443
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 5.9461 | 18 | ULTIMATE MAX | 1 | 0 | 115.9077 | 0
| 2 | ULTIMATE MIN | 0 | -90.2791 | -98.285 | -25.1123 | 18 | ULTIMATE MIN | 0 | -78.5585 | 0 | -2.4332
| 2 | ULTIMATE MIN | 1 | -90.2791 | -100.3136 | -4.8275 | 18 | ULTIMATE MIN | 1 | -78.5585 | 0 | -23.1247
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 5.9461 | 19 | ULTIMATE MAX | 0 | 0 | 115.9077 | 0
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 25.5603 | 19 | ULTIMATE MAX | 1 | 0 | 133.2938 | 0
| 3 | ULTIMATE MIN | 0 | -90.2791 | -100.3136 | -4.8275 | 19 | ULTIMATE MIN | 0 | -78.5585 | 0 | -23.1247
| 3 | ULTIMATE MIN | 1 | -90.2791 | -102.0335 | 0 | 19 | ULTIMATE MIN | 1 | -78.5585 | 0 | -41.8148
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 25.5603 | 20 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 4 | ULTIMATE MAX | 0.5 | 0 | 0 | 34.5079 | 20 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 44.1846 | 20 | ULTIMATE MIN | 0 | -133.2938 | -78.5586 | -41.8148
| 4 | ULTIMATE MIN | 0 | -90.2791 | -30.1655 | 0 | 20 | ULTIMATE MIN | 1 | -134.6168 | -70.0056 | -30.6682
| 4 | ULTIMATE MIN | 0.5 | -90.2791 | -32.7013 | 0 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 4 | ULTIMATE MIN | 1 | -90.2791 | -35.237 | 0 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 0 | 0 | 35.237 | 44.1846 | 21 | ULTIMATE MIN | 0 | -134.6168 | -70.0056 | -30.6682
| 5 | ULTIMATE MAX | 0.5 | 0 | 32.7013 | 34.5079 | 21 | ULTIMATE MIN | 1 | -136.6454 | -56.2267 | -20.8357
| 5 | ULTIMATE MAX | 1 | 0 | 30.1655 | 25.5603 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MIN | 0 | -90.2791 | 0 | 0 | 22 | ULTIMATE MAX | 0.25 | 0 | 0 | 5.2453
| 5 | ULTIMATE MIN | 0.5 | -90.2791 | 0 | 0 | 22 | ULTIMATE MAX | 0.5 | 0 | 0 | 12.1302
| 5 | ULTIMATE MIN | 1 | -90.2791 | 0 | 0 | 22 | ULTIMATE MAX | 0.75 | 0 | 25.2342 | 8.1413
| 6 | ULTIMATE MAX | 0 | 0 | 102.0335 | 25.5603 | 22 | ULTIMATE MAX | 1 | 0 | 56.8573 | 0
| 6 | ULTIMATE MAX | 1 | 0 | 100.3136 | 5.9461 | 22 | ULTIMATE MIN | 0 | -136.6454 | -56.2274 | -20.8357
| 6 | ULTIMATE MIN | 0 | -90.2791 | 0 | 0 | 22 | ULTIMATE MIN | 0.25 | -140.0411 | -31.3633 | -12.1019
| 6 | ULTIMATE MIN | 1 | -90.2791 | 0 | -4.8274 | 22 | ULTIMATE MIN | 0.5 | -143.4368 | -4.2462 | -8.3712
| 7 | ULTIMATE MAX | 0 | 0 | 100.3136 | 5.9461 | 22 | ULTIMATE MIN | 0.75 | -146.8325 | 0 | -10.0774
| 7 | ULTIMATE MAX | 1 | 0 | 98.285 | 0 | 22 | ULTIMATE MIN | 1 | -150.2282 | 0 | -17.6542
| 7 | ULTIMATE MIN | 0 | -90.2791 | 0 | -4.8274 | 23 | ULTIMATE MAX | 0 | 0 | 56.8573 | 0
| 7 | ULTIMATE MIN | 1 | -90.2791 | 0 | -25.1123 | 23 | ULTIMATE MAX | 1 | 0 | 76.8241 | 0
| 8 | ULTIMATE MAX | 0 | 0 | 98.285 | 0 | 23 | ULTIMATE MIN | 0 | -150.2282 | 0 | -17.6542
| 8 | ULTIMATE MAX | 1 | 0 | 96.962 | 0 | 23 | ULTIMATE MIN | 1 | -152.2568 | 0 | -27.2438
| 8 | ULTIMATE MIN | 0 | -90.2791 | 0 | -25.1123 | 24 | ULTIMATE MAX | 0 | 0 | 76.8241 | 0
| 8 | ULTIMATE MIN | 1 | -90.2791 | 0 | -39.7558 | 24 | ULTIMATE MAX | 1 | 0 | 90.2791 | 0
| 9 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 24 | ULTIMATE MIN | 0 | -152.2568 | 0 | -27.2438
| 9 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 24 | ULTIMATE MIN | 1 | -153.5798 | 0 | -39.7558
| 9 | ULTIMATE MIN | 0 | -153.5798 | -90.2791 | -39.7558
| 9 | ULTIMATE MIN | 1 | -152.2568 | -76.8241 | -27.2438
| 10 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 10 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 10 | ULTIMATE MIN | 0 | -152.2568 | -76.8241 | -27.2438
| 10 | ULTIMATE MIN | 1 | -150.2282 | -56.8573 | -17.6542
| 11 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MAX | 0.25 | 0 | 0 | 8.1413
| 11 | ULTIMATE MAX | 0.5 | 0 | 4.2463 | 12.1302
| 11 | ULTIMATE MAX | 0.75 | 0 | 31.3633 | 5.2453
| 11 | ULTIMATE MAX | 1 | 0 | 56.2274 | 0
| 11 | ULTIMATE MIN | 0 | -150.2282 | -56.8573 | -17.6542
| 11 | ULTIMATE MIN | 0.25 | -146.8325 | -25.2342 | -10.0774
| 11 | ULTIMATE MIN | 0.5 | -143.4368 | 0 | -8.3712
| 11 | ULTIMATE MIN | 0.75 | -140.0411 | 0 | -12.1019
| 11 | ULTIMATE MIN | 1 | -136.6454 | 0 | -20.8357
| 12 | ULTIMATE MAX | 0 | 0 | 56.2268 | 0
| 12 | ULTIMATE MAX | 1 | 0 | 70.0056 | 0
| 12 | ULTIMATE MIN | 0 | -136.6454 | 0 | -20.8357
| 12 | ULTIMATE MIN | 1 | -134.6168 | 0 | -30.6682
| 13 | ULTIMATE MAX | 0 | 0 | 70.0056 | 0
| 13 | ULTIMATE MAX | 1 | 0 | 78.5586 | 0
| 13 | ULTIMATE MIN | 0 | -134.6168 | 0 | -30.6682
| 13 | ULTIMATE MIN | 1 | -133.2938 | 0 | -41.8148
| 14 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 14 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 14 | ULTIMATE MIN | 0 | -78.5586 | -133.2938 | -41.8148
| 14 | ULTIMATE MIN | 1 | -78.5586 | -115.9077 | -23.1247
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 8.3443
| 15 | ULTIMATE MIN | 0 | -78.5585 | -115.9077 | -23.1247
| 15 | ULTIMATE MIN | 1 | -78.5585 | -89.2489 | -2.4332
| 16 | ULTIMATE MAX | 0 | 0 | 0 | 8.3443
| 16 | ULTIMATE MAX | 0.5 | 0 | 0 | 34.1149
| 16 | ULTIMATE MAX | 1 | 0 | 0.002278 | 42.7051
| 16 | ULTIMATE MIN | 0 | -78.5585 | -89.2489 | -2.4332
| 16 | ULTIMATE MIN | 0.5 | -78.5585 | -44.6245 | 0
| 16 | ULTIMATE MIN | 1 | -78.5585 | 0 | 0
| 17 | ULTIMATE MAX | 0 | 0 | 0 | 42.7051
| 17 | ULTIMATE MAX | 0.5 | 0 | 44.6245 | 34.1149
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 17 | SERVICE MIN | 1 | -49.3356 | 0 | -1.0535
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 18 | SERVICE MAX | 0 | 0 | 57.1954 | 5.3928
| 1 | SERVICE MIN | 0 | -56.4328 | -58.6934 | -24.7963 | 18 | SERVICE MAX | 1 | 0 | 74.2798 | 0
| 1 | SERVICE MIN | 1 | -56.4328 | -59.7959 | -15.9096 | 18 | SERVICE MIN | 0 | -49.3356 | 0 | -1.0535
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 18 | SERVICE MIN | 1 | -49.3356 | 0 | -14.6493
| 2 | SERVICE MAX | 1 | 0 | 0 | 3.5983 | 19 | SERVICE MAX | 0 | 0 | 74.2798 | 0
| 2 | SERVICE MIN | 0 | -56.4328 | -59.7959 | -15.9096 | 19 | SERVICE MAX | 1 | 0 | 85.4218 | 0
| 2 | SERVICE MIN | 1 | -56.4328 | -65.1664 | -2.8432 | 19 | SERVICE MIN | 0 | -49.3356 | 0 | -14.6493
| 3 | SERVICE MAX | 0 | 0 | 0 | 3.5983 | 19 | SERVICE MIN | 1 | -49.3356 | 0 | -26.627
| 3 | SERVICE MAX | 1 | 0 | 0 | 16.678 | 20 | SERVICE MAX | 0 | 0 | 0 | 0
| 3 | SERVICE MIN | 0 | -56.4328 | -65.1664 | -2.8432 | 20 | SERVICE MAX | 1 | 0 | 0 | 0
| 3 | SERVICE MIN | 1 | -56.4328 | -69.7196 | 0 | 20 | SERVICE MIN | 0 | -85.4218 | -49.3356 | -26.627
| 4 | SERVICE MAX | 0 | 0 | 0 | 16.678 | 20 | SERVICE MIN | 1 | -86.5243 | -43.99 | -19.6249
| 4 | SERVICE MAX | 0.5 | 0 | 0 | 21.6104 | 21 | SERVICE MAX | 0 | 0 | 0 | 0
| 4 | SERVICE MAX | 1 | 0 | 0 | 28.4727 | 21 | SERVICE MAX | 1 | 0 | 0 | 0
| 4 | SERVICE MIN | 0 | -56.4328 | -13.9938 | 0 | 21 | SERVICE MIN | 0 | -86.5243 | -43.99 | -19.6249
| 4 | SERVICE MIN | 0.5 | -56.4328 | -20.7069 | 0 | 21 | SERVICE MIN | 1 | -88.2148 | -35.3783 | -13.4252
| 4 | SERVICE MIN | 1 | -56.4328 | -27.42 | 0 | 22 | SERVICE MAX | 0 | 0 | 0 | 0
| 5 | SERVICE MAX | 0 | 0 | 27.42 | 28.4727 | 22 | SERVICE MAX | 0.25 | 0 | 0 | 2.5664
| 5 | SERVICE MAX | 0.5 | 0 | 20.7069 | 21.6104 | 22 | SERVICE MAX | 0.5 | 0 | 0 | 6.8663
| 5 | SERVICE MAX | 1 | 0 | 13.9938 | 16.678 | 22 | SERVICE MAX | 0.75 | 0 | 15.7798 | 4.37
| 5 | SERVICE MIN | 0 | -56.4328 | 0 | 0 | 22 | SERVICE MAX | 1 | 0 | 35.5442 | 0
| 5 | SERVICE MIN | 0.5 | -56.4328 | 0 | 0 | 22 | SERVICE MIN | 0 | -88.2148 | -35.3787 | -13.4252
| 5 | SERVICE MIN | 1 | -56.4328 | 0 | 0 | 22 | SERVICE MIN | 0.25 | -91.0445 | -19.8386 | -7.8755
| 6 | SERVICE MAX | 0 | 0 | 69.7196 | 16.678 | 22 | SERVICE MIN | 0.5 | -93.8743 | -2.8905 | -5.4528
| 6 | SERVICE MAX | 1 | 0 | 65.1664 | 3.5983 | 22 | SERVICE MIN | 0.75 | -96.704 | 0 | -6.4281
| 6 | SERVICE MIN | 0 | -56.4328 | 0 | 0 | 22 | SERVICE MIN | 1 | -99.5338 | 0 | -11.0726
| 6 | SERVICE MIN | 1 | -56.4328 | 0 | -2.8432 | 23 | SERVICE MAX | 0 | 0 | 35.5442 | 0
| 7 | SERVICE MAX | 0 | 0 | 65.1664 | 3.5983 | 23 | SERVICE MAX | 1 | 0 | 48.0235 | 0
| 7 | SERVICE MAX | 1 | 0 | 59.7959 | 0 | 23 | SERVICE MIN | 0 | -99.5338 | 0 | -11.0726
| 7 | SERVICE MIN | 0 | -56.4328 | 0 | -2.8432 | 23 | SERVICE MIN | 1 | -101.2243 | 0 | -17.0117
| 7 | SERVICE MIN | 1 | -56.4328 | 0 | -15.9096 | 24 | SERVICE MAX | 0 | 0 | 48.0235 | 0
| 8 | SERVICE MAX | 0 | 0 | 59.7959 | 0 | 24 | SERVICE MAX | 1 | 0 | 56.4328 | 0
| 8 | SERVICE MAX | 1 | 0 | 58.6934 | 0 | 24 | SERVICE MIN | 0 | -101.2243 | 0 | -17.0117
| 8 | SERVICE MIN | 0 | -56.4328 | 0 | -15.9096 | 24 | SERVICE MIN | 1 | -102.3268 | 0 | -24.7963
| 8 | SERVICE MIN | 1 | -56.4328 | 0 | -24.7963
| 9 | SERVICE MAX | 0 | 0 | 0 | 0
| 9 | SERVICE MAX | 1 | 0 | 0 | 0
| 9 | SERVICE MIN | 0 | -102.3268 | -56.4328 | -24.7963
| 9 | SERVICE MIN | 1 | -101.2243 | -48.0235 | -17.0117
| 10 | SERVICE MAX | 0 | 0 | 0 | 0
| 10 | SERVICE MAX | 1 | 0 | 0 | 0
| 10 | SERVICE MIN | 0 | -101.2243 | -48.0235 | -17.0117
| 10 | SERVICE MIN | 1 | -99.5338 | -35.5442 | -11.0726
| 11 | SERVICE MAX | 0 | 0 | 0 | 0
| 11 | SERVICE MAX | 0.25 | 0 | 0 | 4.37
| 11 | SERVICE MAX | 0.5 | 0 | 2.8905 | 6.8663
| 11 | SERVICE MAX | 0.75 | 0 | 19.8387 | 2.5664
| 11 | SERVICE MAX | 1 | 0 | 35.3787 | 0
| 11 | SERVICE MIN | 0 | -99.5338 | -35.5442 | -11.0726
| 11 | SERVICE MIN | 0.25 | -96.704 | -15.7798 | -6.4281
| 11 | SERVICE MIN | 0.5 | -93.8743 | 0 | -5.4528
| 11 | SERVICE MIN | 0.75 | -91.0445 | 0 | -7.8755
| 11 | SERVICE MIN | 1 | -88.2148 | 0 | -13.4252
| 12 | SERVICE MAX | 0 | 0 | 35.3783 | 0
| 12 | SERVICE MAX | 1 | 0 | 43.99 | 0
| 12 | SERVICE MIN | 0 | -88.2148 | 0 | -13.4252
| 12 | SERVICE MIN | 1 | -86.5243 | 0 | -19.6249
| 13 | SERVICE MAX | 0 | 0 | 43.99 | 0
| 13 | SERVICE MAX | 1 | 0 | 49.3357 | 0
| 13 | SERVICE MIN | 0 | -86.5243 | 0 | -19.6249
| 13 | SERVICE MIN | 1 | -85.4218 | 0 | -26.627
| 14 | SERVICE MAX | 0 | 0 | 0 | 0
| 14 | SERVICE MAX | 1 | 0 | 0 | 0
| 14 | SERVICE MIN | 0 | -49.3356 | -85.4218 | -26.627
| 14 | SERVICE MIN | 1 | -49.3356 | -74.2798 | -14.6493
| 15 | SERVICE MAX | 0 | 0 | 0 | 0
| 15 | SERVICE MAX | 1 | 0 | 0 | 5.3928
| 15 | SERVICE MIN | 0 | -49.3356 | -74.2798 | -14.6493
| 15 | SERVICE MIN | 1 | -49.3356 | -57.1954 | -1.0535
| 16 | SERVICE MAX | 0 | 0 | 0 | 5.3928
| 16 | SERVICE MAX | 0.5 | 0 | 0 | 21.9079
| 16 | SERVICE MAX | 1 | 0 | 0.001637 | 27.413
| 16 | SERVICE MIN | 0 | -49.3356 | -57.1954 | -1.0535
| 16 | SERVICE MIN | 0.5 | -49.3356 | -28.5977 | 0
| 16 | SERVICE MIN | 1 | -49.3356 | 0 | 0
| 17 | SERVICE MAX | 0 | 0 | 0 | 27.413
| 17 | SERVICE MAX | 0.5 | 0 | 28.5977 | 21.9079
| 17 | SERVICE MAX | 1 | 0 | 57.1954 | 5.3928
| 17 | SERVICE MIN | 0 | -49.3356 | -0.001648 | 0
| 17 | SERVICE MIN | 0.5 | -49.3356 | 0 | 0

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 18 | ULTIMATE MIN | 0 | -13.0599 | -74.9761 | -8.4627
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 18 | ULTIMATE MIN | 1 | -12.5256 | -57.8918 | 0
| 1 | ULTIMATE MIN | 0 | -0.38092 | -31.687 | -7.7313 | 19 | ULTIMATE MAX | 0 | 0 | 0 | 7.889
| 1 | ULTIMATE MIN | 1 | -0.28194 | -32.7895 | -2.8956 | 19 | ULTIMATE MAX | 1 | 0 | 0 | 17.4942
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 19 | ULTIMATE MIN | 0 | -12.5256 | -57.8918 | 0
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 5.7031 | 19 | ULTIMATE MIN | 1 | -12.0725 | -43.4072 | 0
| 2 | ULTIMATE MIN | 0 | -0.28194 | -32.7895 | -2.8956 | 20 | ULTIMATE MAX | 0 | 0 | 0 | 17.4942
| 2 | ULTIMATE MIN | 1 | -0.29868 | -34.48 | 0 | 20 | ULTIMATE MAX | 0.5 | 0 | 0 | 26.5036
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 5.7031 | 20 | ULTIMATE MAX | 1 | 0 | 0.69717 | 29.3734
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 12.3652 | 20 | ULTIMATE MIN | 0 | -12.8852 | -43.407 | 0
| 3 | ULTIMATE MIN | 0 | -0.29868 | -34.48 | 0 | 20 | ULTIMATE MIN | 0.5 | -12.2173 | -22.0516 | 0
| 3 | ULTIMATE MIN | 1 | -0.42735 | -35.9132 | 0 | 20 | ULTIMATE MIN | 1 | -12.3736 | -0.69614 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 12.3652 | 21 | ULTIMATE MAX | 0 | 0 | 0.69614 | 29.3734
| 4 | ULTIMATE MAX | 0.5 | 0 | 0 | 14.912 | 21 | ULTIMATE MAX | 0.5 | 0 | 22.0516 | 26.5036
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 18.0663 | 21 | ULTIMATE MAX | 1 | 0 | 43.407 | 17.4942
| 4 | ULTIMATE MIN | 0 | -0.3962 | -8.9522 | 0 | 21 | ULTIMATE MIN | 0 | -12.3736 | -0.69717 | 0
| 4 | ULTIMATE MIN | 0.5 | -0.22196 | -11.0654 | 0 | 21 | ULTIMATE MIN | 0.5 | -12.2173 | 0 | 0
| 4 | ULTIMATE MIN | 1 | -0.41167 | -13.1785 | 0 | 21 | ULTIMATE MIN | 1 | -12.8852 | 0 | 0
| 5 | ULTIMATE MAX | 0 | 0 | 13.1785 | 18.0663 | 22 | ULTIMATE MAX | 0 | 0 | 43.4072 | 17.4942
| 5 | ULTIMATE MAX | 0.5 | 0 | 11.0654 | 14.912 | 22 | ULTIMATE MAX | 1 | 0 | 57.8918 | 7.889
| 5 | ULTIMATE MAX | 1 | 0 | 8.9522 | 12.3652 | 22 | ULTIMATE MIN | 0 | -12.0725 | 0 | 0
| 5 | ULTIMATE MIN | 0 | -0.41167 | 0 | 0 | 22 | ULTIMATE MIN | 1 | -12.5256 | 0 | 0
| 5 | ULTIMATE MIN | 0.5 | -0.22196 | 0 | 0 | 23 | ULTIMATE MAX | 0 | 0 | 57.8918 | 7.889
| 5 | ULTIMATE MIN | 1 | -0.3962 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 74.9761 | 0
| 6 | ULTIMATE MAX | 0 | 0 | 35.9132 | 12.3652 | 23 | ULTIMATE MIN | 0 | -12.5256 | 0 | 0
| 6 | ULTIMATE MAX | 1 | 0 | 34.48 | 5.7031 | 23 | ULTIMATE MIN | 1 | -13.0599 | 0 | -8.4627
| 6 | ULTIMATE MIN | 0 | -0.42735 | 0 | 0 | 24 | ULTIMATE MAX | 0 | 0 | 74.9761 | 0
| 6 | ULTIMATE MIN | 1 | -0.29868 | 0 | 0 | 24 | ULTIMATE MAX | 1 | 0 | 86.1181 | 0
| 7 | ULTIMATE MAX | 0 | 0 | 34.48 | 5.7031 | 24 | ULTIMATE MIN | 0 | -13.0599 | 0 | -8.4627
| 7 | ULTIMATE MAX | 1 | 0 | 32.7895 | 0 | 24 | ULTIMATE MIN | 1 | -13.4084 | 0 | -20.5448
| 7 | ULTIMATE MIN | 0 | -0.29868 | 0 | 0 | 25 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 7 | ULTIMATE MIN | 1 | -0.28194 | 0 | -2.8956 | 25 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 8 | ULTIMATE MAX | 0 | 0 | 32.7895 | 0 | 25 | ULTIMATE MIN | 0 | -77.9746 | -11.181 | -20.5448
| 8 | ULTIMATE MAX | 1 | 0 | 31.687 | 0 | 25 | ULTIMATE MIN | 1 | -79.0261 | -11.5579 | -18.8548
| 8 | ULTIMATE MIN | 0 | -0.28194 | 0 | -2.8956 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 8 | ULTIMATE MIN | 1 | -0.38092 | 0 | -7.7313 | 26 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 9 | ULTIMATE MAX | 0 | 0 | 0.8198 | 0 | 26 | ULTIMATE MIN | 0 | -79.0261 | -11.5579 | -18.8548
| 9 | ULTIMATE MAX | 1 | 0 | 0.64194 | 0 | 26 | ULTIMATE MIN | 1 | -80.6384 | -12.4159 | -16.0969
| 9 | ULTIMATE MIN | 0 | -63.0664 | -0.34875 | -7.7313 | 27 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 9 | ULTIMATE MIN | 1 | -61.9129 | -0.17088 | -7.692 | 27 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 10 | ULTIMATE MAX | 0 | 0 | 0.64196 | 0 | 27 | ULTIMATE MIN | 0 | -80.6384 | -12.4159 | -16.0969
| 10 | ULTIMATE MAX | 1 | 0 | 0.30431 | 0 | 27 | ULTIMATE MIN | 1 | -82.0053 | -13.1019 | -13.6082
| 10 | ULTIMATE MIN | 0 | -61.9129 | -0.17088 | -7.692 | 28 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 10 | ULTIMATE MIN | 1 | -60.1442 | 0 | -7.6899 | 28 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 11 | ULTIMATE MAX | 0 | 0 | 0.30435 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 11 | ULTIMATE MAX | 1 | 0 | 0.51497 | 0 | 28 | ULTIMATE MIN | 0 | -71.3782 | -7.6229 | -13.6082
| 11 | ULTIMATE MIN | 0 | -60.1442 | 0 | -7.6899 | 28 | ULTIMATE MIN | 0.5 | -73.3936 | -8.2707 | -11.3617
| 11 | ULTIMATE MIN | 1 | -58.6447 | -0.043922 | -7.7555 | 28 | ULTIMATE MIN | 1 | -75.409 | -9.0989 | -9.2845
| 12 | ULTIMATE MAX | 0 | 0 | 4.349 | 0 | 29 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 12 | ULTIMATE MAX | 0.5 | 0 | 3.7392 | 0 | 29 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 12 | ULTIMATE MAX | 1 | 0 | 3.362 | 0 | 29 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 12 | ULTIMATE MIN | 0 | -69.0128 | 0 | -7.7555 | 29 | ULTIMATE MIN | 0 | -64.8515 | -3.362 | -9.2845
| 12 | ULTIMATE MIN | 0.5 | -66.8668 | 0 | -8.4243 | 29 | ULTIMATE MIN | 0.5 | -66.8668 | -3.7392 | -8.4243
| 12 | ULTIMATE MIN | 1 | -64.8515 | 0 | -9.2845 | 29 | ULTIMATE MIN | 1 | -69.0128 | -4.349 | -7.7555
| 13 | ULTIMATE MAX | 0 | 0 | 9.0989 | 0 | 30 | ULTIMATE MAX | 0 | 0 | 0.043922 | 0
| 13 | ULTIMATE MAX | 0.5 | 0 | 8.2707 | 0 | 30 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 13 | ULTIMATE MAX | 1 | 0 | 7.6229 | 0 | 30 | ULTIMATE MIN | 0 | -58.6447 | -0.51497 | -7.7555
| 13 | ULTIMATE MIN | 0 | -75.409 | 0 | -9.2845 | 30 | ULTIMATE MIN | 1 | -60.1442 | -0.30435 | -7.6899
| 13 | ULTIMATE MIN | 0.5 | -73.3936 | 0 | -11.3617 | 31 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 13 | ULTIMATE MIN | 1 | -71.3782 | 0 | -13.6082 | 31 | ULTIMATE MAX | 1 | 0 | 0.17088 | 0
| 14 | ULTIMATE MAX | 0 | 0 | 13.1019 | 0 | 31 | ULTIMATE MIN | 0 | -60.1442 | -0.30431 | -7.6899
| 14 | ULTIMATE MAX | 1 | 0 | 12.4159 | 0 | 31 | ULTIMATE MIN | 1 | -61.9129 | -0.64196 | -7.692
| 14 | ULTIMATE MIN | 0 | -82.0053 | 0 | -13.6082 | 32 | ULTIMATE MAX | 0 | 0 | 0.17088 | 0
| 14 | ULTIMATE MIN | 1 | -80.6384 | 0 | -16.0969 | 32 | ULTIMATE MAX | 1 | 0 | 0.34875 | 0
| 15 | ULTIMATE MAX | 0 | 0 | 12.4159 | 0 | 32 | ULTIMATE MIN | 0 | -61.9129 | -0.64194 | -7.692
| 15 | ULTIMATE MAX | 1 | 0 | 11.5579 | 0 | 32 | ULTIMATE MIN | 1 | -63.0664 | -0.8198 | -7.7313
| 15 | ULTIMATE MIN | 0 | -80.6384 | 0 | -16.0969
| 15 | ULTIMATE MIN | 1 | -79.0261 | 0 | -18.8548
| 16 | ULTIMATE MAX | 0 | 0 | 11.5579 | 0
| 16 | ULTIMATE MAX | 1 | 0 | 11.181 | 0
| 16 | ULTIMATE MIN | 0 | -79.0261 | 0 | -18.8548
| 16 | ULTIMATE MIN | 1 | -77.9746 | 0 | -20.5448
| 17 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 17 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 17 | ULTIMATE MIN | 0 | -13.4084 | -86.1181 | -20.5448
| 17 | ULTIMATE MIN | 1 | -13.0599 | -74.9761 | -8.4627
| 18 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 18 | ULTIMATE MAX | 1 | 0 | 0 | 7.889

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 41.815 | 89.249 | 78.559 | 26.627 | 1000 | 366.667
|  | 중앙부 | 42.705 | - | 78.559 | 27.413 | 1000 | 300
|  | 단지점부(우측) | 41.815 | 89.249 | 78.559 | 26.627 | 1000 | 366.667
| 하부슬래브 | 단지점부(좌측) | 39.756 | 100.314 | 90.279 | 24.796 | 1000 | 300
|  | 중앙부 | 44.185 | - | 90.279 | 28.473 | 1000 | 300
|  | 단지점부(우측) | 39.756 | 100.314 | 90.279 | 24.796 | 1000 | 300
| 좌측벽체 | 상부 | 41.815 | 56.227 | 133.294 | 26.627 | 1000 | 366.667
|  | 중앙부 | 12.13 | - | 143.437 | 6.866 | 1000 | 300
|  | 중앙부(부모멘트) | -20.836 | - | 143.437 | -13.425 | 1000 | 300 | 부모멘트
|  | 하부 | 39.756 | 56.857 | 153.58 | 24.796 | 1000 | 300
| 우측벽체 | 상부 | 41.815 | 56.227 | 133.294 | 26.627 | 1000 | 366.667
|  | 중앙부 | 12.13 | - | 143.437 | 6.866 | 1000 | 300
|  | 중앙부(부모멘트) | -20.836 | - | 143.437 | -13.425 | 1000 | 300 | 부모멘트
|  | 하부 | 39.756 | 56.857 | 153.58 | 24.796 | 1000 | 300

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 20.545 | 57.892 | 13.408 | 1000 | 366.667
|  | 중앙부 | 29.373 | - | 12.374 | 1000 | 300
|  | 단지점부(우측) | 20.545 | 57.892 | 13.408 | 1000 | 366.667
| 하부슬래브 | 단지점부(좌측) | 7.731 | 34.48 | 0.381 | 1000 | 300
|  | 중앙부 | 18.066 | - | 0.412 | 1000 | 300
|  | 단지점부(우측) | 7.731 | 34.48 | 0.381 | 1000 | 300
| 좌측벽체 | 상부 | 20.545 | 12.416 | 77.975 | 1000 | 366.667
|  | 중앙부 | 0 | - | 80.638 | 1000 | 300
|  | 중앙부(부모멘트) | -16.097 | - | 80.638 | 1000 | 300 | 부모멘트
|  | 하부 | 7.731 | 0.304 | 63.066 | 1000 | 300
| 우측벽체 | 상부 | 20.545 | 12.416 | 77.975 | 1000 | 366.667
|  | 중앙부 | 0 | - | 60.144 | 1000 | 300
|  | 중앙부(부모멘트) | -16.097 | - | 60.144 | 1000 | 300 | 부모멘트
|  | 하부 | 7.731 | 0.304 | 63.066 | 1000 | 300

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 296.667 | 41.815 | 98.814 |  | 420.396 | H13 - 8.0EA |  |  | 1013.6 | 2.363
상부슬래브 : 중앙부 |  |  |  | 1000 |  | 210 | 42.705 | 68.946 |  | 615.815 | H13 - 8.0EA |  |  | 1013.6 | 1.614
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 296.667 | 41.815 | 98.814 |  | 420.396 | H13 - 8.0EA |  |  | 1013.6 | 2.363
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 230 | 39.756 | 75.839 |  | 519.909 | H13 - 8.0EA |  |  | 1013.6 | 1.908
하부슬래브 : 중앙부 |  |  |  | 1000 |  | 210 | 44.185 | 87.262 |  | 637.824 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.975
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 230 | 39.756 | 75.839 |  | 519.909 | H13 - 8.0EA |  |  | 1013.6 | 1.908
좌측벽체 : 상부 |  |  |  | 1000 |  | 296.667 | 41.815 | 185.291 |  | - | H13 - 8.0EA |  |  | - | 4.431
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 210 | 12.13 | 195.4 |  | - | H13 - 4.0EA |  |  | - | 16.109
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 230 | 20.836 | 191.571 |  | - | H13 - 8.0EA |  |  | - | 9.194
좌측벽체 : 하부 |  |  |  | 1000 |  | 230 | 39.756 | 142.048 |  | - | H13 - 8.0EA |  |  | - | 3.573
우측벽체 : 상부 |  |  |  | 1000 |  | 296.667 | 41.815 | 185.291 |  | - | H13 - 8.0EA |  |  | - | 4.431
우측벽체 : 중앙부 |  |  |  | 1000 |  | 210 | 12.13 | 195.4 |  | - | H13 - 4.0EA |  |  | - | 16.109
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 230 | 20.836 | 191.571 |  | - | H13 - 8.0EA |  |  | - | 9.194
우측벽체 : 하부 |  |  |  | 1000 |  | 230 | 39.756 | 142.048 |  | - | H13 - 8.0EA |  |  | - | 3.573
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 140.846 |  | 89.249 | 140.846 | - |  | - | - | - |  | - | O.K
상부슬래브 : 중앙부 |  |  |  | 128.598 |  | - | 128.598 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 140.846 |  | 89.249 | 140.846 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 140.846 |  | 100.314 | 140.846 | - |  | - | - | - |  | - | O.K
하부슬래브 : 중앙부 |  |  |  | 128.598 |  | - | 128.598 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 140.846 |  | 100.314 | 140.846 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 145.316 |  | 56.227 | 145.316 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 132.99 |  | - | 132.99 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 145.996 |  | 56.857 | 145.996 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 145.316 |  | 56.227 | 145.316 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 132.99 |  | - | 132.99 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 145.996 |  | 56.857 | 145.996 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 366.667 |  | 296.667 |  | 70 |  | 41.815 |  | 89.249
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 400.00 = 405440.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 19.875 mm, c = 19.875 / β1 = 19.875 / 0.85 = 23.382 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (296.67 - 23.382) / 23.382 = 0.0351
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 420.396 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00342
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 400 x (296.67 - a/2) = 98.814 kN.m
; a = As x fy / (0.85 x fck x b) = 19.875 mm
≥ Mu (= 41.815 kN.m) ∴ O.K [안전률 2.363]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 230.00 = 140.846 kN
≥ Vu (= 89.249 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 210 |  | 90 |  | 42.705 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 400.00 = 405440.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 19.875 mm, c = 19.875 / β1 = 19.875 / 0.85 = 23.382 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (210.00 - 23.382) / 23.382 = 0.0239
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 615.815 mm²
Use As = 1013.600 mm² (철근도심 : 90.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00483
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 400 x (210.00 - a/2) = 68.946 kN.m
; a = As x fy / (0.85 x fck x b) = 19.875 mm
≥ Mu (= 42.705 kN.m) ∴ O.K [안전률 1.614]
＊ 전단에 대한 검토 (d = 210.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 210.00 = 128.598 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 366.667 |  | 296.667 |  | 70 |  | 41.815 |  | 89.249
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 400.00 = 405440.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 19.875 mm, c = 19.875 / β1 = 19.875 / 0.85 = 23.382 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (296.67 - 23.382) / 23.382 = 0.0351
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 420.396 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00342
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 400 x (296.67 - a/2) = 98.814 kN.m
; a = As x fy / (0.85 x fck x b) = 19.875 mm
≥ Mu (= 41.815 kN.m) ∴ O.K [안전률 2.363]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 230.00 = 140.846 kN
≥ Vu (= 89.249 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 230 |  | 70 |  | 39.756 |  | 100.314
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 400.00 = 405440.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 19.875 mm, c = 19.875 / β1 = 19.875 / 0.85 = 23.382 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (230.00 - 23.382) / 23.382 = 0.0265
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 519.909 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00441
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 400 x (230.00 - a/2) = 75.839 kN.m
; a = As x fy / (0.85 x fck x b) = 19.875 mm
≥ Mu (= 39.756 kN.m) ∴ O.K [안전률 1.908]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 230.00 = 140.846 kN
≥ Vu (= 100.314 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 210 |  | 90 |  | 44.185 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (210.00 - 30.016) / 30.016 = 0.0180
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 637.824 mm²
Use As = 1301.200 mm² (철근도심 : 90.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00620
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (210.00 - a/2) = 87.262 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 44.185 kN.m) ∴ O.K [안전률 1.975]
＊ 전단에 대한 검토 (d = 210.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 210.00 = 128.598 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 230 |  | 70 |  | 39.756 |  | 100.314
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 400.00 = 405440.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 19.875 mm, c = 19.875 / β1 = 19.875 / 0.85 = 23.382 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (230.00 - 23.382) / 23.382 = 0.0265
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 519.909 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00441
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 400 x (230.00 - a/2) = 75.839 kN.m
; a = As x fy / (0.85 x fck x b) = 19.875 mm
≥ Mu (= 39.756 kN.m) ∴ O.K [안전률 1.908]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 230.00 = 140.846 kN
≥ Vu (= 100.314 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 366.667 |  | 296.667 |  | 133.294 |  | 41.815 |  | 56.227 |  | 313.704
＊ 철근비 검토
As = 1013.600 mm² (인장중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0041) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 366.7 x 1000.0 = 7480000.0 N
Cs = As x fy = 405440.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (7480000.0 x 183.33 + 405440.0 x 70.000 + 202720.0 x 276.667) / 8088160.0
= 179.991 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 178.000 mm, ab = k1 x cb = 151.300 mm
fs' = 600 x (178.000 - 90.000) / 178.000 (≤fy) = 296.629 MPa
Cc = 0.85 x 24.0 x 151.300 x 1000.000 = 3086.520 kN
Cs = As' x (fs' - 0.85 x fck) = 139.993 kN
Ts = As x fs = 405.440 kN
Pb = 3086.520 + 139.993 - 405.440 = 2821.073 kN
Mb = 3086.520 x (296.667 - 151.300/2) + 139.993 x (296.667 - 90.00)
- 2821.073 x (179.991 - 70.000)
= 400.810 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 142.077 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 67.960 mm, a = k1 x c = 57.766 mm 를 사용.
fs = 600 x (296.667 - 67.960) / 67.960 (≤fy) = 400.000 MPa
fs' = 600 x ( 67.960 - 90.000) / 67.960 (≤fy) = 57.820 MPa
Cc = 0.85 x 24.0 x 57.766 x 1000.000 = 1178.434 kN
Cs = As' x (fs' - 0.85 x fck) = 18.964 kN
Ts = As x fs = 405.440 kN
Pn = 1178.434 + 18.964 - 405.440 = 754.030 kN
Mn' = 1178.434 x (296.667 - 57.766/2) + 18.964 x (296.667 - 90.00)
= 319.485 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0073 ＜ 0.0100 (e' = e + Xp - dc = 423.695 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6445.715 kN ≥ Pn = 754.030 kN
ΦPn = 0.78 x 754.030 = 590.657 kN ≥ Pu = 133.294 kN ∴ O.K
ΦMn = ΦPn x 0.314 = 185.291 kN.m ≥ Mu = 41.815 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.316 kN
≥ Vu (= 56.227 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 210 |  | 143.437 |  | 12.13 |  | 0 |  | 84.568
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 1013.600 mm² (압축중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0051) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 405440.0 N
Xp = (6120000.0 x 150.00 + 202720.0 x 90.000 + 405440.0 x 230.000) / 6728160.0
= 153.013 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 126.000 mm, ab = k1 x cb = 107.100 mm
fs' = 600 x (126.000 - 70.000) / 126.000 (≤fy) = 266.667 MPa
Cc = 0.85 x 24.0 x 107.100 x 1000.000 = 2184.840 kN
Cs = As' x (fs' - 0.85 x fck) = 249.616 kN
Ts = As x fs = 202.720 kN
Pb = 2184.840 + 249.616 - 202.720 = 2231.736 kN
Mb = 2184.840 x (210.000 - 107.100/2) + 249.616 x (210.000 - 70.00)
- 2231.736 x (153.013 - 90.000)
= 236.136 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 105.808 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 157.628 mm, a = k1 x c = 133.984 mm 를 사용.
fs = 600 x (210.000 - 157.628) / 157.628 (≤fy) = 199.349 MPa
fs' = 600 x (157.628 - 70.000) / 157.628 (≤fy) = 333.550 MPa
Cc = 0.85 x 24.0 x 133.984 x 1000.000 = 2733.273 kN
Cs = As' x (fs' - 0.85 x fck) = 317.409 kN
Ts = As x fs = 101.030 kN
Pn = 2733.273 + 317.409 - 101.030 = 2949.651 kN
Mn' = 2733.273 x (210.000 - 133.984/2) + 317.409 x (210.000 - 70.00)
= 435.317 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0014 ＜ 0.0100 (e' = e + Xp - dc = 147.581 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 90.00 = 210.000 mm
c = 600.00 / (600.00+400.00) x 210.000 = 126.000 mm, a = k1 x c = 107.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (210.00-126.00) / 126.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5357.715 kN ≥ Pn = 2949.651 kN
ΦPn = 0.78 x 2949.651 = 2310.560 kN ≥ Pu = 143.437 kN ∴ O.K
ΦMn = ΦPn x 0.085 = 195.400 kN.m ≥ Mu = 12.130 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 210.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 210.00 = 132.990 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 143.437 |  | 20.836 |  | 0 |  | 145.261
＊ 철근비 검토
As = 1013.600 mm² (인장중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0051) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 405440.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (6120000.0 x 150.00 + 405440.0 x 70.000 + 202720.0 x 210.000) / 6728160.0
= 146.987 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 90.000) / 138.000 (≤fy) = 208.696 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 95.428 kN
Ts = As x fs = 405.440 kN
Pb = 2392.920 + 95.428 - 405.440 = 2082.908 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 95.428 x (230.000 - 90.00)
- 2082.908 x (146.987 - 70.000)
= 263.030 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 126.280 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 117.021 mm, a = k1 x c = 99.468 mm 를 사용.
fs = 600 x (230.000 - 117.021) / 117.021 (≤fy) = 400.000 MPa
fs' = 600 x (117.021 - 90.000) / 117.021 (≤fy) = 138.546 MPa
Cc = 0.85 x 24.0 x 99.468 x 1000.000 = 2029.153 kN
Cs = As' x (fs' - 0.85 x fck) = 59.877 kN
Ts = As x fs = 405.440 kN
Pn = 2029.153 + 59.877 - 405.440 = 1683.589 kN
Mn' = 2029.153 x (230.000 - 99.468/2) + 59.877 x (230.000 - 90.00)
= 374.170 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0024 ＜ 0.0100 (e' = e + Xp - dc = 222.248 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5357.715 kN ≥ Pn = 1683.589 kN
ΦPn = 0.78 x 1683.589 = 1318.811 kN ≥ Pu = 143.437 kN ∴ O.K
ΦMn = ΦPn x 0.145 = 191.571 kN.m ≥ Mu = 20.836 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.656 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 153.58 |  | 39.756 |  | 56.857 |  | 258.861
＊ 철근비 검토
As = 1013.600 mm² (인장중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0051) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 405440.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (6120000.0 x 150.00 + 405440.0 x 70.000 + 202720.0 x 210.000) / 6728160.0
= 146.987 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 90.000) / 138.000 (≤fy) = 208.696 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 95.428 kN
Ts = As x fs = 405.440 kN
Pb = 2392.920 + 95.428 - 405.440 = 2082.908 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 95.428 x (230.000 - 90.00)
- 2082.908 x (146.987 - 70.000)
= 263.030 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 126.280 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 65.772 mm, a = k1 x c = 55.906 mm 를 사용.
fs = 600 x (230.000 - 65.772) / 65.772 (≤fy) = 400.000 MPa
fs' = 600 x ( 65.772 - 90.000) / 65.772 (≤fy) = 88.516 MPa
Cc = 0.85 x 24.0 x 55.906 x 1000.000 = 1140.485 kN
Cs = As' x (fs' - 0.85 x fck) = 34.521 kN
Ts = As x fs = 405.440 kN
Pn = 1140.485 + 34.521 - 405.440 = 700.524 kN
Mn' = 1140.485 x (230.000 - 55.906/2) + 34.521 x (230.000 - 90.00)
= 235.265 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0073 ＜ 0.0100 (e' = e + Xp - dc = 335.848 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5357.715 kN ≥ Pn = 700.524 kN
ΦPn = 0.78 x 700.524 = 548.744 kN ≥ Pu = 153.580 kN ∴ O.K
ΦMn = ΦPn x 0.259 = 142.048 kN.m ≥ Mu = 39.756 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.996 kN
≥ Vu (= 56.857 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 366.667 |  | 296.667 |  | 133.294 |  | 41.815 |  | 56.227 |  | 313.704
＊ 철근비 검토
As = 1013.600 mm² (인장중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0041) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 366.7 x 1000.0 = 7480000.0 N
Cs = As x fy = 405440.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (7480000.0 x 183.33 + 405440.0 x 70.000 + 202720.0 x 276.667) / 8088160.0
= 179.991 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 178.000 mm, ab = k1 x cb = 151.300 mm
fs' = 600 x (178.000 - 90.000) / 178.000 (≤fy) = 296.629 MPa
Cc = 0.85 x 24.0 x 151.300 x 1000.000 = 3086.520 kN
Cs = As' x (fs' - 0.85 x fck) = 139.993 kN
Ts = As x fs = 405.440 kN
Pb = 3086.520 + 139.993 - 405.440 = 2821.073 kN
Mb = 3086.520 x (296.667 - 151.300/2) + 139.993 x (296.667 - 90.00)
- 2821.073 x (179.991 - 70.000)
= 400.810 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 142.077 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 67.960 mm, a = k1 x c = 57.766 mm 를 사용.
fs = 600 x (296.667 - 67.960) / 67.960 (≤fy) = 400.000 MPa
fs' = 600 x ( 67.960 - 90.000) / 67.960 (≤fy) = 57.820 MPa
Cc = 0.85 x 24.0 x 57.766 x 1000.000 = 1178.434 kN
Cs = As' x (fs' - 0.85 x fck) = 18.964 kN
Ts = As x fs = 405.440 kN
Pn = 1178.434 + 18.964 - 405.440 = 754.030 kN
Mn' = 1178.434 x (296.667 - 57.766/2) + 18.964 x (296.667 - 90.00)
= 319.485 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0073 ＜ 0.0100 (e' = e + Xp - dc = 423.695 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6445.715 kN ≥ Pn = 754.030 kN
ΦPn = 0.78 x 754.030 = 590.657 kN ≥ Pu = 133.294 kN ∴ O.K
ΦMn = ΦPn x 0.314 = 185.291 kN.m ≥ Mu = 41.815 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.316 kN
≥ Vu (= 56.227 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 210 |  | 143.437 |  | 12.13 |  | 0 |  | 84.568
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 1013.600 mm² (압축중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0051) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 405440.0 N
Xp = (6120000.0 x 150.00 + 202720.0 x 90.000 + 405440.0 x 230.000) / 6728160.0
= 153.013 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 126.000 mm, ab = k1 x cb = 107.100 mm
fs' = 600 x (126.000 - 70.000) / 126.000 (≤fy) = 266.667 MPa
Cc = 0.85 x 24.0 x 107.100 x 1000.000 = 2184.840 kN
Cs = As' x (fs' - 0.85 x fck) = 249.616 kN
Ts = As x fs = 202.720 kN
Pb = 2184.840 + 249.616 - 202.720 = 2231.736 kN
Mb = 2184.840 x (210.000 - 107.100/2) + 249.616 x (210.000 - 70.00)
- 2231.736 x (153.013 - 90.000)
= 236.136 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 105.808 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 157.628 mm, a = k1 x c = 133.984 mm 를 사용.
fs = 600 x (210.000 - 157.628) / 157.628 (≤fy) = 199.349 MPa
fs' = 600 x (157.628 - 70.000) / 157.628 (≤fy) = 333.550 MPa
Cc = 0.85 x 24.0 x 133.984 x 1000.000 = 2733.273 kN
Cs = As' x (fs' - 0.85 x fck) = 317.409 kN
Ts = As x fs = 101.030 kN
Pn = 2733.273 + 317.409 - 101.030 = 2949.651 kN
Mn' = 2733.273 x (210.000 - 133.984/2) + 317.409 x (210.000 - 70.00)
= 435.317 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0014 ＜ 0.0100 (e' = e + Xp - dc = 147.581 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 90.00 = 210.000 mm
c = 600.00 / (600.00+400.00) x 210.000 = 126.000 mm, a = k1 x c = 107.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (210.00-126.00) / 126.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5357.715 kN ≥ Pn = 2949.651 kN
ΦPn = 0.78 x 2949.651 = 2310.560 kN ≥ Pu = 143.437 kN ∴ O.K
ΦMn = ΦPn x 0.085 = 195.400 kN.m ≥ Mu = 12.130 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 210.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 210.00 = 132.990 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 143.437 |  | 20.836 |  | 0 |  | 145.261
＊ 철근비 검토
As = 1013.600 mm² (인장중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0051) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 405440.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (6120000.0 x 150.00 + 405440.0 x 70.000 + 202720.0 x 210.000) / 6728160.0
= 146.987 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 90.000) / 138.000 (≤fy) = 208.696 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 95.428 kN
Ts = As x fs = 405.440 kN
Pb = 2392.920 + 95.428 - 405.440 = 2082.908 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 95.428 x (230.000 - 90.00)
- 2082.908 x (146.987 - 70.000)
= 263.030 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 126.280 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 117.021 mm, a = k1 x c = 99.468 mm 를 사용.
fs = 600 x (230.000 - 117.021) / 117.021 (≤fy) = 400.000 MPa
fs' = 600 x (117.021 - 90.000) / 117.021 (≤fy) = 138.546 MPa
Cc = 0.85 x 24.0 x 99.468 x 1000.000 = 2029.153 kN
Cs = As' x (fs' - 0.85 x fck) = 59.877 kN
Ts = As x fs = 405.440 kN
Pn = 2029.153 + 59.877 - 405.440 = 1683.589 kN
Mn' = 2029.153 x (230.000 - 99.468/2) + 59.877 x (230.000 - 90.00)
= 374.170 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0024 ＜ 0.0100 (e' = e + Xp - dc = 222.248 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5357.715 kN ≥ Pn = 1683.589 kN
ΦPn = 0.78 x 1683.589 = 1318.811 kN ≥ Pu = 143.437 kN ∴ O.K
ΦMn = ΦPn x 0.145 = 191.571 kN.m ≥ Mu = 20.836 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.656 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 153.58 |  | 39.756 |  | 56.857 |  | 258.861
＊ 철근비 검토
As = 1013.600 mm² (인장중심 = 70.00 mm) , 1단 : H13- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0051) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 405440.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (6120000.0 x 150.00 + 405440.0 x 70.000 + 202720.0 x 210.000) / 6728160.0
= 146.987 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 90.000) / 138.000 (≤fy) = 208.696 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 95.428 kN
Ts = As x fs = 405.440 kN
Pb = 2392.920 + 95.428 - 405.440 = 2082.908 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 95.428 x (230.000 - 90.00)
- 2082.908 x (146.987 - 70.000)
= 263.030 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 126.280 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 65.772 mm, a = k1 x c = 55.906 mm 를 사용.
fs = 600 x (230.000 - 65.772) / 65.772 (≤fy) = 400.000 MPa
fs' = 600 x ( 65.772 - 90.000) / 65.772 (≤fy) = 88.516 MPa
Cc = 0.85 x 24.0 x 55.906 x 1000.000 = 1140.485 kN
Cs = As' x (fs' - 0.85 x fck) = 34.521 kN
Ts = As x fs = 405.440 kN
Pn = 1140.485 + 34.521 - 405.440 = 700.524 kN
Mn' = 1140.485 x (230.000 - 55.906/2) + 34.521 x (230.000 - 90.00)
= 235.265 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0073 ＜ 0.0100 (e' = e + Xp - dc = 335.848 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5357.715 kN ≥ Pn = 700.524 kN
ΦPn = 0.78 x 700.524 = 548.744 kN ≥ Pu = 153.580 kN ∴ O.K
ΦMn = ΦPn x 0.259 = 142.048 kN.m ≥ Mu = 39.756 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.996 kN
≥ Vu (= 56.857 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
2) 상부슬래브 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
3) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
4) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
5) 하부슬래브 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
6) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
7) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
8) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
9) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
10) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
11) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
12) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
13) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!
14) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1013.6 |  | × | 0.2 |  | = | 202.72 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 202.720 ----------> O.K !!!

## 절점부 검토
21. 절점부 검토
1) 절점 20
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 26.627 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 26.627 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 565.685 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 26.63 × 10^6 |  |  | = | 0.416 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 565.685²× 1000
∴ 절점부 보강철근 필요없음 !!!
2) 절점 1
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 24.796 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 24.796 kN.m
R = √(T1² + T2²) = 424.264 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 24.80 × 10^6 |  |  | = | 0.689 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 424.264²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 24.80 × 10^6 |  |  | = | 649.393 mm²
|  |  |  | R × fsa |  |  | 424.264 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 649.393 mm² - 506.800 mm²
[5 empty] | = | 142.593 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H13 @250 - 4EA
∴ Total As = 506.800 mm² > Req'd As (= 142.593 mm²) -------------> O.K !!!
3) 절점 14
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 26.627 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 26.627 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 565.685 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 26.63 × 10^6 |  |  | = | 0.416 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 565.685²× 1000
∴ 절점부 보강철근 필요없음 !!!
4) 절점 9
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 24.796 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 24.796 kN.m
R = √(T1² + T2²) = 424.264 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 24.80 × 10^6 |  |  | = | 0.689 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 424.264²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 24.80 × 10^6 |  |  | = | 649.393 mm²
|  |  |  | R × fsa |  |  | 424.264 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 649.393 mm² - 506.800 mm²
[5 empty] | = | 142.593 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H13 @250 - 4EA
∴ Total As = 506.800 mm² > Req'd As (= 142.593 mm²) -------------> O.K !!!

## 사용성 검토
22. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 296.667 |  | H13 - 8.0EA |  |  | 125 | 664.961 | O.K |  | 5.32
2 | 상부슬래브 : 중앙부 |  | 210 |  | H13 - 8.0EA |  |  | 125 | 356.183 | O.K |  | 2.849
3 | 상부슬래브 : 단지점부(우측) |  | 296.667 |  | H13 - 8.0EA |  |  | 125 | 664.961 | O.K |  | 5.32
4 | 하부슬래브 : 단지점부(좌측) |  | 230 |  | H13 - 8.0EA |  |  | 125 | 527.478 | O.K |  | 4.22
5 | 하부슬래브 : 중앙부 |  | 210 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 486.691 | O.K |  | 3.894
6 | 하부슬래브 : 단지점부(우측) |  | 230 |  | H13 - 8.0EA |  |  | 125 | 527.478 | O.K |  | 4.22
7 | 좌측벽체 : 상부 |  | 296.667 |  | H13 - 8.0EA |  |  | 125 | 664.961 | O.K |  | 5.32
8 | 좌측벽체 : 중앙부 |  | 210 |  | H13 - 4.0EA |  |  | 250 | 921.92 | O.K |  | 3.688
9 | 좌측벽체 : 중앙부(부모멘트) |  | 230 |  | H13 - 8.0EA |  |  | 125 | 1013.967 | O.K |  | 8.112
10 | 좌측벽체 : 하부 |  | 230 |  | H13 - 8.0EA |  |  | 125 | 527.478 | O.K |  | 4.22
11 | 우측벽체 : 상부 |  | 296.667 |  | H13 - 8.0EA |  |  | 125 | 664.961 | O.K |  | 5.32
12 | 우측벽체 : 중앙부 |  | 210 |  | H13 - 4.0EA |  |  | 250 | 921.921 | O.K |  | 3.688
13 | 우측벽체 : 중앙부(부모멘트) |  | 230 |  | H13 - 8.0EA |  |  | 125 | 1013.967 | O.K |  | 8.112
14 | 우측벽체 : 하부 |  | 230 |  | H13 - 8.0EA |  |  | 125 | 527.478 | O.K |  | 4.22
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 26.627 x 1000000 / [1013.600 x (296.667 - 58.175/3)]
= 94.742 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x296.7/(7x1013.600)]
= 58.175 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 94.74) - 2.5 x 63.50 = 672.45 mm
300 x (210 / fs) = 300 x (210 / 94.74) = 664.96 mm
Sa는 작은 값인 664.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 664.96 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 27.413 x 1000000 / [1013.600 x (210.000 - 47.953/3)]
= 139.397 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x210.0/(7x1013.600)]
= 47.953 mm
Use As = 1013.600 mm² (철근도심 : 90.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 13/2 = 83.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 139.40) - 2.5 x 83.50 = 356.18 mm
300 x (210 / fs) = 300 x (210 / 139.40) = 451.95 mm
Sa는 작은 값인 356.18 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 356.18 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 26.627 x 1000000 / [1013.600 x (296.667 - 58.175/3)]
= 94.742 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x296.7/(7x1013.600)]
= 58.175 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 94.74) - 2.5 x 63.50 = 672.45 mm
300 x (210 / fs) = 300 x (210 / 94.74) = 664.96 mm
Sa는 작은 값인 664.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 664.96 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 24.796 x 1000000 / [1013.600 x (230.000 - 50.473/3)]
= 114.758 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(7x1013.600)]
= 50.473 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 114.76) - 2.5 x 63.50 = 527.48 mm
300 x (210 / fs) = 300 x (210 / 114.76) = 548.98 mm
Sa는 작은 값인 527.48 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 527.48 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 28.473 x 1000000 / [1301.200 x (210.000 - 53.410/3)]
= 113.851 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x210.0/(7x1301.200)]
= 53.410 mm
Use As = 1301.200 mm² (철근도심 : 90.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 113.85) - 2.5 x 82.00 = 486.69 mm
300 x (210 / fs) = 300 x (210 / 113.85) = 553.35 mm
Sa는 작은 값인 486.69 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 486.69 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 24.796 x 1000000 / [1013.600 x (230.000 - 50.473/3)]
= 114.758 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(7x1013.600)]
= 50.473 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 114.76) - 2.5 x 63.50 = 527.48 mm
300 x (210 / fs) = 300 x (210 / 114.76) = 548.98 mm
Sa는 작은 값인 527.48 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 527.48 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 26.627 x 1000000 / [1013.600 x (296.667 - 58.175/3)]
= 94.742 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x296.7/(7x1013.600)]
= 58.175 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 94.74) - 2.5 x 63.50 = 672.45 mm
300 x (210 / fs) = 300 x (210 / 94.74) = 664.96 mm
Sa는 작은 값인 664.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 664.96 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 6.866 x 1000000 / [506.800 x (210.000 - 35.215/3)]
= 68.336 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x506.800/1000.0 + 7x506.800/1000.0 x √[(1 + 2x1000.0x210.0/(7x506.800)]
= 35.215 mm
Use As = 506.800 mm² (철근도심 : 90.000 mm)
1단 : H13 - 4.0 EA (= 506.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 13/2 = 83.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 68.34) - 2.5 x 83.50 = 943.65 mm
300 x (210 / fs) = 300 x (210 / 68.34) = 921.92 mm
Sa는 작은 값인 921.92 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 921.92 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 13.425 x 1000000 / [1013.600 x (230.000 - 50.473/3)]
= 62.132 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(7x1013.600)]
= 50.473 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 62.13) - 2.5 x 63.50 = 1108.71 mm
300 x (210 / fs) = 300 x (210 / 62.13) = 1013.97 mm
Sa는 작은 값인 1013.97 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 1013.97 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 24.796 x 1000000 / [1013.600 x (230.000 - 50.473/3)]
= 114.758 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(7x1013.600)]
= 50.473 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 114.76) - 2.5 x 63.50 = 527.48 mm
300 x (210 / fs) = 300 x (210 / 114.76) = 548.98 mm
Sa는 작은 값인 527.48 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 527.48 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 26.627 x 1000000 / [1013.600 x (296.667 - 58.175/3)]
= 94.742 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x296.7/(7x1013.600)]
= 58.175 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 94.74) - 2.5 x 63.50 = 672.45 mm
300 x (210 / fs) = 300 x (210 / 94.74) = 664.96 mm
Sa는 작은 값인 664.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 664.96 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 6.866 x 1000000 / [506.800 x (210.000 - 35.215/3)]
= 68.336 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x506.800/1000.0 + 7x506.800/1000.0 x √[(1 + 2x1000.0x210.0/(7x506.800)]
= 35.215 mm
Use As = 506.800 mm² (철근도심 : 90.000 mm)
1단 : H13 - 4.0 EA (= 506.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 13/2 = 83.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 68.34) - 2.5 x 83.50 = 943.65 mm
300 x (210 / fs) = 300 x (210 / 68.34) = 921.92 mm
Sa는 작은 값인 921.92 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 921.92 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 13.425 x 1000000 / [1013.600 x (230.000 - 50.473/3)]
= 62.132 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(7x1013.600)]
= 50.473 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 62.13) - 2.5 x 63.50 = 1108.71 mm
300 x (210 / fs) = 300 x (210 / 62.13) = 1013.97 mm
Sa는 작은 값인 1013.97 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 1013.97 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 24.796 x 1000000 / [1013.600 x (230.000 - 50.473/3)]
= 114.758 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1013.600/1000.0 + 7x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(7x1013.600)]
= 50.473 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : H13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 114.76) - 2.5 x 63.50 = 527.48 mm
300 x (210 / fs) = 300 x (210 / 114.76) = 548.98 mm
Sa는 작은 값인 527.48 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 527.48 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 2.300 m
- fy = 400 MPa
- 부재두께(T) = 0.30 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 2.300 / 28
T = 0.082 m < 0.300 m -----------> O.K

## 기초 지지력 검토
23. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  | = | 68.6 |  | / | 2.6 |  | = | 26.385 |  | kN/m²
|  |  | - 상부연직하중 |  |  | = | 57 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  | 11.355 |  | kN/m²
3) 내부 수압
|  |  | - 암거1내부수압 |  |  | = | 16 |  | kN/m²
4) 최대 지반 반력
|  |  | Qmax | = | 26.385 |  | + | 57 |  | + | 11.355 |  | + | 16
|  |  |  | = | 110.739 |  | kN/m²

## 주철근 조립도
24. 주철근 조립도