## 표지
H2-30C 구조계산서
| ▣ 구조형식 |  | : | 지중 2 련 암거
( 내공 : 2@(3M ⅹ 3M) )
| ▣ 토 피(FH) |  | = | 8.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 거더,기둥,내측벽체 검토
[5 empty] | 22. | 절점부 검토
[5 empty] | 23. | 사용성 검토
[5 empty] | 24. | 기초 지지력 검토
[5 empty] | 25. | 주철근 조립도

## 설계요약표
1. 설계 요약표
H2-30C (토피=8.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 8.0m
안정(지지력)검토 | Qmax = 235.800 kN/m²
단면 위치 | 내구성검토 |  |  | 단 면 검 토 | [13 empty] | 절 점 부 보 강
| 균열검토 |  |  | 휨 검 토 | [6 empty] | 전 단 검 토
| 철근간격 mm | 최대간격 mm |  | 사용철근 | Mu kN.m |  | ΦMn kN.m |  | S.F |  | 사용철근 |  | Vu kN |  | ΦVn kN |  | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 487.802 |  | H16 - 8.0EA | 217.062 |  | 394.929 |  | 1.82 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.538 | 0.637 | H19 @250 - 4EA
상부슬래브 : 제 1경간 중앙부 | 125 | 442.154 |  | H16 - 8.0EA | 172.096 |  | 321.103 |  | 1.87 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 지점부 | 125 | 491.324 |  | H19 - 4.0EA + H16 - 4.0EA | 261.597 |  | 480.052 |  | 1.84 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 중앙부 | 125 | 442.16 |  | H16 - 8.0EA | 172.094 |  | 321.103 |  | 1.87 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 단지점부(우측) | 125 | 487.793 |  | H16 - 8.0EA | 217.065 |  | 394.929 |  | 1.82 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.538 | 0.637 | H19 @250 - 4EA
하부슬래브 : 단지점부(좌측) | 125 | 463.957 |  | H16 - 8.0EA | 192.515 |  | 331.907 |  | 1.72 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.758 | 0.637 | H19 @250 - 4EA
하부슬래브 : 제 1경간 중앙부 | 125 | 455.753 |  | H16 - 8.0EA | 169.102 |  | 321.103 |  | 1.9 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 지점부 | 125 | 398.474 |  | H19 - 8.0EA | 299.852 |  | 473.436 |  | 1.58 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 중앙부 | 125 | 455.636 |  | H16 - 8.0EA | 169.134 |  | 321.103 |  | 1.9 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 단지점부(우측) | 125 | 463.967 |  | H16 - 8.0EA | 192.512 |  | 331.907 |  | 1.72 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.758 | 0.637 | H19 @250 - 4EA
좌측벽체 : 상부 | 125 | 355.596 |  | H16 - 8.0EA | 217.062 |  | 623.465 |  | 2.87 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부 | 250 | 369.088 |  | H16 - 4.0EA | 79.457 |  | 684.546 |  | 8.62 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부(부모멘트) | 250 | 784.192 |  | H16 - 4.0EA | 119.729 |  | 516.177 |  | 4.31 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 하부 | 125 | 312.874 |  | H16 - 8.0EA | 192.515 |  | 499.397 |  | 2.59 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 상부 | 125 | 355.589 |  | H16 - 8.0EA | 217.065 |  | 623.473 |  | 2.87 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부 | 250 | 369.086 |  | H16 - 4.0EA | 79.457 |  | 684.547 |  | 8.62 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부(부모멘트) | 250 | 784.175 |  | H16 - 4.0EA | 119.732 |  | 516.077 |  | 4.31 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 하부 | 125 | 312.882 |  | H16 - 8.0EA | 192.512 |  | 499.436 |  | 2.59 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
기둥단면검토
기둥 위치 | 기둥 형태 |  | 사용 철근 |  |  | e |  | eb |  | Pu |  | ΦPn |  | Mu |  | ΦMn |  | 비 고
[6 empty] | (mm) |  | (mm) |  | (kN) |  | (kN) |  | (kN.m) |  | (kN.m)
P1 | 벽 체 |  | H13 |  |  | 0.003 |  | 135.217 |  | 977.684 |  | 4443.277 |  | 0.003 |  | 0.015 |  | 축력 최대시
[6 empty] | 44.534 |  | 135.217 |  | 542.059 |  | 5182.981 |  | 24.14 |  | 230.821 |  | 모멘트 최대시

## 설계조건
2. 설계조건
1) 구조형식
- 지중 2 련 암거 ( 내공 : 2@(3M ⅹ 3M), 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 10 |  | kN/m² |  | (∵ 토피 : | 8 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.700 × 1.000 = 0.700 |  |  |  | 0.02858 |  | 1~20,26~37
| 2 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 21~25,38~42
| 3 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 43
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.275 | 0.35 | 29 |  | 5.45 |  | 4.05
| 2 |  | 0.55 | 0.35 | 30 |  | 4.58 |  | 4.05
| 3 |  | 0.854 | 0.35 | 31 |  | 3.95 |  | 4.05
| 4 |  | 1.18 | 0.35 | 32 |  | 3.75 |  | 4.05
| 5 |  | 1.433 | 0.35 | 33 |  | 3.55 |  | 4.05
| 6 |  | 2.013 | 0.35 | 34 |  | 2.92 |  | 4.05
| 7 |  | 2.592 | 0.35 | 35 |  | 2.05 |  | 4.05
| 8 |  | 2.92 | 0.35 | 36 |  | 1.18 |  | 4.05
| 9 |  | 3.171 | 0.35 | 37 |  | 0.55 |  | 4.05
| 10 |  | 3.55 | 0.35 | 38 |  | 0.275 |  | 4.05
| 11 |  | 3.75 | 0.35 | 39 |  | 0.275 |  | 3.7
| 12 |  | 3.95 | 0.35 | 40 |  | 0.275 |  | 3.22
| 13 |  | 4.329 | 0.35 | 41 |  | 0.275 |  | 1.18
| 14 |  | 4.58 | 0.35 | 42 |  | 0.275 |  | 0.7
| 15 |  | 4.908 | 0.35 | 43 |  | 0.275 |  | -0.15
| 16 |  | 5.488 | 0.35 | 44 |  | 0.854 |  | -0.15
| 17 |  | 6.067 | 0.35 | 45 |  | 1.433 |  | -0.15
| 18 |  | 6.32 | 0.35 | 46 |  | 2.013 |  | -0.15
| 19 |  | 6.646 | 0.35 | 47 |  | 2.592 |  | -0.15
| 20 |  | 6.95 | 0.35 | 48 |  | 3.171 |  | -0.15
| 21 |  | 7.225 | 0.35 | 49 |  | 3.75 |  | -0.15
| 22 |  | 7.225 | 0.7 | 50 |  | 4.329 |  | -0.15
| 23 |  | 7.225 | 1.18 | 51 |  | 4.908 |  | -0.15
| 24 |  | 7.225 | 3.22 | 52 |  | 5.488 |  | -0.15
| 25 |  | 7.225 | 3.7 | 53 |  | 6.067 |  | -0.15
| 26 |  | 7.225 | 4.05 | 54 |  | 6.646 |  | -0.15
| 27 |  | 6.95 | 4.05 | 55 |  | 7.225 |  | -0.15
| 28 |  | 6.32 | 4.05

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.700 × 1.000 = 0.700 |  |  |  | 0.02858 |  | 1~20,33~41,43~52
| 2 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 21~32,53~64
| 3 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 65
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.275 | 0.35 | 54 |  | 0.275 |  | 3.7
| 2 |  | 0.55 | 0.35 | 55 |  | 0.275 |  | 3.521
| 3 |  | 0.854 | 0.35 | 56 |  | 0.275 |  | 3.22
| 4 |  | 1.18 | 0.35 | 57 |  | 0.275 |  | 2.993
| 5 |  | 1.433 | 0.35 | 58 |  | 0.275 |  | 2.464
| 6 |  | 2.013 | 0.35 | 59 |  | 0.275 |  | 2.2
| 7 |  | 2.592 | 0.35 | 60 |  | 0.275 |  | 1.936
| 8 |  | 2.92 | 0.35 | 61 |  | 0.275 |  | 1.407
| 9 |  | 3.171 | 0.35 | 62 |  | 0.275 |  | 1.18
| 10 |  | 3.55 | 0.35 | 63 |  | 0.275 |  | 0.879
| 11 |  | 3.75 | 0.35 | 64 |  | 0.275 |  | 0.7
| 12 |  | 3.95 | 0.35 | 65 |  | 0.275 |  | -0.15
| 13 |  | 4.329 | 0.35 | 66 |  | 0.854 |  | -0.15
| 14 |  | 4.58 | 0.35 | 67 |  | 1.433 |  | -0.15
| 15 |  | 4.908 | 0.35 | 68 |  | 2.013 |  | -0.15
| 16 |  | 5.488 | 0.35 | 69 |  | 2.592 |  | -0.15
| 17 |  | 6.067 | 0.35 | 70 |  | 3.171 |  | -0.15
| 18 |  | 6.32 | 0.35 | 71 |  | 3.75 |  | -0.15
| 19 |  | 6.646 | 0.35 | 72 |  | 4.329 |  | -0.15
| 20 |  | 6.95 | 0.35 | 73 |  | 4.908 |  | -0.15
| 21 |  | 7.225 | 0.35 | 74 |  | 5.488 |  | -0.15
| 22 |  | 7.225 | 0.7 | 75 |  | 6.067 |  | -0.15
| 23 |  | 7.225 | 0.879 | 76 |  | 6.646 |  | -0.15
| 24 |  | 7.225 | 1.18 | 77 |  | 7.225 |  | -0.15
| 25 |  | 7.225 | 1.407 | 78 |  | 7.725 |  | 0.35
| 26 |  | 7.225 | 1.936 | 79 |  | 7.725 |  | 0.879
| 27 |  | 7.225 | 2.2 | 80 |  | 7.725 |  | 1.407
| 28 |  | 7.225 | 2.464 | 81 |  | 7.725 |  | 1.936
| 29 |  | 7.225 | 2.993 | 82 |  | 7.725 |  | 2.464
| 30 |  | 7.225 | 3.22 | 83 |  | 7.725 |  | 2.993
| 31 |  | 7.225 | 3.521 | 84 |  | 7.725 |  | 3.521
| 32 |  | 7.225 | 3.7 | 85 |  | 7.725 |  | 4.05
| 33 |  | 7.225 | 4.05 | 86 |  | 7.225 |  | 4.55
| 34 |  | 6.95 | 4.05 | 87 |  | 6.646 |  | 4.55
| 35 |  | 6.646 | 4.05 | 88 |  | 6.067 |  | 4.55
| 36 |  | 6.32 | 4.05 | 89 |  | 5.487 |  | 4.55
| 37 |  | 6.067 | 4.05 | 90 |  | 4.908 |  | 4.55
| 38 |  | 5.487 | 4.05 | 91 |  | 4.329 |  | 4.55
| 39 |  | 4.908 | 4.05 | 92 |  | 3.75 |  | 4.55
| 40 |  | 4.58 | 4.05 | 93 |  | 3.171 |  | 4.55
| 41 |  | 4.329 | 4.05 | 94 |  | 2.592 |  | 4.55
| 42 |  | 3.95 | 4.05 | 95 |  | 2.012 |  | 4.55
| 43 |  | 3.75 | 4.05 | 96 |  | 1.433 |  | 4.55
| 44 |  | 3.55 | 4.05 | 97 |  | 0.854 |  | 4.55
| 45 |  | 3.171 | 4.05 | 98 |  | 0.275 |  | 4.55
| 46 |  | 2.92 | 4.05 | 99 |  | -0.225 |  | 4.05
| 47 |  | 2.592 | 4.05 | 100 |  | -0.225 |  | 3.521
| 48 |  | 2.012 | 4.05 | 101 |  | -0.225 |  | 2.993
| 49 |  | 1.433 | 4.05 | 102 |  | -0.225 |  | 2.464
| 50 |  | 1.18 | 4.05 | 103 |  | -0.225 |  | 1.936
| 51 |  | 0.854 | 4.05 | 104 |  | -0.225 |  | 1.407
| 52 |  | 0.55 | 4.05 | 105 |  | -0.225 |  | 0.879
| 53 |  | 0.275 | 4.05 | 106 |  | -0.225 |  | 0.35

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 7.500 × 7.500 ) |  |  | = | 7.5 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 7.500 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 12521.981 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.550/2 + 0.579/2) = 7069 kN/m |  |  |  |  | 1,21
| Kv2 |  |  | Kvⅹ(0.579/2 + 0.579/2) = 7250 kN/m |  |  |  |  | 3,5~7,9,11,13,15~17,19
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 3.700m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 7.500 × 7.500 ) |  |  |  |  | = | 7.5 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 7.500 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 31501.96 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 31501.960 |  |  |  |  | = | 10500.65 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 7.500 × 7.500 ) |  |  |  |  | = | 7.5 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 7.500 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 31501.96 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 31501.960 |  |  |  |  | = | 10500.65 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 4.400 × 4.400 ) |  |  |  |  | = | 4.4 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 4.400 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 46994.18 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 46994.180 |  |  |  |  | = | 15664.73 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.579/2 + 0.550/2) = 17783 kN/m | [8 empty] | 33,53
|  | Ksb1 |  |  | Ksbⅹ(0.579/2 + 0.550/2) = 5928 kN/m
|  | Kv2 |  |  | Kvⅹ(0.579/2 + 0.579/2) = 18240 kN/m | [8 empty] | 35,37~39,41,43,45,47~49,51
|  | Ksb2 |  |  | Ksbⅹ(0.579/2 + 0.579/2) = 6080 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(0.529/2 + 0.700/2) = 28878 kN/m | [8 empty] | 1,21,33,53
|  | Kss1 |  |  | Kssⅹ(0.529/2 + 0.700/2) = 9626 kN/m
|  | Kh2 |  |  | Khⅹ(0.529/2 + 0.529/2) = 24860 kN/m | [8 empty] | 23,25~26,28~29,31,55,57~58,60~61,63
|  | Kss2 |  |  | Kssⅹ(0.529/2 + 0.529/2) = 8287 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.550/2 + 0.579/2) = 17783 kN/m | [8 empty] | 1,21
|  | Ksb1 |  |  | Ksbⅹ(0.550/2 + 0.579/2) = 5928 kN/m
|  | Kv2 |  |  | Kvⅹ(0.579/2 + 0.579/2) = 18240 kN/m | [8 empty] | 3,5~7,9,11,13,15~17,19
|  | Ksb2 |  |  | Ksbⅹ(0.579/2 + 0.579/2) = 6080 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 8.00 × 19.00 |  |  |  |  | = | 152 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 152 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 상부 슬래브에 작용하는 하중 (Wl1) - 토피 4m 이상
|  |  | - Wl1 |  | = | 10.000 kN/m²
② 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (8.350 × 19.000) × 0.500 | [9 empty] | = | 79.325 | kN/m²
|  | - Wh2 |  | = | 79.325 + 0.350 × 19.000 × 0.500 | [9 empty] | = | 82.65 | kN/m²
|  | - Wh3 |  | = | 82.650 + 0.480 × 19.000 × 0.500 | [9 empty] | = | 87.21 | kN/m²
|  | - Wh4 |  | = | 87.210 + 2.040 × 19.000 × 0.500 | [9 empty] | = | 106.59 | kN/m²
|  | - Wh5 |  | = | 106.590 + 0.480 × 19.000 × 0.500 | [9 empty] | = | 111.15 | kN/m²
|  | - Wh6 |  | = | 111.150 + 0.350 × 19.000 × 0.500 | [9 empty] | = | 114.475 | kN/m²
5) 암거내부수압
- Win = 24.000 kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 11.7 |  | 197.3 |  |  |  | 19 |  |  | 0.237
|  | 계 | [11 empty] | 0.237
Tg = 1.25 Tg' = 1.25 × 0.237 = 0.296 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.296 / 2π × 2.617 = 0.123 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 8.35 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 12.05 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.123 × 0.296 × cos(π× 8.350 / (2 × 30.000)) = 0.006684
U(Zb) = 2 / π²× 0.123 × 0.296 × cos(π× 12.050 / (2 × 30.000)) = 0.005957
Po = Ksb,top × (U(Zu) - U(Zb))
= 10500.650 × (0.006684 - 0.005957) = 7.634 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 8.35 |  | 46994.18 |  |  |  | 0.006684 |  |  |  |  | 0.000727 |  | 34.165
|  | 8.7 |  | 46994.18 |  |  |  | 0.006625 |  |  |  |  | 0.000668 |  | 31.392
|  | 8.879 |  | 46994.18 |  |  |  | 0.006595 |  |  |  |  | 0.000638 |  | 29.982
|  | 9.18 |  | 46994.18 |  |  |  | 0.006542 |  |  |  |  | 0.000585 |  | 27.492
|  | 9.407 |  | 46994.18 |  |  |  | 0.006501 |  |  |  |  | 0.000544 |  | 25.565
|  | 9.936 |  | 46994.18 |  |  |  | 0.006402 |  |  |  |  | 0.000445 |  | 20.912
|  | 10.2 |  | 46994.18 |  |  |  | 0.00635 |  |  |  |  | 0.000393 |  | 18.469
|  | 10.464 |  | 46994.18 |  |  |  | 0.006298 |  |  |  |  | 0.000341 |  | 16.025
|  | 10.993 |  | 46994.18 |  |  |  | 0.006189 |  |  |  |  | 0.000232 |  | 10.903
|  | 11.22 |  | 46994.18 |  |  |  | 0.006141 |  |  |  |  | 0.000184 |  | 8.647
|  | 11.521 |  | 46994.18 |  |  |  | 0.006076 |  |  |  |  | 0.000119 |  | 5.592
|  | 11.7 |  | 46994.18 |  |  |  | 0.006036 |  |  |  |  | 7.9e-05 |  | 3.713
|  | 12.05 |  | 46994.18 |  |  |  | 0.005957 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000164 = 3.090 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000228 = 4.300 kN/m²
Vs = (Vu - Vb) / 2 = (3.090 + 4.300) / 2 = 3.700 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.700 × 24.500 × 0.160 × (1 - 0.015 × 8.350) = 2.400 kN/m²
② 하부슬래브
fb = 0.700 × 24.500 × 0.160 × (1 - 0.015 × 12.050) = 2.248 kN/m²
③ 중간벽체
fu1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 8.350) = 1.372 kN/m²
fb1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 12.050) = 1.285 kN/m²
④ 측벽
f1 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.350) = 1.886 kN/m²
f2 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.700) = 1.875 kN/m²
f3 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.879) = 1.869 kN/m²
f4 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.180) = 1.859 kN/m²
f5 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.407) = 1.852 kN/m²
f6 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.936) = 1.835 kN/m²
f7 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.200) = 1.826 kN/m²
f8 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.464) = 1.818 kN/m²
f9 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.993) = 1.800 kN/m²
f10 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.220) = 1.793 kN/m²
f11 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.521) = 1.783 kN/m²
f12 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.700) = 1.778 kN/m²
f13 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 12.050) = 1.766 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)
6) CASE6 - 암거내부수압

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 0.875, h = 8.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
2) 극한하중 기둥최대편심 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
3) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1
| 2 |  | 1 | 0.875 |  | 1 | 1
| 3 |  | 1 | 0.875 | 1 | 0.5 | 0.5
4) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | DOF=U1 KE=7068.66 CE=0.99999 K=7068.66 OPEN=0
NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| JOINT | DOF=U1 KE=7250.23 CE=0.99999 K=7250.23 OPEN=0
1 X= 0.275 Y= 0.000 Z= 0.350
| 2 X= 0.550 Y= 0.000 Z= 0.350 | FRAME SECTION
| 3 X= 0.854 Y= 0.000 Z= 0.350 | NAME=1 MAT=CONC SH=R T=0.7, 1
| 4 X= 1.180 Y= 0.000 Z= 0.350 | NAME=2 MAT=CONC SH=R T=0.55, 1
| 5 X= 1.433 Y= 0.000 Z= 0.350 | NAME=3 MAT=CONC SH=R T=0.4, 1
6 X= 2.013 Y= 0.000 Z= 0.350
| 7 X= 2.592 Y= 0.000 Z= 0.350 | FRAME
| 8 X= 2.920 Y= 0.000 Z= 0.350 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 9 X= 3.171 Y= 0.000 Z= 0.350 | 2 J= 2, 3 SEC=1 NSEG=1 ANG=180
| 10 X= 3.550 Y= 0.000 Z= 0.350 | 3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 11 X= 3.750 Y= 0.000 Z= 0.350 | 4 J= 4, 5 SEC=1 NSEG=1 ANG=180
| 12 X= 3.950 Y= 0.000 Z= 0.350 | 5 J= 5, 6 SEC=1 NSEG=2 ANG=180
| 13 X= 4.329 Y= 0.000 Z= 0.350 | 6 J= 6, 7 SEC=1 NSEG=2 ANG=180
| 14 X= 4.580 Y= 0.000 Z= 0.350 | 7 J= 7, 8 SEC=1 NSEG=1 ANG=180
| 15 X= 4.908 Y= 0.000 Z= 0.350 | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| 16 X= 5.488 Y= 0.000 Z= 0.350 | 9 J= 9, 10 SEC=1 NSEG=1 ANG=180
| 17 X= 6.067 Y= 0.000 Z= 0.350 | 10 J= 10, 11 SEC=1 NSEG=1 ANG=180
| 18 X= 6.320 Y= 0.000 Z= 0.350 | 11 J= 11, 12 SEC=1 NSEG=1 ANG=180
| 19 X= 6.646 Y= 0.000 Z= 0.350 | 12 J= 12, 13 SEC=1 NSEG=1 ANG=180
| 20 X= 6.950 Y= 0.000 Z= 0.350 | 13 J= 13, 14 SEC=1 NSEG=1 ANG=180
| 21 X= 7.225 Y= 0.000 Z= 0.350 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=180
| 22 X= 7.225 Y= 0.000 Z= 0.700 | 15 J= 15, 16 SEC=1 NSEG=2 ANG=180
| 23 X= 7.225 Y= 0.000 Z= 1.180 | 16 J= 16, 17 SEC=1 NSEG=2 ANG=180
| 24 X= 7.225 Y= 0.000 Z= 3.220 | 17 J= 17, 18 SEC=1 NSEG=1 ANG=180
| 25 X= 7.225 Y= 0.000 Z= 3.700 | 18 J= 18, 19 SEC=1 NSEG=1 ANG=180
| 26 X= 7.225 Y= 0.000 Z= 4.050 | 19 J= 19, 20 SEC=1 NSEG=1 ANG=180
| 27 X= 6.950 Y= 0.000 Z= 4.050 | 20 J= 20, 21 SEC=1 NSEG=1 ANG=180
| 28 X= 6.320 Y= 0.000 Z= 4.050 | 21 J= 21, 22 SEC=2 NSEG=1 ANG=0
| 29 X= 5.450 Y= 0.000 Z= 4.050 | 22 J= 22, 23 SEC=2 NSEG=1 ANG=0
| 30 X= 4.580 Y= 0.000 Z= 4.050 | 23 J= 23, 24 SEC=2 NSEG=4 ANG=0
| 31 X= 3.950 Y= 0.000 Z= 4.050 | 24 J= 24, 25 SEC=2 NSEG=1 ANG=0
| 32 X= 3.750 Y= 0.000 Z= 4.050 | 25 J= 25, 26 SEC=2 NSEG=1 ANG=0
| 33 X= 3.550 Y= 0.000 Z= 4.050 | 26 J= 26, 27 SEC=1 NSEG=1 ANG=0
| 34 X= 2.920 Y= 0.000 Z= 4.050 | 27 J= 27, 28 SEC=1 NSEG=2 ANG=0
| 35 X= 2.050 Y= 0.000 Z= 4.050 | 28 J= 28, 29 SEC=1 NSEG=2 ANG=0
| 36 X= 1.180 Y= 0.000 Z= 4.050 | 29 J= 29, 30 SEC=1 NSEG=2 ANG=0
| 37 X= 0.550 Y= 0.000 Z= 4.050 | 30 J= 30, 31 SEC=1 NSEG=2 ANG=0
| 38 X= 0.275 Y= 0.000 Z= 4.050 | 31 J= 31, 32 SEC=1 NSEG=1 ANG=0
| 39 X= 0.275 Y= 0.000 Z= 3.700 | 32 J= 32, 33 SEC=1 NSEG=1 ANG=0
| 40 X= 0.275 Y= 0.000 Z= 3.220 | 33 J= 33, 34 SEC=1 NSEG=2 ANG=0
| 41 X= 0.275 Y= 0.000 Z= 1.180 | 34 J= 34, 35 SEC=1 NSEG=2 ANG=0
| 42 X= 0.275 Y= 0.000 Z= 0.700 | 35 J= 35, 36 SEC=1 NSEG=2 ANG=0
| 43 X= 0.275 Y= 0.000 Z= -0.150 | 36 J= 36, 37 SEC=1 NSEG=2 ANG=0
| 44 X= 0.854 Y= 0.000 Z= -0.150 | 37 J= 37, 38 SEC=1 NSEG=1 ANG=0
| 45 X= 1.433 Y= 0.000 Z= -0.150 | 38 J= 38, 39 SEC=2 NSEG=1 ANG=180
| 46 X= 2.013 Y= 0.000 Z= -0.150 | 39 J= 39, 40 SEC=2 NSEG=1 ANG=180
| 47 X= 2.592 Y= 0.000 Z= -0.150 | 40 J= 40, 41 SEC=2 NSEG=4 ANG=180
| 48 X= 3.171 Y= 0.000 Z= -0.150 | 41 J= 41, 42 SEC=2 NSEG=1 ANG=180
| 49 X= 3.750 Y= 0.000 Z= -0.150 | 42 J= 42, 1 SEC=2 NSEG=1 ANG=180
| 50 X= 4.329 Y= 0.000 Z= -0.150 | 43 J= 32, 11 SEC=3 NSEG=4 ANG=0
51 X= 4.908 Y= 0.000 Z= -0.150
| 52 X= 5.488 Y= 0.000 Z= -0.150 | NLLINK
| 53 X= 6.067 Y= 0.000 Z= -0.150 | 1 J=1,43 NLP=SP1 ANG=0
| 54 X= 6.646 Y= 0.000 Z= -0.150 | 2 J=3,44 NLP=SP2 ANG=0
| 55 X= 7.225 Y= 0.000 Z= -0.150 | 3 J=5,45 NLP=SP2 ANG=0
4 J=6,46 NLP=SP2 ANG=0
| RESTRAINT | 5 J=7,47 NLP=SP2 ANG=0
| ADD=43 DOF=U1, U2, U3, R1, R2, R3 | 6 J=9,48 NLP=SP2 ANG=0
| ADD=44 DOF=U1, U2, U3, R1, R2, R3 | 7 J=11,49 NLP=SP2 ANG=0
| ADD=45 DOF=U1, U2, U3, R1, R2, R3 | 8 J=13,50 NLP=SP2 ANG=0
| ADD=46 DOF=U1, U2, U3, R1, R2, R3 | 9 J=15,51 NLP=SP2 ANG=0
| ADD=47 DOF=U1, U2, U3, R1, R2, R3 | 10 J=16,52 NLP=SP2 ANG=0
| ADD=48 DOF=U1, U2, U3, R1, R2, R3 | 11 J=17,53 NLP=SP2 ANG=0
| ADD=49 DOF=U1, U2, U3, R1, R2, R3 | 12 J=19,54 NLP=SP2 ANG=0
| ADD=50 DOF=U1, U2, U3, R1, R2, R3 | 13 J=21,55 NLP=SP1 ANG=0
ADD=51 DOF=U1, U2, U3, R1, R2, R3
| ADD=52 DOF=U1, U2, U3, R1, R2, R3 | LOAD
| ADD=53 DOF=U1, U2, U3, R1, R2, R3 | NAME=SELFWGT SW=1
| ADD=54 DOF=U1, U2, U3, R1, R2, R3 | NAME=NWDEAD
| ADD=55 DOF=U1, U2, U3, R1, R2, R3 | TYPE=Distributed Span
ADD=26 RD=0,1 UZ=-152,-152
| SPRING | ADD=27 RD=0,1 UZ=-152,-152
| ADD=1 U1=1e+010 | ADD=28 RD=0,1 UZ=-152,-152
ADD=29 RD=0,1 UZ=-152,-152
| MATERIAL | ADD=30 RD=0,1 UZ=-152,-152
| NAME=CONC IDES=C M=0.0001 W=24.5 | ADD=31 RD=0,1 UZ=-152,-152
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | ADD=32 RD=0,1 UZ=-152,-152
ADD=33 RD=0,1 UZ=-152,-152
| NLPROP | ADD=34 RD=0,1 UZ=-152,-152
| ADD=35 RD=0,1 UZ=-152,-152 | LOAD=HORLIVE SF=0.8 AT=1
| ADD=36 RD=0,1 UZ=-152,-152 | LOAD=NWSOFULL SF=0.8 AT=1
| ADD=37 RD=0,1 UZ=-152,-152 | NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| NAME=LIVEFULL | LOAD=SELFWGT SF=1.2 AT=1
| TYPE=Distributed Span | LOAD=NWDEAD SF=1.4 AT=1
| ADD=26 RD=0,1 UZ=-10,-10 | LOAD=LIVEFULL SF=1.6 AT=1
| ADD=27 RD=0,1 UZ=-10,-10 | LOAD=HORLIVE SF=1.6 AT=1
| ADD=28 RD=0,1 UZ=-10,-10 | LOAD=NWSOFULL SF=1.6 AT=1
| ADD=29 RD=0,1 UZ=-10,-10 | NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=30 RD=0,1 UZ=-10,-10 | LOAD=SELFWGT SF=0.9 AT=1
| ADD=31 RD=0,1 UZ=-10,-10 | LOAD=NWDEAD SF=1.4 AT=1
| ADD=32 RD=0,1 UZ=-10,-10 | LOAD=HORLIVE SF=1.6 AT=1
| ADD=33 RD=0,1 UZ=-10,-10 | LOAD=NWSOFULL SF=1.6 AT=1
| ADD=34 RD=0,1 UZ=-10,-10 | NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=35 RD=0,1 UZ=-10,-10 | LOAD=SELFWGT SF=1.2 AT=1
| ADD=36 RD=0,1 UZ=-10,-10 | LOAD=NWDEAD SF=1.4 AT=1
| ADD=37 RD=0,1 UZ=-10,-10 | LOAD=LIVEFULL SF=1.6 AT=1
| NAME=HORLIVE | LOAD=HORLIVE SF=0.8 AT=1
| TYPE=Distributed Span | LOAD=NWSOFULL SF=0.8 AT=1
| ADD=21 RD=0,1 UX=-5,-5 | NAME=HIST7 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=22 RD=0,1 UX=-5,-5 | LOAD=SELFWGT SF=1 AT=1
| ADD=23 RD=0,1 UX=-5,-5 | LOAD=NWDEAD SF=0.875 AT=1
| ADD=24 RD=0,1 UX=-5,-5 | LOAD=LIVEFULL SF=1 AT=1
| ADD=25 RD=0,1 UX=-5,-5 | LOAD=HORLIVE SF=1 AT=1
| ADD=38 RD=0,1 UX=5,5 | LOAD=NWSOFULL SF=1 AT=1
| ADD=39 RD=0,1 UX=5,5 | LOAD=INWATER SF=1 AT=1
| ADD=40 RD=0,1 UX=5,5 | NAME=HIST8 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=41 RD=0,1 UX=5,5 | LOAD=SELFWGT SF=1 AT=1
| ADD=42 RD=0,1 UX=5,5 | LOAD=NWDEAD SF=0.875 AT=1
| NAME=NWSOFULL | LOAD=HORLIVE SF=1 AT=1
| TYPE=Distributed Span | LOAD=NWSOFULL SF=1 AT=1
| ADD=21 RD=0,1 UX=-114.475,-111.15 | LOAD=INWATER SF=1 AT=1
| ADD=22 RD=0,1 UX=-111.15,-106.59 | NAME=HIST9 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=23 RD=0,1 UX=-106.59,-87.21 | LOAD=SELFWGT SF=1 AT=1
| ADD=24 RD=0,1 UX=-87.21,-82.65 | LOAD=NWDEAD SF=0.875 AT=1
| ADD=25 RD=0,1 UX=-82.65,-79.325 | LOAD=LIVEFULL SF=1 AT=1
| ADD=38 RD=0,1 UX=79.325,82.65 | LOAD=HORLIVE SF=0.5 AT=1
| ADD=39 RD=0,1 UX=82.65,87.21 | LOAD=NWSOFULL SF=0.5 AT=1
| ADD=40 RD=0,1 UX=87.21,106.59 | LOAD=INWATER SF=1 AT=1
ADD=41 RD=0,1 UX=106.59,111.15
| ADD=42 RD=0,1 UX=111.15,114.475 | COMBO
| NAME=INWATER | NAME=ULTIMATE TYPE=ENVE
| TYPE=Distributed Span | HIST=HIST1 SF=1
| ADD=2 RD=0,1 UZ=-24,-24 | HIST=HIST2 SF=1
| ADD=3 RD=0,1 UZ=-24,-24 | HIST=HIST3 SF=1
| ADD=4 RD=0,1 UZ=-24,-24 | HIST=HIST4 SF=1
| ADD=5 RD=0,1 UZ=-24,-24 | HIST=HIST5 SF=1
| ADD=6 RD=0,1 UZ=-24,-24 | HIST=HIST6 SF=1
| ADD=7 RD=0,1 UZ=-24,-24 | NAME=SERVICE TYPE=ENVE
| ADD=8 RD=0,1 UZ=-24,-24 | HIST=HIST7 SF=1
| ADD=9 RD=0,1 UZ=-24,-24 | HIST=HIST8 SF=1
| ADD=12 RD=0,1 UZ=-24,-24 | HIST=HIST9 SF=1
ADD=13 RD=0,1 UZ=-24,-24
| ADD=14 RD=0,1 UZ=-24,-24 | OUTPUT
| ADD=15 RD=0,1 UZ=-24,-24 | ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
| ADD=16 RD=0,1 UZ=-24,-24 | ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*
ADD=17 RD=0,1 UZ=-24,-24
ADD=18 RD=0,1 UZ=-24,-24
ADD=19 RD=0,1 UZ=-24,-24
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=HORLIVE
LOAD=NWSOFULL
LOAD=INWATER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | 80 X= 7.725 Y= 0.000 Z= 1.407
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 81 X= 7.725 Y= 0.000 Z= 1.936
82 X= 7.725 Y= 0.000 Z= 2.464
| JOINT | 83 X= 7.725 Y= 0.000 Z= 2.993
| 1 X= 0.275 Y= 0.000 Z= 0.350 | 84 X= 7.725 Y= 0.000 Z= 3.521
| 2 X= 0.550 Y= 0.000 Z= 0.350 | 85 X= 7.725 Y= 0.000 Z= 4.050
| 3 X= 0.854 Y= 0.000 Z= 0.350 | 86 X= 7.225 Y= 0.000 Z= 4.550
| 4 X= 1.180 Y= 0.000 Z= 0.350 | 87 X= 6.646 Y= 0.000 Z= 4.550
| 5 X= 1.433 Y= 0.000 Z= 0.350 | 88 X= 6.067 Y= 0.000 Z= 4.550
| 6 X= 2.013 Y= 0.000 Z= 0.350 | 89 X= 5.487 Y= 0.000 Z= 4.550
| 7 X= 2.592 Y= 0.000 Z= 0.350 | 90 X= 4.908 Y= 0.000 Z= 4.550
| 8 X= 2.920 Y= 0.000 Z= 0.350 | 91 X= 4.329 Y= 0.000 Z= 4.550
| 9 X= 3.171 Y= 0.000 Z= 0.350 | 92 X= 3.750 Y= 0.000 Z= 4.550
| 10 X= 3.550 Y= 0.000 Z= 0.350 | 93 X= 3.171 Y= 0.000 Z= 4.550
| 11 X= 3.750 Y= 0.000 Z= 0.350 | 94 X= 2.592 Y= 0.000 Z= 4.550
| 12 X= 3.950 Y= 0.000 Z= 0.350 | 95 X= 2.012 Y= 0.000 Z= 4.550
| 13 X= 4.329 Y= 0.000 Z= 0.350 | 96 X= 1.433 Y= 0.000 Z= 4.550
| 14 X= 4.580 Y= 0.000 Z= 0.350 | 97 X= 0.854 Y= 0.000 Z= 4.550
| 15 X= 4.908 Y= 0.000 Z= 0.350 | 98 X= 0.275 Y= 0.000 Z= 4.550
| 16 X= 5.488 Y= 0.000 Z= 0.350 | 99 X= -0.225 Y= 0.000 Z= 4.050
| 17 X= 6.067 Y= 0.000 Z= 0.350 | 100 X= -0.225 Y= 0.000 Z= 3.521
| 18 X= 6.320 Y= 0.000 Z= 0.350 | 101 X= -0.225 Y= 0.000 Z= 2.993
| 19 X= 6.646 Y= 0.000 Z= 0.350 | 102 X= -0.225 Y= 0.000 Z= 2.464
| 20 X= 6.950 Y= 0.000 Z= 0.350 | 103 X= -0.225 Y= 0.000 Z= 1.936
| 21 X= 7.225 Y= 0.000 Z= 0.350 | 104 X= -0.225 Y= 0.000 Z= 1.407
| 22 X= 7.225 Y= 0.000 Z= 0.700 | 105 X= -0.225 Y= 0.000 Z= 0.879
| 23 X= 7.225 Y= 0.000 Z= 0.879 | 106 X= -0.225 Y= 0.000 Z= 0.350
24 X= 7.225 Y= 0.000 Z= 1.180
| 25 X= 7.225 Y= 0.000 Z= 1.407 | RESTRAINT
| 26 X= 7.225 Y= 0.000 Z= 1.936 | ADD=65 DOF=U1, U2, U3, R1, R2, R3
| 27 X= 7.225 Y= 0.000 Z= 2.200 | ADD=66 DOF=U1, U2, U3, R1, R2, R3
| 28 X= 7.225 Y= 0.000 Z= 2.464 | ADD=67 DOF=U1, U2, U3, R1, R2, R3
| 29 X= 7.225 Y= 0.000 Z= 2.993 | ADD=68 DOF=U1, U2, U3, R1, R2, R3
| 30 X= 7.225 Y= 0.000 Z= 3.220 | ADD=69 DOF=U1, U2, U3, R1, R2, R3
| 31 X= 7.225 Y= 0.000 Z= 3.521 | ADD=70 DOF=U1, U2, U3, R1, R2, R3
| 32 X= 7.225 Y= 0.000 Z= 3.700 | ADD=71 DOF=U1, U2, U3, R1, R2, R3
| 33 X= 7.225 Y= 0.000 Z= 4.050 | ADD=72 DOF=U1, U2, U3, R1, R2, R3
| 34 X= 6.950 Y= 0.000 Z= 4.050 | ADD=73 DOF=U1, U2, U3, R1, R2, R3
| 35 X= 6.646 Y= 0.000 Z= 4.050 | ADD=74 DOF=U1, U2, U3, R1, R2, R3
| 36 X= 6.320 Y= 0.000 Z= 4.050 | ADD=75 DOF=U1, U2, U3, R1, R2, R3
| 37 X= 6.067 Y= 0.000 Z= 4.050 | ADD=76 DOF=U1, U2, U3, R1, R2, R3
| 38 X= 5.487 Y= 0.000 Z= 4.050 | ADD=77 DOF=U1, U2, U3, R1, R2, R3
| 39 X= 4.908 Y= 0.000 Z= 4.050 | ADD=78 DOF=U1, U2, U3, R1, R2, R3
| 40 X= 4.580 Y= 0.000 Z= 4.050 | ADD=79 DOF=U1, U2, U3, R1, R2, R3
| 41 X= 4.329 Y= 0.000 Z= 4.050 | ADD=80 DOF=U1, U2, U3, R1, R2, R3
| 42 X= 3.950 Y= 0.000 Z= 4.050 | ADD=81 DOF=U1, U2, U3, R1, R2, R3
| 43 X= 3.750 Y= 0.000 Z= 4.050 | ADD=82 DOF=U1, U2, U3, R1, R2, R3
| 44 X= 3.550 Y= 0.000 Z= 4.050 | ADD=83 DOF=U1, U2, U3, R1, R2, R3
| 45 X= 3.171 Y= 0.000 Z= 4.050 | ADD=84 DOF=U1, U2, U3, R1, R2, R3
| 46 X= 2.920 Y= 0.000 Z= 4.050 | ADD=85 DOF=U1, U2, U3, R1, R2, R3
| 47 X= 2.592 Y= 0.000 Z= 4.050 | ADD=86 DOF=U1, U2, U3, R1, R2, R3
| 48 X= 2.012 Y= 0.000 Z= 4.050 | ADD=87 DOF=U1, U2, U3, R1, R2, R3
| 49 X= 1.433 Y= 0.000 Z= 4.050 | ADD=88 DOF=U1, U2, U3, R1, R2, R3
| 50 X= 1.180 Y= 0.000 Z= 4.050 | ADD=89 DOF=U1, U2, U3, R1, R2, R3
| 51 X= 0.854 Y= 0.000 Z= 4.050 | ADD=90 DOF=U1, U2, U3, R1, R2, R3
| 52 X= 0.550 Y= 0.000 Z= 4.050 | ADD=91 DOF=U1, U2, U3, R1, R2, R3
| 53 X= 0.275 Y= 0.000 Z= 4.050 | ADD=92 DOF=U1, U2, U3, R1, R2, R3
| 54 X= 0.275 Y= 0.000 Z= 3.700 | ADD=93 DOF=U1, U2, U3, R1, R2, R3
| 55 X= 0.275 Y= 0.000 Z= 3.521 | ADD=94 DOF=U1, U2, U3, R1, R2, R3
| 56 X= 0.275 Y= 0.000 Z= 3.220 | ADD=95 DOF=U1, U2, U3, R1, R2, R3
| 57 X= 0.275 Y= 0.000 Z= 2.993 | ADD=96 DOF=U1, U2, U3, R1, R2, R3
| 58 X= 0.275 Y= 0.000 Z= 2.464 | ADD=97 DOF=U1, U2, U3, R1, R2, R3
| 59 X= 0.275 Y= 0.000 Z= 2.200 | ADD=98 DOF=U1, U2, U3, R1, R2, R3
| 60 X= 0.275 Y= 0.000 Z= 1.936 | ADD=99 DOF=U1, U2, U3, R1, R2, R3
| 61 X= 0.275 Y= 0.000 Z= 1.407 | ADD=100 DOF=U1, U2, U3, R1, R2, R3
| 62 X= 0.275 Y= 0.000 Z= 1.180 | ADD=101 DOF=U1, U2, U3, R1, R2, R3
| 63 X= 0.275 Y= 0.000 Z= 0.879 | ADD=102 DOF=U1, U2, U3, R1, R2, R3
| 64 X= 0.275 Y= 0.000 Z= 0.700 | ADD=103 DOF=U1, U2, U3, R1, R2, R3
| 65 X= 0.275 Y= 0.000 Z= -0.150 | ADD=104 DOF=U1, U2, U3, R1, R2, R3
| 66 X= 0.854 Y= 0.000 Z= -0.150 | ADD=105 DOF=U1, U2, U3, R1, R2, R3
| 67 X= 1.433 Y= 0.000 Z= -0.150 | ADD=106 DOF=U1, U2, U3, R1, R2, R3
68 X= 2.013 Y= 0.000 Z= -0.150
| 69 X= 2.592 Y= 0.000 Z= -0.150 | SPRING
| 70 X= 3.171 Y= 0.000 Z= -0.150 | ADD=1 U1=5927.62 U3=9625.98
| 71 X= 3.750 Y= 0.000 Z= -0.150 | ADD=3 U1=6079.88
| 72 X= 4.329 Y= 0.000 Z= -0.150 | ADD=5 U1=6079.88
| 73 X= 4.908 Y= 0.000 Z= -0.150 | ADD=6 U1=6079.88
| 74 X= 5.488 Y= 0.000 Z= -0.150 | ADD=7 U1=6079.88
| 75 X= 6.067 Y= 0.000 Z= -0.150 | ADD=9 U1=6079.88
| 76 X= 6.646 Y= 0.000 Z= -0.150 | ADD=11 U1=6079.88
| 77 X= 7.225 Y= 0.000 Z= -0.150 | ADD=13 U1=6079.88
| 78 X= 7.725 Y= 0.000 Z= 0.350 | ADD=15 U1=6079.88
| 79 X= 7.725 Y= 0.000 Z= 0.879 | ADD=16 U1=6079.88
| ADD=17 U1=6079.88 | 38 J= 38, 39 SEC=1 NSEG=2 ANG=0
| ADD=19 U1=6079.88 | 39 J= 39, 40 SEC=1 NSEG=1 ANG=0
| ADD=21 U1=5927.62 U3=9625.98 | 40 J= 40, 41 SEC=1 NSEG=1 ANG=0
| ADD=23 U3=8286.64 | 41 J= 41, 42 SEC=1 NSEG=1 ANG=0
| ADD=25 U3=8286.64 | 42 J= 42, 43 NSEG=1 ANG=0
| ADD=26 U3=8286.64 | 43 J= 43, 44 SEC=1 NSEG=1 ANG=0
| ADD=28 U3=8286.64 | 44 J= 44, 45 SEC=1 NSEG=1 ANG=0
| ADD=29 U3=8286.64 | 45 J= 45, 46 SEC=1 NSEG=1 ANG=0
| ADD=31 U3=8286.64 | 46 J= 46, 47 SEC=1 NSEG=1 ANG=0
| ADD=33 U1=5927.62 U3=9625.98 | 47 J= 47, 48 SEC=1 NSEG=2 ANG=0
| ADD=35 U1=6079.88 | 48 J= 48, 49 SEC=1 NSEG=2 ANG=0
| ADD=37 U1=6079.88 | 49 J= 49, 50 SEC=1 NSEG=1 ANG=0
| ADD=38 U1=6079.88 | 50 J= 50, 51 SEC=1 NSEG=1 ANG=0
| ADD=39 U1=6079.88 | 51 J= 51, 52 SEC=1 NSEG=1 ANG=0
| ADD=41 U1=6079.88 | 52 J= 52, 53 SEC=1 NSEG=1 ANG=0
| ADD=43 U1=6079.88 | 53 J= 53, 54 SEC=2 NSEG=1 ANG=180
| ADD=45 U1=6079.88 | 54 J= 54, 55 SEC=2 NSEG=1 ANG=180
| ADD=47 U1=6079.88 | 55 J= 55, 56 SEC=2 NSEG=1 ANG=180
| ADD=48 U1=6079.88 | 56 J= 56, 57 SEC=2 NSEG=1 ANG=180
| ADD=49 U1=6079.88 | 57 J= 57, 58 SEC=2 NSEG=2 ANG=180
| ADD=51 U1=6079.88 | 58 J= 58, 59 SEC=2 NSEG=1 ANG=180
| ADD=53 U1=5927.62 U3=9625.98 | 59 J= 59, 60 SEC=2 NSEG=1 ANG=180
| ADD=55 U3=8286.64 | 60 J= 60, 61 SEC=2 NSEG=2 ANG=180
| ADD=57 U3=8286.64 | 61 J= 61, 62 SEC=2 NSEG=1 ANG=180
| ADD=58 U3=8286.64 | 62 J= 62, 63 SEC=2 NSEG=1 ANG=180
| ADD=60 U3=8286.64 | 63 J= 63, 64 SEC=2 NSEG=1 ANG=180
| ADD=61 U3=8286.64 | 64 J= 64, 1 SEC=2 NSEG=1 ANG=180
| ADD=63 U3=8286.64 | 65 J= 43, 11 SEC=3 NSEG=4 ANG=0
| MATERIAL | NLLINK
| NAME=CONC IDES=C M=0.0001 W=24.5 | 1 J=1,65 NLP=SP1 ANG=0
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | 2 J=3,66 NLP=SP2 ANG=0
3 J=5,67 NLP=SP2 ANG=0
| NLPROP | 4 J=6,68 NLP=SP2 ANG=0
| NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 5 J=7,69 NLP=SP2 ANG=0
| DOF=U1 KE=17782.9 CE=0.99999 K=17782.9 OPEN=0 | 6 J=9,70 NLP=SP2 ANG=0
| NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 7 J=11,71 NLP=SP2 ANG=0
| DOF=U1 KE=18239.6 CE=0.99999 K=18239.6 OPEN=0 | 8 J=13,72 NLP=SP2 ANG=0
| NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 9 J=15,73 NLP=SP2 ANG=0
| DOF=U1 KE=28877.9 CE=0.99999 K=28877.9 OPEN=0 | 10 J=16,74 NLP=SP2 ANG=0
| NAME=SP4 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 11 J=17,75 NLP=SP2 ANG=0
| DOF=U1 KE=24859.9 CE=0.99999 K=24859.9 OPEN=0 | 12 J=19,76 NLP=SP2 ANG=0
13 J=21,77 NLP=SP1 ANG=0
| FRAME SECTION | 14 J=21,78 NLP=SP3 ANG=180
| NAME=1 MAT=CONC SH=R T=0.7, 1 | 15 J=23,79 NLP=SP4 ANG=180
| NAME=2 MAT=CONC SH=R T=0.55, 1 | 16 J=25,80 NLP=SP4 ANG=180
| NAME=3 MAT=CONC SH=R T=0.4, 1 | 17 J=26,81 NLP=SP4 ANG=180
18 J=28,82 NLP=SP4 ANG=180
| FRAME | 19 J=29,83 NLP=SP4 ANG=180
| 1 J= 1, 2 SEC=1 NSEG=1 ANG=180 | 20 J=31,84 NLP=SP4 ANG=180
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | 21 J=33,85 NLP=SP3 ANG=180
| 3 J= 3, 4 SEC=1 NSEG=1 ANG=180 | 22 J=33,86 NLP=SP1 ANG=0
| 4 J= 4, 5 SEC=1 NSEG=1 ANG=180 | 23 J=35,87 NLP=SP2 ANG=0
| 5 J= 5, 6 SEC=1 NSEG=2 ANG=180 | 24 J=37,88 NLP=SP2 ANG=0
| 6 J= 6, 7 SEC=1 NSEG=2 ANG=180 | 25 J=38,89 NLP=SP2 ANG=0
| 7 J= 7, 8 SEC=1 NSEG=1 ANG=180 | 26 J=39,90 NLP=SP2 ANG=0
| 8 J= 8, 9 SEC=1 NSEG=1 ANG=180 | 27 J=41,91 NLP=SP2 ANG=0
| 9 J= 9, 10 SEC=1 NSEG=1 ANG=180 | 28 J=43,92 NLP=SP2 ANG=0
| 10 J= 10, 11 SEC=1 NSEG=1 ANG=180 | 29 J=45,93 NLP=SP2 ANG=0
| 11 J= 11, 12 SEC=1 NSEG=1 ANG=180 | 30 J=47,94 NLP=SP2 ANG=0
| 12 J= 12, 13 SEC=1 NSEG=1 ANG=180 | 31 J=48,95 NLP=SP2 ANG=0
| 13 J= 13, 14 SEC=1 NSEG=1 ANG=180 | 32 J=49,96 NLP=SP2 ANG=0
| 14 J= 14, 15 SEC=1 NSEG=1 ANG=180 | 33 J=51,97 NLP=SP2 ANG=0
| 15 J= 15, 16 SEC=1 NSEG=2 ANG=180 | 34 J=53,98 NLP=SP1 ANG=0
| 16 J= 16, 17 SEC=1 NSEG=2 ANG=180 | 35 J=53,99 NLP=SP3 ANG=180
| 17 J= 17, 18 SEC=1 NSEG=1 ANG=180 | 36 J=55,100 NLP=SP4 ANG=180
| 18 J= 18, 19 SEC=1 NSEG=1 ANG=180 | 37 J=57,101 NLP=SP4 ANG=180
| 19 J= 19, 20 SEC=1 NSEG=1 ANG=180 | 38 J=58,102 NLP=SP4 ANG=180
| 20 J= 20, 21 SEC=1 NSEG=1 ANG=180 | 39 J=60,103 NLP=SP4 ANG=180
| 21 J= 21, 22 SEC=2 NSEG=1 ANG=0 | 40 J=61,104 NLP=SP4 ANG=180
| 22 J= 22, 23 SEC=2 NSEG=1 ANG=0 | 41 J=63,105 NLP=SP4 ANG=180
| 23 J= 23, 24 SEC=2 NSEG=1 ANG=0 | 42 J=1,106 NLP=SP3 ANG=180
24 J= 24, 25 SEC=2 NSEG=1 ANG=0
| 25 J= 25, 26 SEC=2 NSEG=2 ANG=0 | LOAD
| 26 J= 26, 27 SEC=2 NSEG=1 ANG=0 | NAME=SELFWGT SW=1
| 27 J= 27, 28 SEC=2 NSEG=1 ANG=0 | NAME=NWDEAD
| 28 J= 28, 29 SEC=2 NSEG=2 ANG=0 | TYPE=Distributed Span
| 29 J= 29, 30 SEC=2 NSEG=1 ANG=0 | ADD=33 RD=0,1 UZ=-152,-152
| 30 J= 30, 31 SEC=2 NSEG=1 ANG=0 | ADD=34 RD=0,1 UZ=-152,-152
| 31 J= 31, 32 SEC=2 NSEG=1 ANG=0 | ADD=35 RD=0,1 UZ=-152,-152
| 32 J= 32, 33 SEC=2 NSEG=1 ANG=0 | ADD=36 RD=0,1 UZ=-152,-152
| 33 J= 33, 34 SEC=1 NSEG=1 ANG=0 | ADD=37 RD=0,1 UZ=-152,-152
| 34 J= 34, 35 SEC=1 NSEG=1 ANG=0 | ADD=38 RD=0,1 UZ=-152,-152
| 35 J= 35, 36 SEC=1 NSEG=1 ANG=0 | ADD=39 RD=0,1 UZ=-152,-152
| 36 J= 36, 37 SEC=1 NSEG=1 ANG=0 | ADD=40 RD=0,1 UZ=-152,-152
| 37 J= 37, 38 SEC=1 NSEG=2 ANG=0 | ADD=41 RD=0,1 UZ=-152,-152
| ADD=42 RD=0,1 UZ=-152,-152 | ADD=4 RD=0,1 UX=-4.3,-4.3
| ADD=43 RD=0,1 UZ=-152,-152 | ADD=5 RD=0,1 UX=-4.3,-4.3
| ADD=44 RD=0,1 UZ=-152,-152 | ADD=6 RD=0,1 UX=-4.3,-4.3
| ADD=45 RD=0,1 UZ=-152,-152 | ADD=7 RD=0,1 UX=-4.3,-4.3
| ADD=46 RD=0,1 UZ=-152,-152 | ADD=8 RD=0,1 UX=-4.3,-4.3
| ADD=47 RD=0,1 UZ=-152,-152 | ADD=9 RD=0,1 UX=-4.3,-4.3
| ADD=48 RD=0,1 UZ=-152,-152 | ADD=10 RD=0,1 UX=-4.3,-4.3
| ADD=49 RD=0,1 UZ=-152,-152 | ADD=11 RD=0,1 UX=-4.3,-4.3
| ADD=50 RD=0,1 UZ=-152,-152 | ADD=12 RD=0,1 UX=-4.3,-4.3
| ADD=51 RD=0,1 UZ=-152,-152 | ADD=13 RD=0,1 UX=-4.3,-4.3
| ADD=52 RD=0,1 UZ=-152,-152 | ADD=14 RD=0,1 UX=-4.3,-4.3
| NAME=LIVEFULL | ADD=15 RD=0,1 UX=-4.3,-4.3
| TYPE=Distributed Span | ADD=16 RD=0,1 UX=-4.3,-4.3
| ADD=33 RD=0,1 UZ=-10,-10 | ADD=17 RD=0,1 UX=-4.3,-4.3
| ADD=34 RD=0,1 UZ=-10,-10 | ADD=18 RD=0,1 UX=-4.3,-4.3
| ADD=35 RD=0,1 UZ=-10,-10 | ADD=19 RD=0,1 UX=-4.3,-4.3
| ADD=36 RD=0,1 UZ=-10,-10 | ADD=20 RD=0,1 UX=-4.3,-4.3
| ADD=37 RD=0,1 UZ=-10,-10 | ADD=21 RD=0,1 UZ=3.7,3.7
| ADD=38 RD=0,1 UZ=-10,-10 | ADD=22 RD=0,1 UZ=3.7,3.7
| ADD=39 RD=0,1 UZ=-10,-10 | ADD=23 RD=0,1 UZ=3.7,3.7
| ADD=40 RD=0,1 UZ=-10,-10 | ADD=24 RD=0,1 UZ=3.7,3.7
| ADD=41 RD=0,1 UZ=-10,-10 | ADD=25 RD=0,1 UZ=3.7,3.7
| ADD=42 RD=0,1 UZ=-10,-10 | ADD=26 RD=0,1 UZ=3.7,3.7
| ADD=43 RD=0,1 UZ=-10,-10 | ADD=27 RD=0,1 UZ=3.7,3.7
| ADD=44 RD=0,1 UZ=-10,-10 | ADD=28 RD=0,1 UZ=3.7,3.7
| ADD=45 RD=0,1 UZ=-10,-10 | ADD=29 RD=0,1 UZ=3.7,3.7
| ADD=46 RD=0,1 UZ=-10,-10 | ADD=30 RD=0,1 UZ=3.7,3.7
| ADD=47 RD=0,1 UZ=-10,-10 | ADD=31 RD=0,1 UZ=3.7,3.7
| ADD=48 RD=0,1 UZ=-10,-10 | ADD=32 RD=0,1 UZ=3.7,3.7
| ADD=49 RD=0,1 UZ=-10,-10 | ADD=33 RD=0,1 UX=3.09,3.09
| ADD=50 RD=0,1 UZ=-10,-10 | ADD=34 RD=0,1 UX=3.09,3.09
| ADD=51 RD=0,1 UZ=-10,-10 | ADD=35 RD=0,1 UX=3.09,3.09
| ADD=52 RD=0,1 UZ=-10,-10 | ADD=36 RD=0,1 UX=3.09,3.09
| NAME=SEUPSLAB | ADD=37 RD=0,1 UX=3.09,3.09
| TYPE=Distributed Span | ADD=38 RD=0,1 UX=3.09,3.09
| ADD=33 RD=0,1 UX=7.634,7.634 | ADD=39 RD=0,1 UX=3.09,3.09
| ADD=34 RD=0,1 UX=7.634,7.634 | ADD=40 RD=0,1 UX=3.09,3.09
| ADD=35 RD=0,1 UX=7.634,7.634 | ADD=41 RD=0,1 UX=3.09,3.09
| ADD=36 RD=0,1 UX=7.634,7.634 | ADD=42 RD=0,1 UX=3.09,3.09
| ADD=37 RD=0,1 UX=7.634,7.634 | ADD=43 RD=0,1 UX=3.09,3.09
| ADD=38 RD=0,1 UX=7.634,7.634 | ADD=44 RD=0,1 UX=3.09,3.09
| ADD=39 RD=0,1 UX=7.634,7.634 | ADD=45 RD=0,1 UX=3.09,3.09
| ADD=40 RD=0,1 UX=7.634,7.634 | ADD=46 RD=0,1 UX=3.09,3.09
| ADD=41 RD=0,1 UX=7.634,7.634 | ADD=47 RD=0,1 UX=3.09,3.09
| ADD=42 RD=0,1 UX=7.634,7.634 | ADD=48 RD=0,1 UX=3.09,3.09
| ADD=43 RD=0,1 UX=7.634,7.634 | ADD=49 RD=0,1 UX=3.09,3.09
| ADD=44 RD=0,1 UX=7.634,7.634 | ADD=50 RD=0,1 UX=3.09,3.09
| ADD=45 RD=0,1 UX=7.634,7.634 | ADD=51 RD=0,1 UX=3.09,3.09
| ADD=46 RD=0,1 UX=7.634,7.634 | ADD=52 RD=0,1 UX=3.09,3.09
| ADD=47 RD=0,1 UX=7.634,7.634 | ADD=53 RD=0,1 UZ=-3.7,-3.7
| ADD=48 RD=0,1 UX=7.634,7.634 | ADD=54 RD=0,1 UZ=-3.7,-3.7
| ADD=49 RD=0,1 UX=7.634,7.634 | ADD=55 RD=0,1 UZ=-3.7,-3.7
| ADD=50 RD=0,1 UX=7.634,7.634 | ADD=56 RD=0,1 UZ=-3.7,-3.7
| ADD=51 RD=0,1 UX=7.634,7.634 | ADD=57 RD=0,1 UZ=-3.7,-3.7
| ADD=52 RD=0,1 UX=7.634,7.634 | ADD=58 RD=0,1 UZ=-3.7,-3.7
| NAME=SEWALL | ADD=59 RD=0,1 UZ=-3.7,-3.7
| TYPE=Distributed Span | ADD=60 RD=0,1 UZ=-3.7,-3.7
| ADD=21 RD=0,1 UX=0,3.7125 | ADD=61 RD=0,1 UZ=-3.7,-3.7
| ADD=22 RD=0,1 UX=3.7125,5.5923 | ADD=62 RD=0,1 UZ=-3.7,-3.7
| ADD=23 RD=0,1 UX=5.5923,8.6469 | ADD=63 RD=0,1 UZ=-3.7,-3.7
| ADD=24 RD=0,1 UX=8.6469,10.9026 | ADD=64 RD=0,1 UZ=-3.7,-3.7
| ADD=25 RD=0,1 UX=10.9026,16.025 | NAME=SEINER
| ADD=26 RD=0,1 UX=16.025,18.4687 | TYPE=Distributed Span
| ADD=27 RD=0,1 UX=18.4687,20.9124 | ADD=1 RD=0,1 UX=2.24802,2.24802
| ADD=28 RD=0,1 UX=20.9124,25.5648 | ADD=2 RD=0,1 UX=2.24802,2.24802
| ADD=29 RD=0,1 UX=25.5648,27.4916 | ADD=3 RD=0,1 UX=2.24802,2.24802
| ADD=30 RD=0,1 UX=27.4916,29.9823 | ADD=4 RD=0,1 UX=2.24802,2.24802
| ADD=31 RD=0,1 UX=29.9823,31.3921 | ADD=5 RD=0,1 UX=2.24802,2.24802
| ADD=32 RD=0,1 UX=31.3921,34.1648 | ADD=6 RD=0,1 UX=2.24802,2.24802
| ADD=53 RD=0,1 UX=34.1648,31.3921 | ADD=7 RD=0,1 UX=2.24802,2.24802
| ADD=54 RD=0,1 UX=31.3921,29.9823 | ADD=8 RD=0,1 UX=2.24802,2.24802
| ADD=55 RD=0,1 UX=29.9823,27.4916 | ADD=9 RD=0,1 UX=2.24802,2.24802
| ADD=56 RD=0,1 UX=27.4916,25.5648 | ADD=10 RD=0,1 UX=2.24802,2.24802
| ADD=57 RD=0,1 UX=25.5648,20.9124 | ADD=11 RD=0,1 UX=2.24802,2.24802
| ADD=58 RD=0,1 UX=20.9124,18.4687 | ADD=12 RD=0,1 UX=2.24802,2.24802
| ADD=59 RD=0,1 UX=18.4687,16.025 | ADD=13 RD=0,1 UX=2.24802,2.24802
| ADD=60 RD=0,1 UX=16.025,10.9026 | ADD=14 RD=0,1 UX=2.24802,2.24802
| ADD=61 RD=0,1 UX=10.9026,8.6469 | ADD=15 RD=0,1 UX=2.24802,2.24802
| ADD=62 RD=0,1 UX=8.6469,5.5923 | ADD=16 RD=0,1 UX=2.24802,2.24802
| ADD=63 RD=0,1 UX=5.5923,3.7125 | ADD=17 RD=0,1 UX=2.24802,2.24802
| ADD=64 RD=0,1 UX=3.7125,0 | ADD=18 RD=0,1 UX=2.24802,2.24802
| NAME=SEPRINSH | ADD=19 RD=0,1 UX=2.24802,2.24802
| TYPE=Distributed Span | ADD=20 RD=0,1 UX=2.24802,2.24802
| ADD=1 RD=0,1 UX=-4.3,-4.3 | ADD=21 RD=0,1 UX=1.7663,1.77762
| ADD=2 RD=0,1 UX=-4.3,-4.3 | ADD=22 RD=0,1 UX=1.77762,1.78341
| ADD=3 RD=0,1 UX=-4.3,-4.3 | ADD=23 RD=0,1 UX=1.78341,1.79315
ADD=24 RD=0,1 UX=1.79315,1.80049
ADD=25 RD=0,1 UX=1.80049,1.81759
ADD=26 RD=0,1 UX=1.81759,1.82613
ADD=27 RD=0,1 UX=1.82613,1.83467
ADD=28 RD=0,1 UX=1.83467,1.85178
ADD=29 RD=0,1 UX=1.85178,1.85912
ADD=30 RD=0,1 UX=1.85912,1.86885
ADD=31 RD=0,1 UX=1.86885,1.87464
ADD=32 RD=0,1 UX=1.87464,1.88596
ADD=33 RD=0,1 UX=2.40031,2.40031
ADD=34 RD=0,1 UX=2.40031,2.40031
ADD=35 RD=0,1 UX=2.40031,2.40031
ADD=36 RD=0,1 UX=2.40031,2.40031
ADD=37 RD=0,1 UX=2.40031,2.40031
ADD=38 RD=0,1 UX=2.40031,2.40031
ADD=39 RD=0,1 UX=2.40031,2.40031
ADD=40 RD=0,1 UX=2.40031,2.40031
ADD=41 RD=0,1 UX=2.40031,2.40031
ADD=42 RD=0,1 UX=2.40031,2.40031
ADD=43 RD=0,1 UX=2.40031,2.40031
ADD=44 RD=0,1 UX=2.40031,2.40031
ADD=45 RD=0,1 UX=2.40031,2.40031
ADD=46 RD=0,1 UX=2.40031,2.40031
ADD=47 RD=0,1 UX=2.40031,2.40031
ADD=48 RD=0,1 UX=2.40031,2.40031
ADD=49 RD=0,1 UX=2.40031,2.40031
ADD=50 RD=0,1 UX=2.40031,2.40031
ADD=51 RD=0,1 UX=2.40031,2.40031
ADD=52 RD=0,1 UX=2.40031,2.40031
ADD=53 RD=0,1 UX=1.88596,1.87464
ADD=54 RD=0,1 UX=1.87464,1.86885
ADD=55 RD=0,1 UX=1.86885,1.85912
ADD=56 RD=0,1 UX=1.85912,1.85178
ADD=57 RD=0,1 UX=1.85178,1.83467
ADD=58 RD=0,1 UX=1.83467,1.82613
ADD=59 RD=0,1 UX=1.82613,1.81759
ADD=60 RD=0,1 UX=1.81759,1.80049
ADD=61 RD=0,1 UX=1.80049,1.79315
ADD=62 RD=0,1 UX=1.79315,1.78341
ADD=63 RD=0,1 UX=1.78341,1.77762
ADD=64 RD=0,1 UX=1.77762,1.7663
ADD=65 RD=0,1 UX=1.37161,1.28458
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=SEUPSLAB
LOAD=SEWALL
LOAD=SEPRINSH
LOAD=SEINER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=1 AT=1
LOAD=SEWALL SF=1 AT=1
LOAD=SEPRINSH SF=1 AT=1
LOAD=SEINER SF=1 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=-1 AT=1
LOAD=SEWALL SF=-1 AT=1
LOAD=SEPRINSH SF=-1 AT=1
LOAD=SEINER SF=-1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 18 | ULTIMATE MIN | 0 | -312.3295 | 0 | 0
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 18 | ULTIMATE MIN | 1 | -312.3295 | 0 | -5.4213
| 1 | ULTIMATE MIN | 0 | -312.3307 | -335.131 | -192.5151 | 19 | ULTIMATE MAX | 0 | 0 | 347.0647 | 61.8424
| 1 | ULTIMATE MIN | 1 | -312.3307 | -340.7905 | -100.8741 | 19 | ULTIMATE MAX | 1 | 0 | 340.8084 | 0
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 19 | ULTIMATE MIN | 0 | -312.3295 | 0 | -5.4214
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 61.8295 | 19 | ULTIMATE MIN | 1 | -312.3295 | 0 | -100.8674
| 2 | ULTIMATE MIN | 0 | -312.3307 | -340.7905 | -100.8741 | 20 | ULTIMATE MAX | 0 | 0 | 340.8084 | 0
| 2 | ULTIMATE MIN | 1 | -312.3307 | -347.0469 | -5.434 | 20 | ULTIMATE MAX | 1 | 0 | 335.1489 | 0
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 61.8295 | 20 | ULTIMATE MIN | 0 | -312.3295 | 0 | -100.8674
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 114.7969 | 20 | ULTIMATE MIN | 1 | -312.3295 | 0 | -192.5124
| 3 | ULTIMATE MIN | 0 | -312.3307 | -189.44 | -5.434 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 3 | ULTIMATE MIN | 1 | -312.3307 | -196.1491 | 0 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 114.7969 | 21 | ULTIMATE MIN | 0 | -489.4485 | -312.3295 | -192.5124
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 157.4108 | 21 | ULTIMATE MIN | 1 | -483.789 | -246.3545 | -94.7971
| 4 | ULTIMATE MIN | 0 | -312.3307 | -196.1491 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 4 | ULTIMATE MIN | 1 | -312.3307 | -201.3558 | 0 | 22 | ULTIMATE MAX | 1 | 0 | 0 | 8.2821
| 5 | ULTIMATE MAX | 0 | 0 | 0 | 157.4108 | 22 | ULTIMATE MIN | 0 | -483.789 | -246.3545 | -94.7971
| 5 | ULTIMATE MAX | 0.5 | 0 | 0 | 162.3911 | 22 | ULTIMATE MIN | 1 | -476.0274 | -158.9023 | -23.7664
| 5 | ULTIMATE MAX | 1 | 0 | 0 | 169.1023 | 23 | ULTIMATE MAX | 0 | 0 | 0 | 8.2821
| 5 | ULTIMATE MIN | 0 | -312.3307 | -45.1663 | 0 | 23 | ULTIMATE MAX | 0.25 | 0 | 0 | 66.081
| 5 | ULTIMATE MIN | 0.5 | -312.3307 | -50.331 | 0 | 23 | ULTIMATE MAX | 0.5 | 0 | 16.0067 | 79.457
| 5 | ULTIMATE MIN | 1 | -312.3307 | -56.2992 | 0 | 23 | ULTIMATE MAX | 0.75 | 0 | 97.1804 | 50.4263
| 6 | ULTIMATE MAX | 0 | 0 | 130.541 | 169.1023 | 23 | ULTIMATE MAX | 1 | 0 | 174.4005 | 0
| 6 | ULTIMATE MAX | 0.5 | 0 | 124.5831 | 132.173 | 23 | ULTIMATE MIN | 0 | -476.0274 | -158.9023 | -23.7664
| 6 | ULTIMATE MAX | 1 | 0 | 118.6252 | 96.9686 | 23 | ULTIMATE MIN | 0.25 | -467.7807 | -69.8216 | 0
| 6 | ULTIMATE MIN | 0 | -312.3307 | 0 | 0 | 23 | ULTIMATE MIN | 0.5 | -459.534 | 0 | 0
| 6 | ULTIMATE MIN | 0.5 | -312.3307 | 0 | 0 | 23 | ULTIMATE MIN | 0.75 | -451.2873 | 0 | -7.8751
| 6 | ULTIMATE MIN | 1 | -312.3307 | 0 | 0 | 23 | ULTIMATE MIN | 1 | -443.0406 | 0 | -44.3126
| 7 | ULTIMATE MAX | 0 | 0 | 275.6883 | 96.9686 | 24 | ULTIMATE MAX | 0 | 0 | 174.3968 | 0
| 7 | ULTIMATE MAX | 1 | 0 | 268.9381 | 13.0863 | 24 | ULTIMATE MAX | 1 | 0 | 243.463 | 0
| 7 | ULTIMATE MIN | 0 | -312.3307 | 0 | 0 | 24 | ULTIMATE MIN | 0 | -443.0406 | 0 | -44.3126
| 7 | ULTIMATE MIN | 1 | -312.3307 | 0 | 0 | 24 | ULTIMATE MIN | 1 | -435.279 | 0 | -123.6152
| 8 | ULTIMATE MAX | 0 | 0 | 268.9381 | 13.0863 | 25 | ULTIMATE MAX | 0 | 0 | 243.4625 | 0
| 8 | ULTIMATE MAX | 1 | 0 | 263.7725 | 0 | 25 | ULTIMATE MAX | 1 | 0 | 291.6155 | 0
| 8 | ULTIMATE MIN | 0 | -312.3307 | 0 | 0 | 25 | ULTIMATE MIN | 0 | -435.279 | 0 | -123.6152
| 8 | ULTIMATE MIN | 1 | -312.3307 | 0 | -59.2059 | 25 | ULTIMATE MIN | 1 | -429.6195 | 0 | -217.0651
| 9 | ULTIMATE MAX | 0 | 0 | 421.5818 | 0 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 9 | ULTIMATE MAX | 1 | 0 | 413.782 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 9 | ULTIMATE MIN | 0 | -312.3307 | 0 | -59.2058 | 26 | ULTIMATE MIN | 0 | -291.6153 | -429.6195 | -217.0651
| 9 | ULTIMATE MIN | 1 | -312.3307 | 0 | -217.5067 | 26 | ULTIMATE MIN | 1 | -291.6153 | -361.04 | -111.7945
| 10 | ULTIMATE MAX | 0 | 0 | 413.782 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 10 | ULTIMATE MAX | 1 | 0 | 409.666 | 0 | 27 | ULTIMATE MAX | 0.5 | 0 | 0 | 48.1218
| 10 | ULTIMATE MIN | 0 | -312.3307 | 0 | -217.5067 | 27 | ULTIMATE MAX | 1 | 0 | 0 | 115.2477
| 10 | ULTIMATE MIN | 1 | -312.3307 | 0 | -299.8515 | 27 | ULTIMATE MIN | 0 | -291.615 | -361.04 | -111.7945
| 11 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 27 | ULTIMATE MIN | 0.5 | -291.615 | -282.4853 | -16.943
| 11 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 27 | ULTIMATE MIN | 1 | -291.615 | -203.9306 | 0
| 11 | ULTIMATE MIN | 0 | -312.3295 | -409.6036 | -299.8482 | 28 | ULTIMATE MAX | 0 | 0 | 0 | 115.2477
| 11 | ULTIMATE MIN | 1 | -312.3295 | -413.7196 | -217.5158 | 28 | ULTIMATE MAX | 0.5 | 0 | 0 | 167.2654
| 12 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 43.1397 | 172.0941
| 12 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 0 | -291.6146 | -203.9336 | 0
| 12 | ULTIMATE MIN | 0 | -312.3295 | -413.7196 | -217.5158 | 28 | ULTIMATE MIN | 0.5 | -291.6146 | -95.4533 | 0
| 12 | ULTIMATE MIN | 1 | -312.3295 | -421.5195 | -59.2386 | 28 | ULTIMATE MIN | 1 | -291.6146 | 0 | 0
| 13 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 29 | ULTIMATE MAX | 0 | 0 | 43.1397 | 172.0941
| 13 | ULTIMATE MAX | 1 | 0 | 0 | 13.0386 | 29 | ULTIMATE MAX | 0.5 | 0 | 151.62 | 129.7338
| 13 | ULTIMATE MIN | 0 | -312.3295 | -263.7129 | -59.2386 | 29 | ULTIMATE MAX | 1 | 0 | 260.1003 | 46.952
| 13 | ULTIMATE MIN | 1 | -312.3295 | -268.8785 | 0 | 29 | ULTIMATE MIN | 0 | -291.6143 | 0 | 0
| 14 | ULTIMATE MAX | 0 | 0 | 0 | 13.0386 | 29 | ULTIMATE MIN | 0.5 | -291.6143 | 0 | 0
| 14 | ULTIMATE MAX | 1 | 0 | 0 | 96.9014 | 29 | ULTIMATE MIN | 1 | -291.6143 | 0 | 0
| 14 | ULTIMATE MIN | 0 | -312.3295 | -268.8785 | 0 | 30 | ULTIMATE MAX | 0 | 0 | 260.1003 | 46.952
| 14 | ULTIMATE MIN | 1 | -312.3295 | -275.6287 | 0 | 30 | ULTIMATE MAX | 0.5 | 0 | 338.655 | 0
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 96.9014 | 30 | ULTIMATE MAX | 1 | 0 | 417.2097 | 0
| 15 | ULTIMATE MAX | 0.5 | 0 | 0 | 132.1524 | 30 | ULTIMATE MIN | 0 | -291.6142 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 169.1342 | 30 | ULTIMATE MIN | 0.5 | -291.6142 | 0 | -54.1193
| 15 | ULTIMATE MIN | 0 | -312.3295 | -118.5712 | 0 | 30 | ULTIMATE MIN | 1 | -291.6142 | 0 | -173.168
| 15 | ULTIMATE MIN | 0.5 | -312.3295 | -124.5394 | 0 | 31 | ULTIMATE MAX | 0 | 0 | 417.2097 | 0
| 15 | ULTIMATE MIN | 1 | -312.3295 | -130.5076 | 0 | 31 | ULTIMATE MAX | 1 | 0 | 467.0857 | 0
| 16 | ULTIMATE MAX | 0 | 0 | 56.3237 | 169.1342 | 31 | ULTIMATE MIN | 0 | -291.6142 | 0 | -173.168
| 16 | ULTIMATE MAX | 0.5 | 0 | 50.3658 | 162.4261 | 31 | ULTIMATE MIN | 1 | -291.6142 | 0 | -261.5975
| 16 | ULTIMATE MAX | 1 | 0 | 45.2065 | 157.4428 | 32 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 16 | ULTIMATE MIN | 0 | -312.3295 | 0 | 0 | 32 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 16 | ULTIMATE MIN | 0.5 | -312.3295 | 0 | 0 | 32 | ULTIMATE MIN | 0 | -291.6132 | -467.0859 | -261.5964
| 16 | ULTIMATE MIN | 1 | -312.3295 | 0 | 0 | 32 | ULTIMATE MIN | 1 | -291.6132 | -417.2099 | -173.1668
| 17 | ULTIMATE MAX | 0 | 0 | 201.3888 | 157.4428 | 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 17 | ULTIMATE MAX | 1 | 0 | 196.1821 | 114.8205 | 33 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 17 | ULTIMATE MIN | 0 | -312.3295 | 0 | 0 | 33 | ULTIMATE MAX | 1 | 0 | 0 | 46.9533
| 17 | ULTIMATE MIN | 1 | -312.3295 | 0 | 0 | 33 | ULTIMATE MIN | 0 | -291.6132 | -417.2099 | -173.1668
| 18 | ULTIMATE MAX | 0 | 0 | 196.1821 | 114.8205 | 33 | ULTIMATE MIN | 0.5 | -291.6132 | -338.6552 | -54.118
| 18 | ULTIMATE MAX | 1 | 0 | 189.473 | 61.8424 | 33 | ULTIMATE MIN | 1 | -291.6132 | -260.1005 | 0
| FRAME | LOAD | DIST | P | V2 | M3
| 34 | ULTIMATE MAX | 0 | 0 | 0 | 46.9533
| 34 | ULTIMATE MAX | 0.5 | 0 | 0 | 129.7352
| 34 | ULTIMATE MAX | 1 | 0 | 0 | 172.0956
| 34 | ULTIMATE MIN | 0 | -291.6133 | -260.1005 | 0
| 34 | ULTIMATE MIN | 0.5 | -291.6133 | -151.6202 | 0
| 34 | ULTIMATE MIN | 1 | -291.6133 | -43.1399 | 0
| 35 | ULTIMATE MAX | 0 | 0 | 0 | 172.0956
| 35 | ULTIMATE MAX | 0.5 | 0 | 95.4527 | 167.2669
| 35 | ULTIMATE MAX | 1 | 0 | 203.933 | 115.2494
| 35 | ULTIMATE MIN | 0 | -291.6135 | -43.1399 | 0
| 35 | ULTIMATE MIN | 0.5 | -291.6135 | 0 | 0
| 35 | ULTIMATE MIN | 1 | -291.6135 | 0 | 0
| 36 | ULTIMATE MAX | 0 | 0 | 203.9304 | 115.2494
| 36 | ULTIMATE MAX | 0.5 | 0 | 282.4851 | 48.1235
| 36 | ULTIMATE MAX | 1 | 0 | 361.0398 | 0
| 36 | ULTIMATE MIN | 0 | -291.6138 | 0 | 0
| 36 | ULTIMATE MIN | 0.5 | -291.6138 | 0 | -16.9408
| 36 | ULTIMATE MIN | 1 | -291.6138 | 0 | -111.7921
| 37 | ULTIMATE MAX | 0 | 0 | 361.0398 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 429.6193 | 0
| 37 | ULTIMATE MIN | 0 | -291.6141 | 0 | -111.7921
| 37 | ULTIMATE MIN | 1 | -291.6141 | 0 | -217.0624
| 38 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 38 | ULTIMATE MIN | 0 | -429.6193 | -291.6142 | -217.0624
| 38 | ULTIMATE MIN | 1 | -435.2788 | -243.4612 | -123.613
| 39 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 39 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 39 | ULTIMATE MIN | 0 | -435.2788 | -243.4617 | -123.613
| 39 | ULTIMATE MIN | 1 | -443.0404 | -174.3955 | -44.3117
| 40 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 0.25 | 0 | 0 | 50.4269
| 40 | ULTIMATE MAX | 0.5 | 0 | 0 | 79.4568
| 40 | ULTIMATE MAX | 0.75 | 0 | 69.8228 | 66.0801
| 40 | ULTIMATE MAX | 1 | 0 | 158.9035 | 8.2803
| 40 | ULTIMATE MIN | 0 | -443.0404 | -174.3989 | -44.3117
| 40 | ULTIMATE MIN | 0.25 | -451.2871 | -97.1788 | -7.8748
| 40 | ULTIMATE MIN | 0.5 | -459.5338 | -16.0052 | 0
| 40 | ULTIMATE MIN | 0.75 | -467.7805 | 0 | 0
| 40 | ULTIMATE MIN | 1 | -476.0272 | 0 | -23.768
| 41 | ULTIMATE MAX | 0 | 0 | 158.9035 | 8.2803
| 41 | ULTIMATE MAX | 1 | 0 | 246.3557 | 0
| 41 | ULTIMATE MIN | 0 | -476.0272 | 0 | -23.768
| 41 | ULTIMATE MIN | 1 | -483.7888 | 0 | -94.7993
| 42 | ULTIMATE MAX | 0 | 0 | 246.3557 | 0
| 42 | ULTIMATE MAX | 1 | 0 | 312.3307 | 0
| 42 | ULTIMATE MIN | 0 | -483.7888 | 0 | -94.7993
| 42 | ULTIMATE MIN | 1 | -489.4483 | 0 | -192.5151
| 43 | ULTIMATE MAX | 0 | 0 | 0.001208 | 0.001123
| 43 | ULTIMATE MAX | 0.25 | 0 | 0.001208 | 5e-06
| 43 | ULTIMATE MAX | 0.5 | 0 | 0.001208 | 0
| 43 | ULTIMATE MAX | 0.75 | 0 | 0.001208 | 0
| 43 | ULTIMATE MAX | 1 | 0 | 0.001208 | 0
| 43 | ULTIMATE MIN | 0 | -934.1716 | 0 | 0
| 43 | ULTIMATE MIN | 0.25 | -945.0496 | 0 | -0.000181
| 43 | ULTIMATE MIN | 0.5 | -955.9276 | 0 | -0.001112
| 43 | ULTIMATE MIN | 0.75 | -966.8056 | 0 | -0.00223
| 43 | ULTIMATE MIN | 1 | -977.6836 | 0 | -0.003347
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 19 | SERVICE MAX | 1 | 0 | 215.6957 | 0
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 19 | SERVICE MIN | 0 | -195.2246 | 0 | 0
| 1 | SERVICE MIN | 0 | -195.2254 | -210.9662 | -120.0882 | 19 | SERVICE MIN | 1 | -195.2246 | 0 | -63.081
| 1 | SERVICE MIN | 1 | -195.2254 | -215.6824 | -63.0863 | 20 | SERVICE MAX | 0 | 0 | 215.6957 | 0
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 20 | SERVICE MAX | 1 | 0 | 210.9795 | 0
| 2 | SERVICE MAX | 1 | 0 | 0 | 41.5787 | 20 | SERVICE MIN | 0 | -195.2246 | 0 | -63.081
| 2 | SERVICE MIN | 0 | -195.2254 | -215.6824 | -63.0863 | 20 | SERVICE MIN | 1 | -195.2246 | 0 | -120.0863
| 2 | SERVICE MIN | 1 | -195.2254 | -228.192 | 0 | 21 | SERVICE MAX | 0 | 0 | 0 | 0
| 3 | SERVICE MAX | 0 | 0 | 0 | 41.5787 | 21 | SERVICE MAX | 1 | 0 | 0 | 0
| 3 | SERVICE MAX | 1 | 0 | 0 | 73.8891 | 21 | SERVICE MIN | 0 | -325.3017 | -195.2246 | -120.0863
| 3 | SERVICE MIN | 0 | -195.2254 | -111.3531 | 0 | 21 | SERVICE MIN | 1 | -320.5855 | -153.9902 | -59.2254
| 3 | SERVICE MIN | 1 | -195.2254 | -124.768 | 0 | 22 | SERVICE MAX | 0 | 0 | 0 | 0
| 4 | SERVICE MAX | 0 | 0 | 0 | 73.8891 | 22 | SERVICE MAX | 1 | 0 | 0 | 2.7774
| 4 | SERVICE MAX | 1 | 0 | 0 | 101.9784 | 22 | SERVICE MIN | 0 | -320.5855 | -153.9902 | -59.2254
| 4 | SERVICE MIN | 0 | -195.2254 | -124.768 | 0 | 22 | SERVICE MIN | 1 | -314.1175 | -99.3326 | -15.121
| 4 | SERVICE MIN | 1 | -195.2254 | -135.1789 | 0 | 23 | SERVICE MAX | 0 | 0 | 0 | 2.7774
| 5 | SERVICE MAX | 0 | 0 | 0.13647 | 101.9784 | 23 | SERVICE MAX | 0.25 | 0 | 0 | 39.1324
| 5 | SERVICE MAX | 0.5 | 0 | 0 | 103.6707 | 23 | SERVICE MAX | 0.5 | 0 | 10.1745 | 47.723
| 5 | SERVICE MAX | 1 | 0 | 0 | 108.8238 | 23 | SERVICE MAX | 0.75 | 0 | 60.908 | 29.8094
| 5 | SERVICE MIN | 0 | -195.2254 | -19.5021 | 0 | 23 | SERVICE MAX | 1 | 0 | 109.1706 | 0
| 5 | SERVICE MIN | 0.5 | -195.2254 | -31.4356 | 0 | 23 | SERVICE MIN | 0 | -314.1175 | -99.3326 | -15.121
| 5 | SERVICE MIN | 1 | -195.2254 | -43.3691 | 0 | 23 | SERVICE MIN | 0.25 | -307.2452 | -43.6572 | 0
| 6 | SERVICE MAX | 0 | 0 | 92.518 | 108.8238 | 23 | SERVICE MIN | 0.5 | -300.373 | 0 | 0
| 6 | SERVICE MAX | 0.5 | 0 | 80.6051 | 83.7642 | 23 | SERVICE MIN | 0.75 | -293.5007 | 0 | -6.1125
| 6 | SERVICE MAX | 1 | 0 | 68.6921 | 62.1535 | 23 | SERVICE MIN | 1 | -286.6285 | 0 | -29.1937
| 6 | SERVICE MIN | 0 | -195.2254 | 0 | 0 | 24 | SERVICE MAX | 0 | 0 | 109.1683 | 0
| 6 | SERVICE MIN | 0.5 | -195.2254 | 0 | 0 | 24 | SERVICE MAX | 1 | 0 | 152.3347 | 0
| 6 | SERVICE MIN | 1 | -195.2254 | 0 | 0 | 24 | SERVICE MIN | 0 | -286.6285 | 0 | -29.1937
| 7 | SERVICE MAX | 0 | 0 | 185.2076 | 62.1535 | 24 | SERVICE MIN | 1 | -280.1605 | 0 | -79.048
| 7 | SERVICE MAX | 1 | 0 | 171.7104 | 7.4452 | 25 | SERVICE MAX | 0 | 0 | 152.3344 | 0
| 7 | SERVICE MIN | 0 | -195.2254 | 0 | 0 | 25 | SERVICE MAX | 1 | 0 | 182.43 | 0
| 7 | SERVICE MIN | 1 | -195.2254 | 0 | 0 | 25 | SERVICE MIN | 0 | -280.1605 | 0 | -79.048
| 8 | SERVICE MAX | 0 | 0 | 171.7104 | 7.4452 | 25 | SERVICE MIN | 1 | -275.4442 | 0 | -137.6657
| 8 | SERVICE MAX | 1 | 0 | 161.3817 | 0 | 26 | SERVICE MAX | 0 | 0 | 0 | 0
| 8 | SERVICE MIN | 0 | -195.2254 | 0 | 0 | 26 | SERVICE MAX | 1 | 0 | 0 | 0
| 8 | SERVICE MIN | 1 | -195.2254 | 0 | -38.1847 | 26 | SERVICE MIN | 0 | -182.4299 | -275.4442 | -137.6657
| 9 | SERVICE MAX | 0 | 0 | 278.3805 | 0 | 26 | SERVICE MIN | 1 | -182.4299 | -231.403 | -68.4095
| 9 | SERVICE MAX | 1 | 0 | 262.7846 | 0 | 27 | SERVICE MAX | 0 | 0 | 0 | 0
| 9 | SERVICE MIN | 0 | -195.2254 | 0 | -38.1847 | 27 | SERVICE MAX | 0.5 | 0 | 0 | 31.4204
| 9 | SERVICE MIN | 1 | -195.2254 | 0 | -140.7349 | 27 | SERVICE MAX | 1 | 0 | 0 | 74.5481
| 10 | SERVICE MAX | 0 | 0 | 262.7846 | 0 | 27 | SERVICE MIN | 0 | -182.4297 | -231.403 | -68.4095
| 10 | SERVICE MAX | 1 | 0 | 259.3546 | 0 | 27 | SERVICE MIN | 0.5 | -182.4297 | -180.9557 | -6.888
| 10 | SERVICE MIN | 0 | -195.2254 | 0 | -140.7349 | 27 | SERVICE MIN | 1 | -182.4297 | -130.5085 | 0
| 10 | SERVICE MIN | 1 | -195.2254 | 0 | -192.9488 | 28 | SERVICE MAX | 0 | 0 | 0 | 74.5481
| 11 | SERVICE MAX | 0 | 0 | 0 | 0 | 28 | SERVICE MAX | 0.5 | 0 | 0 | 107.981
| 11 | SERVICE MAX | 1 | 0 | 0 | 0 | 28 | SERVICE MAX | 1 | 0 | 27.6406 | 111.1095
| 11 | SERVICE MIN | 0 | -195.2246 | -259.3083 | -192.9463 | 28 | SERVICE MIN | 0 | -182.4295 | -130.5108 | 0
| 11 | SERVICE MIN | 1 | -195.2246 | -262.7383 | -140.7417 | 28 | SERVICE MIN | 0.5 | -182.4295 | -60.8456 | 0
| 12 | SERVICE MAX | 0 | 0 | 0 | 0 | 28 | SERVICE MIN | 1 | -182.4295 | 0 | 0
| 12 | SERVICE MAX | 1 | 0 | 0 | 0 | 29 | SERVICE MAX | 0 | 0 | 27.6406 | 111.1095
| 12 | SERVICE MIN | 0 | -195.2246 | -262.7383 | -140.7417 | 29 | SERVICE MAX | 0.5 | 0 | 97.3059 | 83.9337
| 12 | SERVICE MIN | 1 | -195.2246 | -278.3342 | -38.209 | 29 | SERVICE MAX | 1 | 0 | 166.9711 | 30.6837
| 13 | SERVICE MAX | 0 | 0 | 0 | 0 | 29 | SERVICE MIN | 0 | -182.4293 | 0 | 0
| 13 | SERVICE MAX | 1 | 0 | 0 | 7.4114 | 29 | SERVICE MIN | 0.5 | -182.4293 | 0 | 0
| 13 | SERVICE MIN | 0 | -195.2246 | -161.3375 | -38.209 | 29 | SERVICE MIN | 1 | -182.4293 | 0 | 0
| 13 | SERVICE MIN | 1 | -195.2246 | -171.6661 | 0 | 30 | SERVICE MAX | 0 | 0 | 166.9711 | 30.6837
| 14 | SERVICE MAX | 0 | 0 | 0 | 7.4114 | 30 | SERVICE MAX | 0.5 | 0 | 217.4184 | 0
| 14 | SERVICE MAX | 1 | 0 | 0 | 62.1035 | 30 | SERVICE MAX | 1 | 0 | 267.8656 | 0
| 14 | SERVICE MIN | 0 | -195.2246 | -171.6661 | 0 | 30 | SERVICE MIN | 0 | -182.4292 | 0 | 0
| 14 | SERVICE MIN | 1 | -195.2246 | -185.1633 | 0 | 30 | SERVICE MIN | 0.5 | -182.4292 | 0 | -34.0879
| 15 | SERVICE MAX | 0 | 0 | 0 | 62.1035 | 30 | SERVICE MIN | 1 | -182.4292 | 0 | -110.5202
| 15 | SERVICE MAX | 0.5 | 0 | 0 | 83.743 | 31 | SERVICE MAX | 0 | 0 | 267.8656 | 0
| 15 | SERVICE MAX | 1 | 0 | 0 | 108.8432 | 31 | SERVICE MAX | 1 | 0 | 299.8956 | 0
| 15 | SERVICE MIN | 0 | -195.2246 | -68.6521 | 0 | 31 | SERVICE MIN | 0 | -182.4292 | 0 | -110.5202
| 15 | SERVICE MIN | 0.5 | -195.2246 | -80.5856 | 0 | 31 | SERVICE MIN | 1 | -182.4292 | 0 | -167.2963
| 15 | SERVICE MIN | 1 | -195.2246 | -92.5191 | 0 | 32 | SERVICE MAX | 0 | 0 | 0 | 0
| 16 | SERVICE MAX | 0 | 0 | 43.3598 | 108.8432 | 32 | SERVICE MAX | 1 | 0 | 0 | 0
| 16 | SERVICE MAX | 0.5 | 0 | 31.4469 | 103.6983 | 32 | SERVICE MIN | 0 | -182.4284 | -299.8958 | -167.2954
| 16 | SERVICE MAX | 1 | 0 | 19.534 | 102.0022 | 32 | SERVICE MIN | 1 | -182.4284 | -267.8658 | -110.5193
| 16 | SERVICE MIN | 0 | -195.2246 | 0 | 0 | 33 | SERVICE MAX | 0 | 0 | 0 | 0
| 16 | SERVICE MIN | 0.5 | -195.2246 | 0 | 0 | 33 | SERVICE MAX | 0.5 | 0 | 0 | 0
| 16 | SERVICE MIN | 1 | -195.2246 | -0.10324 | 0 | 33 | SERVICE MAX | 1 | 0 | 0 | 30.6847
| 17 | SERVICE MAX | 0 | 0 | 135.2034 | 102.0022 | 33 | SERVICE MIN | 0 | -182.4284 | -267.8658 | -110.5193
| 17 | SERVICE MAX | 1 | 0 | 124.7925 | 73.9067 | 33 | SERVICE MIN | 0.5 | -182.4284 | -217.4185 | -34.087
| 17 | SERVICE MIN | 0 | -195.2246 | 0 | 0 | 33 | SERVICE MIN | 1 | -182.4284 | -166.9713 | 0
| 17 | SERVICE MIN | 1 | -195.2246 | 0 | 0 | 34 | SERVICE MAX | 0 | 0 | 0 | 30.6847
| 18 | SERVICE MAX | 0 | 0 | 124.7925 | 73.9067 | 34 | SERVICE MAX | 0.5 | 0 | 0 | 83.9347
| 18 | SERVICE MAX | 1 | 0 | 111.3776 | 41.5883 | 34 | SERVICE MAX | 1 | 0 | 0 | 111.1106
| 18 | SERVICE MIN | 0 | -195.2246 | 0 | 0 | 34 | SERVICE MIN | 0 | -182.4284 | -166.9713 | 0
| 18 | SERVICE MIN | 1 | -195.2246 | 0 | 0 | 34 | SERVICE MIN | 0.5 | -182.4284 | -97.306 | 0
| 19 | SERVICE MAX | 0 | 0 | 228.2053 | 41.5883 | 34 | SERVICE MIN | 1 | -182.4284 | -27.6408 | 0
| FRAME | LOAD | DIST | P | V2 | M3
| 35 | SERVICE MAX | 0 | 0 | 0 | 111.1106
| 35 | SERVICE MAX | 0.5 | 0 | 60.8452 | 107.9822
| 35 | SERVICE MAX | 1 | 0 | 130.5105 | 74.5493
| 35 | SERVICE MIN | 0 | -182.4285 | -27.6408 | 0
| 35 | SERVICE MIN | 0.5 | -182.4285 | 0 | 0
| 35 | SERVICE MIN | 1 | -182.4285 | 0 | 0
| 36 | SERVICE MAX | 0 | 0 | 130.5083 | 74.5493
| 36 | SERVICE MAX | 0.5 | 0 | 180.9556 | 31.4216
| 36 | SERVICE MAX | 1 | 0 | 231.4028 | 0
| 36 | SERVICE MIN | 0 | -182.4287 | 0 | 0
| 36 | SERVICE MIN | 0.5 | -182.4287 | 0 | -6.8864
| 36 | SERVICE MIN | 1 | -182.4287 | 0 | -68.4077
| 37 | SERVICE MAX | 0 | 0 | 231.4028 | 0
| 37 | SERVICE MAX | 1 | 0 | 275.4441 | 0
| 37 | SERVICE MIN | 0 | -182.4289 | 0 | -68.4077
| 37 | SERVICE MIN | 1 | -182.4289 | 0 | -137.6638
| 38 | SERVICE MAX | 0 | 0 | 0 | 0
| 38 | SERVICE MAX | 1 | 0 | 0 | 0
| 38 | SERVICE MIN | 0 | -275.4441 | -182.429 | -137.6638
| 38 | SERVICE MIN | 1 | -280.1603 | -152.3334 | -79.0464
| 39 | SERVICE MAX | 0 | 0 | 0 | 0
| 39 | SERVICE MAX | 1 | 0 | 0 | 0
| 39 | SERVICE MIN | 0 | -280.1603 | -152.3337 | -79.0464
| 39 | SERVICE MIN | 1 | -286.6283 | -109.1673 | -29.1931
| 40 | SERVICE MAX | 0 | 0 | 0 | 0
| 40 | SERVICE MAX | 0.25 | 0 | 0 | 29.8098
| 40 | SERVICE MAX | 0.5 | 0 | 0 | 47.7228
| 40 | SERVICE MAX | 0.75 | 0 | 43.658 | 39.1316
| 40 | SERVICE MAX | 1 | 0 | 99.3334 | 2.7761
| 40 | SERVICE MIN | 0 | -286.6283 | -109.1694 | -29.1931
| 40 | SERVICE MIN | 0.25 | -293.5006 | -60.9068 | -6.1123
| 40 | SERVICE MIN | 0.5 | -300.3728 | -10.1733 | 0
| 40 | SERVICE MIN | 0.75 | -307.2451 | 0 | 0
| 40 | SERVICE MIN | 1 | -314.1173 | 0 | -15.1222
| 41 | SERVICE MAX | 0 | 0 | 99.3334 | 2.7761
| 41 | SERVICE MAX | 1 | 0 | 153.991 | 0
| 41 | SERVICE MIN | 0 | -314.1173 | 0 | -15.1222
| 41 | SERVICE MIN | 1 | -320.5853 | 0 | -59.227
| 42 | SERVICE MAX | 0 | 0 | 153.991 | 0
| 42 | SERVICE MAX | 1 | 0 | 195.2254 | 0
| 42 | SERVICE MIN | 0 | -320.5853 | 0 | -59.227
| 42 | SERVICE MIN | 1 | -325.3016 | 0 | -120.0882
| 43 | SERVICE MAX | 0 | 0 | 0.000896 | 0.000833
| 43 | SERVICE MAX | 0.25 | 0 | 0.000896 | 4e-06
| 43 | SERVICE MAX | 0.5 | 0 | 0.000896 | 0
| 43 | SERVICE MAX | 0.75 | 0 | 0.000896 | 0
| 43 | SERVICE MAX | 1 | 0 | 0.000896 | 0
| 43 | SERVICE MIN | 0 | -599.7914 | 0 | 0
| 43 | SERVICE MIN | 0.25 | -608.8564 | 0 | -0.000111
| 43 | SERVICE MIN | 0.5 | -617.9214 | 0 | -0.000825
| 43 | SERVICE MIN | 0.75 | -626.9864 | 0 | -0.001654
| 43 | SERVICE MIN | 1 | -636.0514 | 0 | -0.002483

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 35.7831 | 0 | 83.9599 | 18 | ULTIMATE MIN | 0 | 0 | -14.5795 | 0
| 1 | ULTIMATE MAX | 1 | 35.2188 | 0 | 94.41 | 18 | ULTIMATE MIN | 1 | 0 | -20.1704 | 0
| 1 | ULTIMATE MIN | 0 | 0 | -58.3897 | 0 | 19 | ULTIMATE MAX | 0 | 34.595 | 68.3322 | 107.4825
| 1 | ULTIMATE MIN | 1 | 0 | -63.1059 | 0 | 19 | ULTIMATE MAX | 1 | 35.2188 | 63.1186 | 94.4171
| 2 | ULTIMATE MAX | 0 | 35.2188 | 0 | 94.41 | 19 | ULTIMATE MIN | 0 | 0 | 0 | 0
| 2 | ULTIMATE MAX | 1 | 34.595 | 0 | 107.4714 | 19 | ULTIMATE MIN | 1 | 0 | 0 | 0
| 2 | ULTIMATE MIN | 0 | 0 | -63.1059 | 0 | 20 | ULTIMATE MAX | 0 | 35.2188 | 63.1186 | 94.4171
| 2 | ULTIMATE MIN | 1 | 0 | -68.3195 | 0 | 20 | ULTIMATE MAX | 1 | 35.7831 | 58.4024 | 83.9634
| 3 | ULTIMATE MAX | 0 | 32.3125 | 20.1856 | 107.4714 | 20 | ULTIMATE MIN | 0 | 0 | 0 | 0
| 3 | ULTIMATE MAX | 1 | 31.6435 | 14.5947 | 101.8022 | 20 | ULTIMATE MIN | 1 | 0 | 0 | 0
| 3 | ULTIMATE MIN | 0 | 0 | -4.7488 | 0 | 21 | ULTIMATE MAX | 0 | 0 | 48.8885 | 83.9634
| 3 | ULTIMATE MIN | 1 | 0 | -10.3397 | 0 | 21 | ULTIMATE MAX | 1 | 0 | 47.6187 | 67.0367
| 4 | ULTIMATE MAX | 0 | 31.6435 | 14.5947 | 101.8022 | 21 | ULTIMATE MIN | 0 | -152.1472 | 0 | 0
| 4 | ULTIMATE MAX | 1 | 31.1244 | 10.2558 | 98.6586 | 21 | ULTIMATE MIN | 1 | -146.1359 | 0 | 0
| 4 | ULTIMATE MIN | 0 | 0 | -10.3379 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 47.6187 | 67.0367
| 4 | ULTIMATE MIN | 1 | 0 | -14.6769 | 0 | 22 | ULTIMATE MAX | 1 | 0 | 46.4672 | 58.6109
| 5 | ULTIMATE MAX | 0 | 28.8478 | 76.8527 | 98.6586 | 22 | ULTIMATE MIN | 0 | -146.1359 | 0 | 0
| 5 | ULTIMATE MAX | 0.5 | 28.2527 | 71.8792 | 77.0925 | 22 | ULTIMATE MIN | 1 | -143.0616 | 0 | 0
| 5 | ULTIMATE MAX | 1 | 27.6577 | 66.9057 | 56.9687 | 23 | ULTIMATE MAX | 0 | 0 | 57.0849 | 58.6109
| 5 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 54.4036 | 41.8088
| 5 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 23 | ULTIMATE MIN | 0 | -171.4474 | 0 | 0
| 5 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 23 | ULTIMATE MIN | 1 | -166.2777 | 0 | 0
| 6 | ULTIMATE MAX | 0 | 25.3864 | 135.1687 | 56.9687 | 24 | ULTIMATE MAX | 0 | 0 | 54.4036 | 41.8088
| 6 | ULTIMATE MAX | 0.5 | 24.7923 | 130.2038 | 18.556 | 24 | ULTIMATE MAX | 1 | 0 | 51.7769 | 29.7476
| 6 | ULTIMATE MAX | 1 | 24.1983 | 125.2389 | 0 | 24 | ULTIMATE MIN | 0 | -166.2777 | 0 | 0
| 6 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 24 | ULTIMATE MIN | 1 | -162.379 | 0 | 0
| 6 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 25 | ULTIMATE MAX | 0 | 0 | 64.7383 | 29.7476
| 6 | ULTIMATE MIN | 1 | 0 | 0 | -26.569 | 25 | ULTIMATE MAX | 0.5 | 0 | 61.0385 | 13.0986
| 7 | ULTIMATE MAX | 0 | 24.9671 | 195.6602 | 0 | 25 | ULTIMATE MAX | 1 | 0 | 56.659 | 0
| 7 | ULTIMATE MAX | 1 | 25.6402 | 190.035 | 0 | 25 | ULTIMATE MIN | 0 | -190.814 | 0 | 0
| 7 | ULTIMATE MIN | 0 | 0 | 0 | -26.569 | 25 | ULTIMATE MIN | 0.5 | -186.2712 | 0 | -0.33786
| 7 | ULTIMATE MIN | 1 | 0 | 0 | -81.6733 | 25 | ULTIMATE MIN | 1 | -181.7284 | 0 | -6.3205
| 8 | ULTIMATE MAX | 0 | 25.6402 | 190.035 | 0 | 26 | ULTIMATE MAX | 0 | 0 | 72.5204 | 0
| 8 | ULTIMATE MAX | 1 | 26.1552 | 185.7303 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 67.4863 | 0
| 8 | ULTIMATE MIN | 0 | 0 | 0 | -81.6733 | 26 | ULTIMATE MIN | 0 | -210.2184 | 0 | -6.3205
| 8 | ULTIMATE MIN | 1 | 0 | 0 | -128.8319 | 26 | ULTIMATE MIN | 1 | -206.4205 | 0 | -20.977
| 9 | ULTIMATE MAX | 0 | 28.4094 | 258.2088 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 67.4863 | 0
| 9 | ULTIMATE MAX | 1 | 29.1871 | 251.709 | 0 | 27 | ULTIMATE MAX | 1 | 0 | 61.8048 | 0
| 9 | ULTIMATE MIN | 0 | 0 | 0 | -128.8319 | 27 | ULTIMATE MIN | 0 | -206.4205 | 0 | -20.977
| 9 | ULTIMATE MIN | 1 | 0 | 0 | -225.4613 | 27 | ULTIMATE MIN | 1 | -203.8399 | 0 | -38.0576
| 10 | ULTIMATE MAX | 0 | 29.1871 | 251.709 | 0 | 28 | ULTIMATE MAX | 0 | 0 | 80.513 | 0
| 10 | ULTIMATE MAX | 1 | 29.5975 | 248.279 | 0 | 28 | ULTIMATE MAX | 0.5 | 0 | 74.1876 | 0
| 10 | ULTIMATE MIN | 0 | 0 | 0 | -225.4613 | 28 | ULTIMATE MAX | 1 | 0 | 67.2447 | 0
| 10 | ULTIMATE MIN | 1 | 0 | 0 | -275.4601 | 28 | ULTIMATE MIN | 0 | -233.9377 | 0 | -38.0576
| 11 | ULTIMATE MAX | 0 | 29.5982 | 0 | 0 | 28 | ULTIMATE MIN | 0.5 | -231.3522 | 0 | -58.5304
| 11 | ULTIMATE MAX | 1 | 29.1878 | 0 | 0 | 28 | ULTIMATE MIN | 1 | -228.7667 | 0 | -77.2484
| 11 | ULTIMATE MIN | 0 | 0 | -248.2568 | -275.4606 | 29 | ULTIMATE MAX | 0 | 0 | 88.0939 | 0
| 11 | ULTIMATE MIN | 1 | 0 | -251.6868 | -225.4662 | 29 | ULTIMATE MAX | 1 | 0 | 81.6508 | 0
| 12 | ULTIMATE MAX | 0 | 29.1878 | 0 | 0 | 29 | ULTIMATE MIN | 0 | -258.9328 | 0 | -77.2484
| 12 | ULTIMATE MAX | 1 | 28.4101 | 0 | 0 | 29 | ULTIMATE MIN | 1 | -256.7138 | 0 | -96.5228
| 12 | ULTIMATE MIN | 0 | 0 | -251.6868 | -225.4662 | 30 | ULTIMATE MAX | 0 | 0 | 81.6508 | 0
| 12 | ULTIMATE MIN | 1 | 0 | -258.1866 | -128.8452 | 30 | ULTIMATE MAX | 1 | 0 | 72.4399 | 0
| 13 | ULTIMATE MAX | 0 | 26.1561 | 0 | 0 | 30 | ULTIMATE MIN | 0 | -256.7138 | 0 | -96.5228
| 13 | ULTIMATE MAX | 1 | 25.6411 | 0 | 0 | 30 | ULTIMATE MIN | 1 | -253.7716 | 0 | -119.7323
| 13 | ULTIMATE MIN | 0 | 0 | -185.7083 | -128.8452 | 31 | ULTIMATE MAX | 0 | 0 | 93.9886 | 0
| 13 | ULTIMATE MIN | 1 | 0 | -190.013 | -81.6922 | 31 | ULTIMATE MAX | 1 | 0 | 88.1606 | 0
| 14 | ULTIMATE MAX | 0 | 25.6411 | 0 | 0 | 31 | ULTIMATE MIN | 0 | -284.0132 | 0 | -119.7323
| 14 | ULTIMATE MAX | 1 | 24.968 | 0 | 0 | 31 | ULTIMATE MIN | 1 | -282.2635 | 0 | -136.0384
| 14 | ULTIMATE MIN | 0 | 0 | -190.013 | -81.6922 | 32 | ULTIMATE MAX | 0 | 0 | 88.1606 | 0
| 14 | ULTIMATE MIN | 1 | 0 | -195.6382 | -26.5949 | 32 | ULTIMATE MAX | 1 | 0 | 82.4639 | 0
| 15 | ULTIMATE MAX | 0 | 24.1975 | 0 | 0 | 32 | ULTIMATE MIN | 0 | -282.2635 | 0 | -136.0384
| 15 | ULTIMATE MAX | 0.5 | 24.7926 | 0 | 18.5888 | 32 | ULTIMATE MIN | 1 | -278.8422 | 0 | -164.8002
| 15 | ULTIMATE MAX | 1 | 25.3877 | 0 | 57.0653 | 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MIN | 0 | 0 | -125.2174 | -26.5949 | 33 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 15 | ULTIMATE MIN | 0.5 | 0 | -130.1909 | 0 | 33 | ULTIMATE MIN | 0 | -104.0542 | -314.0677 | -164.8002
| 15 | ULTIMATE MIN | 1 | 0 | -135.1644 | 0 | 33 | ULTIMATE MIN | 1 | -100.445 | -270.0265 | -84.4872
| 16 | ULTIMATE MAX | 0 | 27.6593 | 0 | 57.0653 | 34 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 16 | ULTIMATE MAX | 0.5 | 28.2533 | 0 | 77.1532 | 34 | ULTIMATE MAX | 1 | 0 | 0 | 29.9209
| 16 | ULTIMATE MAX | 1 | 28.8473 | 0 | 98.6785 | 34 | ULTIMATE MIN | 0 | -100.445 | -270.0265 | -84.4872
| 16 | ULTIMATE MIN | 0 | 0 | -66.9059 | 0 | 34 | ULTIMATE MIN | 1 | -96.4552 | -221.3409 | -9.7995
| 16 | ULTIMATE MIN | 0.5 | 0 | -71.8708 | 0 | 35 | ULTIMATE MAX | 0 | 0 | 0 | 29.9209
| 16 | ULTIMATE MIN | 1 | 0 | -76.8358 | 0 | 35 | ULTIMATE MAX | 1 | 0 | 0 | 86.7596
| 17 | ULTIMATE MAX | 0 | 31.1242 | 14.6916 | 98.6785 | 35 | ULTIMATE MIN | 0 | -101.3692 | -221.3404 | -9.7995
| 17 | ULTIMATE MAX | 1 | 31.6433 | 10.3527 | 101.8183 | 35 | ULTIMATE MIN | 1 | -97.0907 | -169.1315 | 0
| 17 | ULTIMATE MIN | 0 | 0 | -10.2406 | 0 | 36 | ULTIMATE MAX | 0 | 0 | 0 | 86.7596
| 17 | ULTIMATE MIN | 1 | 0 | -14.5795 | 0 | 36 | ULTIMATE MAX | 1 | 0 | 0 | 119.1407
| 18 | ULTIMATE MAX | 0 | 31.6433 | 10.3544 | 101.8183 | 36 | ULTIMATE MIN | 0 | -97.0907 | -169.1315 | 0
| 18 | ULTIMATE MAX | 1 | 32.3123 | 4.7635 | 107.4825 | 36 | ULTIMATE MIN | 1 | -93.7702 | -128.6135 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 37 | ULTIMATE MAX | 0 | 0 | 0 | 119.1407 | 56 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0.5 | 0 | 0 | 143.6477 | 56 | ULTIMATE MIN | 0 | -256.7099 | -81.6486 | -96.5199
| 37 | ULTIMATE MAX | 1 | 0 | 0 | 154.6861 | 56 | ULTIMATE MIN | 1 | -258.9288 | -88.0917 | -77.246
| 37 | ULTIMATE MIN | 0 | -98.7024 | -128.613 | 0 | 57 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 37 | ULTIMATE MIN | 0.5 | -94.8963 | -82.1695 | 0 | 57 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 37 | ULTIMATE MIN | 1 | -91.0903 | -35.726 | 0 | 57 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 0 | 0 | 0 | 154.6861 | 57 | ULTIMATE MIN | 0 | -228.7616 | -67.2421 | -77.246
| 38 | ULTIMATE MAX | 0.5 | 0 | 31.5221 | 152.2716 | 57 | ULTIMATE MIN | 0.5 | -231.3471 | -74.1851 | -58.5287
| 38 | ULTIMATE MAX | 1 | 0 | 77.8856 | 136.4348 | 57 | ULTIMATE MIN | 1 | -233.9326 | -80.5104 | -38.0566
| 38 | ULTIMATE MIN | 0 | -96.0401 | -35.7256 | 0 | 58 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 38 | ULTIMATE MIN | 0.5 | -92.2406 | 0 | 0 | 58 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 38 | ULTIMATE MIN | 1 | -92.7007 | 0 | 0 | 58 | ULTIMATE MIN | 0 | -203.8337 | -61.8021 | -38.0566
| 39 | ULTIMATE MAX | 0 | 0 | 77.8861 | 136.4348 | 58 | ULTIMATE MIN | 1 | -206.4143 | -67.4837 | -20.9766
| 39 | ULTIMATE MAX | 1 | 0 | 130.4153 | 105.6998 | 59 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 39 | ULTIMATE MIN | 0 | -93.4082 | 0 | 0 | 59 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 39 | ULTIMATE MIN | 1 | -91.9708 | 0 | 0 | 59 | ULTIMATE MIN | 0 | -206.4143 | -67.4837 | -20.9766
| 40 | ULTIMATE MAX | 0 | 0 | 130.4153 | 105.6998 | 59 | ULTIMATE MIN | 1 | -210.2125 | -72.5178 | -6.3207
| 40 | ULTIMATE MAX | 1 | 0 | 170.613 | 73.1626 | 60 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 40 | ULTIMATE MIN | 0 | -91.9708 | 0 | 0 | 60 | ULTIMATE MAX | 0.5 | 0 | 0 | 13.0976
| 40 | ULTIMATE MIN | 1 | -95.265 | 0 | 0 | 60 | ULTIMATE MAX | 1 | 0 | 0 | 29.7459
| 41 | ULTIMATE MAX | 0 | 0 | 170.6135 | 73.1626 | 60 | ULTIMATE MIN | 0 | -181.7214 | -56.6565 | -6.3207
| 41 | ULTIMATE MAX | 1 | 0 | 231.3104 | 4.9133 | 60 | ULTIMATE MIN | 0.5 | -186.2642 | -61.036 | -0.33866
| 41 | ULTIMATE MIN | 0 | -90.7929 | 0 | 0 | 60 | ULTIMATE MIN | 1 | -190.807 | -64.7358 | 0
| 41 | ULTIMATE MIN | 1 | -95.2214 | 0 | -11.6754 | 61 | ULTIMATE MAX | 0 | 0 | 0 | 29.7459
| 42 | ULTIMATE MAX | 0 | 0 | 231.3104 | 4.9133 | 61 | ULTIMATE MAX | 1 | 0 | 0 | 41.8066
| 42 | ULTIMATE MAX | 1 | 0 | 263.3404 | 0 | 61 | ULTIMATE MIN | 0 | -162.3709 | -51.7747 | 0
| 42 | ULTIMATE MIN | 0 | -95.2214 | 0 | -11.6754 | 61 | ULTIMATE MIN | 1 | -166.2697 | -54.4015 | 0
| 42 | ULTIMATE MIN | 1 | -97.8463 | 0 | -61.1364 | 62 | ULTIMATE MAX | 0 | 0 | 0 | 41.8066
| 43 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 62 | ULTIMATE MAX | 1 | 0 | 0 | 58.6082
| 43 | ULTIMATE MAX | 1 | 0 | 0 | 4.9124 | 62 | ULTIMATE MIN | 0 | -166.2697 | -54.4015 | 0
| 43 | ULTIMATE MIN | 0 | -97.8456 | -263.3419 | -61.1374 | 62 | ULTIMATE MIN | 1 | -171.4393 | -57.0828 | 0
| 43 | ULTIMATE MIN | 1 | -95.2208 | -231.3119 | -11.6762 | 63 | ULTIMATE MAX | 0 | 0 | 0 | 58.6082
| 44 | ULTIMATE MAX | 0 | 0 | 0 | 4.9124 | 63 | ULTIMATE MAX | 1 | 0 | 0 | 67.0336
| 44 | ULTIMATE MAX | 1 | 0 | 0 | 73.1624 | 63 | ULTIMATE MIN | 0 | -143.0524 | -46.4657 | 0
| 44 | ULTIMATE MIN | 0 | -95.2208 | -231.3119 | -11.6762 | 63 | ULTIMATE MIN | 1 | -146.1268 | -47.6172 | 0
| 44 | ULTIMATE MIN | 1 | -90.7941 | -170.6151 | 0 | 64 | ULTIMATE MAX | 0 | 0 | 0 | 67.0336
| 45 | ULTIMATE MAX | 0 | 0 | 0 | 73.1624 | 64 | ULTIMATE MAX | 1 | 0 | 0 | 83.9599
| 45 | ULTIMATE MAX | 1 | 0 | 0 | 105.6999 | 64 | ULTIMATE MIN | 0 | -146.1268 | -47.6172 | 0
| 45 | ULTIMATE MIN | 0 | -95.2641 | -170.6145 | 0 | 64 | ULTIMATE MIN | 1 | -152.138 | -48.8871 | 0
| 45 | ULTIMATE MIN | 1 | -91.9699 | -130.4169 | 0 | 65 | ULTIMATE MAX | 0 | 0 | 9.6509 | 20.759
| 46 | ULTIMATE MAX | 0 | 0 | 0 | 105.6999 | 65 | ULTIMATE MAX | 0.25 | 0 | 10.9096 | 11.2482
| 46 | ULTIMATE MAX | 1 | 0 | 0 | 136.4356 | 65 | ULTIMATE MAX | 0.5 | 0 | 12.1482 | 0.58247
| 46 | ULTIMATE MIN | 0 | -91.9699 | -130.4169 | 0 | 65 | ULTIMATE MAX | 0.75 | 0 | 13.3666 | 11.2196
| 46 | ULTIMATE MIN | 1 | -93.4091 | -77.8877 | 0 | 65 | ULTIMATE MAX | 1 | 0 | 14.5649 | 24.1402
| 47 | ULTIMATE MAX | 0 | 0 | 0 | 136.4356 | 65 | ULTIMATE MIN | 0 | -505.7987 | -9.6517 | -20.7613
| 47 | ULTIMATE MAX | 0.5 | 0 | 0 | 152.2885 | 65 | ULTIMATE MIN | 0.25 | -514.8637 | -10.9104 | -11.2497
| 47 | ULTIMATE MAX | 1 | 0 | 35.8842 | 154.6729 | 65 | ULTIMATE MIN | 0.5 | -523.9287 | -12.149 | -0.58321
| 47 | ULTIMATE MIN | 0 | -92.6996 | -77.8871 | 0 | 65 | ULTIMATE MIN | 0.75 | -532.9937 | -13.3674 | -11.2196
| 47 | ULTIMATE MIN | 0.5 | -92.2479 | -31.4436 | 0 | 65 | ULTIMATE MIN | 1 | -542.0587 | -14.5657 | -24.1395
| 47 | ULTIMATE MIN | 1 | -96.0539 | 0 | 0
| 48 | ULTIMATE MAX | 0 | 0 | 35.8846 | 154.6729
| 48 | ULTIMATE MAX | 0.5 | 0 | 82.248 | 143.6191
| 48 | ULTIMATE MAX | 1 | 0 | 128.6114 | 119.1432
| 48 | ULTIMATE MIN | 0 | -91.1038 | 0 | 0
| 48 | ULTIMATE MIN | 0.5 | -94.9033 | 0 | 0
| 48 | ULTIMATE MIN | 1 | -98.7028 | 0 | 0
| 49 | ULTIMATE MAX | 0 | 0 | 128.6119 | 119.1432
| 49 | ULTIMATE MAX | 1 | 0 | 169.1299 | 86.7625
| 49 | ULTIMATE MIN | 0 | -93.7704 | 0 | 0
| 49 | ULTIMATE MIN | 1 | -97.0909 | 0 | 0
| 50 | ULTIMATE MAX | 0 | 0 | 169.1299 | 86.7625
| 50 | ULTIMATE MAX | 1 | 0 | 221.3388 | 29.9244
| 50 | ULTIMATE MIN | 0 | -97.0909 | 0 | 0
| 50 | ULTIMATE MIN | 1 | -101.3694 | 0 | -9.7961
| 51 | ULTIMATE MAX | 0 | 0 | 221.3393 | 29.9244
| 51 | ULTIMATE MAX | 1 | 0 | 270.0249 | 0
| 51 | ULTIMATE MIN | 0 | -96.4551 | 0 | -9.7961
| 51 | ULTIMATE MIN | 1 | -100.4449 | 0 | -84.4833
| 52 | ULTIMATE MAX | 0 | 0 | 270.0249 | 0
| 52 | ULTIMATE MAX | 1 | 0 | 314.0661 | 0
| 52 | ULTIMATE MIN | 0 | -100.4449 | 0 | -84.4833
| 52 | ULTIMATE MIN | 1 | -104.0541 | 0 | -164.7958
| 53 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 53 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 53 | ULTIMATE MIN | 0 | -278.8394 | -82.4617 | -164.7958
| 53 | ULTIMATE MIN | 1 | -282.2606 | -88.159 | -136.0346
| 54 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 54 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 54 | ULTIMATE MIN | 0 | -282.2606 | -88.159 | -136.0346
| 54 | ULTIMATE MIN | 1 | -284.0103 | -93.9871 | -119.7287
| 55 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 55 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 55 | ULTIMATE MIN | 0 | -253.7676 | -72.4377 | -119.7287
| 55 | ULTIMATE MIN | 1 | -256.7099 | -81.6486 | -96.5199
| 56 | ULTIMATE MAX | 0 | 0 | 0 | 0

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 217.062 | 203.933 | 291.614 | 137.664 | 1000 | 816.667
|  | 제 1경간 중앙부 | 172.096 | - | 291.613 | 111.111 | 1000 | 700
|  | 제 1경간 지점부 | 261.597 | 260.101 | 291.614 | 167.296 | 1000 | 816.667
|  | 제 2경간 중앙부 | 172.094 | - | 291.614 | 111.11 | 1000 | 700
|  | 단지점부(우측) | 217.065 | 203.934 | 291.615 | 137.666 | 1000 | 816.667
| 하부슬래브 | 단지점부(좌측) | 192.515 | 196.149 | 312.331 | 120.088 | 1000 | 700
|  | 제 1경간 중앙부 | 169.102 | - | 312.331 | 108.824 | 1000 | 700
|  | 제 1경간 지점부 | 299.852 | 268.938 | 312.331 | 192.949 | 1000 | 700
|  | 제 2경간 중앙부 | 169.134 | - | 312.329 | 108.843 | 1000 | 700
|  | 단지점부(우측) | 192.512 | 196.182 | 312.329 | 120.086 | 1000 | 700
| 좌측벽체 | 상부 | 217.062 | 174.399 | 429.619 | 137.664 | 1000 | 666.667
|  | 중앙부 | 79.457 | - | 459.534 | 47.723 | 1000 | 550
|  | 중앙부(부모멘트) | -44.312 | - | 459.534 | -29.193 | 1000 | 550 | 부모멘트
|  | 하부 | 192.515 | 158.904 | 489.448 | 120.088 | 1000 | 550
| 우측벽체 | 상부 | 217.065 | 174.4 | 429.62 | 137.666 | 1000 | 666.667
|  | 중앙부 | 79.457 | - | 459.534 | 47.723 | 1000 | 550
|  | 중앙부(부모멘트) | -44.313 | - | 459.534 | -29.194 | 1000 | 550 | 부모멘트
|  | 하부 | 192.512 | 158.902 | 489.449 | 120.086 | 1000 | 550

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 164.796 | 169.13 | 104.054 | 1000 | 816.667
|  | 제 1경간 중앙부 | 154.673 | - | 91.104 | 1000 | 700
|  | 제 1경간 지점부 | 61.137 | 130.417 | 97.846 | 1000 | 816.667
|  | 제 2경간 중앙부 | 154.686 | - | 96.04 | 1000 | 700
|  | 단지점부(우측) | 164.8 | 169.131 | 104.054 | 1000 | 816.667
| 하부슬래브 | 단지점부(좌측) | 0 | 14.595 | 35.783 | 1000 | 700
|  | 제 1경간 중앙부 | 101.802 | - | 31.644 | 1000 | 700
|  | 제 1경간 지점부 | 275.461 | 190.035 | 29.598 | 1000 | 700
|  | 제 2경간 중앙부 | 101.818 | - | 31.643 | 1000 | 700
|  | 단지점부(우측) | 0 | 14.58 | 35.783 | 1000 | 700
| 좌측벽체 | 상부 | 164.796 | 81.649 | 278.839 | 1000 | 666.667
|  | 중앙부 | 58.608 | - | 171.439 | 1000 | 550
|  | 중앙부(부모멘트) | -119.729 | - | 171.439 | 1000 | 550 | 부모멘트
|  | 하부 | 0 | 54.401 | 152.138 | 1000 | 550
| 우측벽체 | 상부 | 164.8 | 81.651 | 278.842 | 1000 | 666.667
|  | 중앙부 | 58.611 | - | 171.447 | 1000 | 550
|  | 중앙부(부모멘트) | -119.732 | - | 171.447 | 1000 | 550 | 부모멘트
|  | 하부 | 0 | 54.404 | 152.147 | 1000 | 550

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 746.667 | 217.062 | 394.929 |  | 864.846 | H16 - 8.0EA |  |  | 1588.8 | 1.819
상부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 610 | 172.096 | 321.103 |  | 841.147 | H16 - 8.0EA |  |  | 1588.8 | 1.866
상부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 746.667 | 261.597 | 480.052 |  | 1044.785 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.835
상부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 610 | 172.094 | 321.103 |  | 841.14 | H16 - 8.0EA |  |  | 1588.8 | 1.866
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 746.667 | 217.065 | 394.929 |  | 864.857 | H16 - 8.0EA |  |  | 1588.8 | 1.819
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 630 | 192.515 | 331.907 |  | 911.698 | H16 - 8.0EA |  |  | 1588.8 | 1.724
하부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 610 | 169.102 | 321.103 |  | 826.318 | H16 - 8.0EA |  |  | 1588.8 | 1.899
하부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 630 | 299.852 | 473.436 |  | 1431.768 | H19 - 8.0EA |  |  | 2292 | 1.579
하부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 610 | 169.134 | 321.103 |  | 826.476 | H16 - 8.0EA |  |  | 1588.8 | 1.899
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 630 | 192.512 | 331.907 |  | 911.685 | H16 - 8.0EA |  |  | 1588.8 | 1.724
좌측벽체 : 상부 |  |  |  | 1000 |  | 596.667 | 217.062 | 623.465 |  | - | H16 - 8.0EA |  |  | - | 2.872
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 460 | 79.457 | 684.546 |  | - | H16 - 4.0EA |  |  | - | 8.615
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 480 | 119.729 | 516.177 |  | - | H16 - 4.0EA |  |  | - | 4.311
좌측벽체 : 하부 |  |  |  | 1000 |  | 480 | 192.515 | 499.397 |  | - | H16 - 8.0EA |  |  | - | 2.594
우측벽체 : 상부 |  |  |  | 1000 |  | 596.667 | 217.065 | 623.473 |  | - | H16 - 8.0EA |  |  | - | 2.872
우측벽체 : 중앙부 |  |  |  | 1000 |  | 460 | 79.457 | 684.547 |  | - | H16 - 4.0EA |  |  | - | 8.615
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 480 | 119.732 | 516.077 |  | - | H16 - 4.0EA |  |  | - | 4.31
우측벽체 : 하부 |  |  |  | 1000 |  | 480 | 192.512 | 499.436 |  | - | H16 - 8.0EA |  |  | - | 2.594
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 385.795 |  | 203.933 | 385.795 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 1경간 중앙부 |  |  |  | 373.547 |  | - | 373.547 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 지점부 |  |  |  | 385.795 |  | 260.101 | 385.795 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 중앙부 |  |  |  | 373.547 |  | - | 373.547 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 385.795 |  | 203.934 | 385.795 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 385.795 |  | 196.149 | 385.795 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 1경간 중앙부 |  |  |  | 373.547 |  | - | 373.547 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 지점부 |  |  |  | 385.795 |  | 268.938 | 385.795 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 중앙부 |  |  |  | 373.547 |  | - | 373.547 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 385.795 |  | 196.182 | 385.795 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 310.339 |  | 174.399 | 310.339 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 298.503 |  | - | 298.503 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 312.623 |  | 158.904 | 312.623 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 310.339 |  | 174.4 | 310.339 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 298.503 |  | - | 298.503 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 312.623 |  | 158.902 | 312.623 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 816.667 |  | 746.667 |  | 70 |  | 217.062 |  | 203.933
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (746.67 - 36.651) / 36.651 = 0.0581
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 864.846 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00213
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (746.67 - a/2) = 394.929 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 217.062 kN.m) ∴ O.K [안전률 1.819]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 203.933 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 610 |  | 90 |  | 172.096 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (610.00 - 36.651) / 36.651 = 0.0469
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 841.147 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (610.00 - a/2) = 321.103 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 172.096 kN.m) ∴ O.K [안전률 1.866]
＊ 전단에 대한 검토 (d = 610.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 610.00 = 373.547 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 816.667 |  | 746.667 |  | 70 |  | 261.597 |  | 260.101
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (746.67 - 44.761) / 44.761 = 0.0470
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1044.785 mm²
Use As = 1940.400 mm² (철근도심 : 70.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (746.67 - a/2) = 480.052 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 261.597 kN.m) ∴ O.K [안전률 1.835]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 260.101 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 610 |  | 90 |  | 172.094 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (610.00 - 36.651) / 36.651 = 0.0469
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 841.140 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (610.00 - a/2) = 321.103 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 172.094 kN.m) ∴ O.K [안전률 1.866]
＊ 전단에 대한 검토 (d = 610.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 610.00 = 373.547 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 816.667 |  | 746.667 |  | 70 |  | 217.065 |  | 203.934
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (746.67 - 36.651) / 36.651 = 0.0581
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 864.857 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00213
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (746.67 - a/2) = 394.929 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 217.065 kN.m) ∴ O.K [안전률 1.819]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 203.934 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 630 |  | 70 |  | 192.515 |  | 196.149
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (630.00 - 36.651) / 36.651 = 0.0486
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 911.698 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00252
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (630.00 - a/2) = 331.907 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 192.515 kN.m) ∴ O.K [안전률 1.724]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 196.149 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 610 |  | 90 |  | 169.102 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (610.00 - 36.651) / 36.651 = 0.0469
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 826.318 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (610.00 - a/2) = 321.103 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 169.102 kN.m) ∴ O.K [안전률 1.899]
＊ 전단에 대한 검토 (d = 610.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 610.00 = 373.547 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 630 |  | 70 |  | 299.852 |  | 268.938
＊ 강도감소계수(Φ) 산정
T = As x fy = 2292.000 x 400.00 = 916800.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 44.941 mm, c = 44.941 / β1 = 44.941 / 0.85 = 52.872 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (630.00 - 52.872) / 52.872 = 0.0327
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1431.768 mm²
Use As = 2292.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 8.0 EA (= 2292.000 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00364
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 2292.000 x 400 x (630.00 - a/2) = 473.436 kN.m
; a = As x fy / (0.85 x fck x b) = 44.941 mm
≥ Mu (= 299.852 kN.m) ∴ O.K [안전률 1.579]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 268.938 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 610 |  | 90 |  | 169.134 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (610.00 - 36.651) / 36.651 = 0.0469
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 826.476 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (610.00 - a/2) = 321.103 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 169.134 kN.m) ∴ O.K [안전률 1.899]
＊ 전단에 대한 검토 (d = 610.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 610.00 = 373.547 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 630 |  | 70 |  | 192.512 |  | 196.182
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (630.00 - 36.651) / 36.651 = 0.0486
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 911.685 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00252
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (630.00 - a/2) = 331.907 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 192.512 kN.m) ∴ O.K [안전률 1.724]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 196.182 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 666.667 |  | 596.667 |  | 429.619 |  | 217.062 |  | 174.399 |  | 505.244
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0036) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 666.7 x 1000.0 = 13600000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (13600000.0 x 333.33 + 635520.0 x 70.000 + 317760.0 x 576.667) / 14553280.0
= 327.147 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 358.000 mm, ab = k1 x cb = 304.300 mm
fs' = 600 x (358.000 - 90.000) / 358.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 304.300 x 1000.000 = 6207.720 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 635.520 kN
Pb = 6207.720 + 301.554 - 635.520 = 5873.754 kN
Mb = 6207.720 x (596.667 - 304.300/2) + 301.554 x (596.667 - 90.00)
- 5873.754 x (327.147 - 70.000)
= 1401.804 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 238.656 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 121.334 mm, a = k1 x c = 103.134 mm 를 사용.
fs = 600 x (596.667 - 121.334) / 121.334 (≤fy) = 400.000 MPa
fs' = 600 x (121.334 - 90.000) / 121.334 (≤fy) = 154.949 MPa
Cc = 0.85 x 24.0 x 103.134 x 1000.000 = 2103.940 kN
Cs = As' x (fs' - 0.85 x fck) = 106.886 kN
Ts = As x fs = 635.520 kN
Pn = 2103.940 + 106.886 - 635.520 = 1575.306 kN
Mn' = 2103.940 x (596.667 - 103.134/2) + 106.886 x (596.667 - 90.00)
= 1201.012 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0087 ＜ 0.0100 (e' = e + Xp - dc = 762.391 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 11603.730 kN ≥ Pn = 1575.306 kN
ΦPn = 0.78 x 1575.306 = 1233.990 kN ≥ Pu = 429.619 kN ∴ O.K
ΦMn = ΦPn x 0.505 = 623.465 kN.m ≥ Mu = 217.062 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 310.339 kN
≥ Vu (= 174.399 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 460 |  | 459.534 |  | 79.457 |  | 0 |  | 172.907
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0029) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 317760.0 x 90.000 + 317760.0 x 480.000) / 11855520.0
= 275.536 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 276.000 mm, ab = k1 x cb = 234.600 mm
fs' = 600 x (276.000 - 70.000) / 276.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 234.600 x 1000.000 = 4785.840 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 4785.840 + 301.554 - 317.760 = 4769.634 kN
Mb = 4785.840 x (460.000 - 234.600/2) + 301.554 x (460.000 - 70.00)
- 4769.634 x (275.536 - 90.000)
= 872.774 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 182.986 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 290.167 mm, a = k1 x c = 246.642 mm 를 사용.
fs = 600 x (460.000 - 290.167) / 290.167 (≤fy) = 351.176 MPa
fs' = 600 x (290.167 - 70.000) / 290.167 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 246.642 x 1000.000 = 5031.500 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 278.974 kN
Pn = 5031.500 + 301.554 - 278.974 = 5054.080 kN
Mn' = 5031.500 x (460.000 - 246.642/2) + 301.554 x (460.000 - 70.00)
= 1811.606 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0007 ＜ 0.0100 (e' = e + Xp - dc = 358.444 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 90.00 = 460.000 mm
c = 600.00 / (600.00+400.00) x 460.000 = 276.000 mm, a = k1 x c = 234.600 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (460.00-276.00) / 276.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9458.487 kN ≥ Pn = 5054.080 kN
ΦPn = 0.78 x 5054.080 = 3959.029 kN ≥ Pu = 459.534 kN ∴ O.K
ΦMn = ΦPn x 0.173 = 684.546 kN.m ≥ Mu = 79.457 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 460.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 460.00 = 298.503 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 459.534 |  | 119.729 |  | 0 |  | 260.544
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0029) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 317760.0 x 70.000 + 317760.0 x 460.000) / 11855520.0
= 274.464 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 90.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 4993.920 + 301.554 - 317.760 = 4977.714 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 301.554 x (480.000 - 90.00)
- 4977.714 x (274.464 - 70.000)
= 885.669 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 177.927 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 153.721 mm, a = k1 x c = 130.663 mm 를 사용.
fs = 600 x (480.000 - 153.721) / 153.721 (≤fy) = 400.000 MPa
fs' = 600 x (153.721 - 90.000) / 153.721 (≤fy) = 248.714 MPa
Cc = 0.85 x 24.0 x 130.663 x 1000.000 = 2665.517 kN
Cs = As' x (fs' - 0.85 x fck) = 181.372 kN
Ts = As x fs = 317.760 kN
Pn = 2665.517 + 181.372 - 317.760 = 2529.129 kN
Mn' = 2665.517 x (480.000 - 130.663/2) + 181.372 x (480.000 - 90.00)
= 1176.042 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0092 ＜ 0.0100 (e' = e + Xp - dc = 465.008 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9458.487 kN ≥ Pn = 2529.129 kN
ΦPn = 0.78 x 2529.129 = 1981.151 kN ≥ Pu = 459.534 kN ∴ O.K
ΦMn = ΦPn x 0.261 = 516.177 kN.m ≥ Mu = 119.729 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 311.481 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 489.448 |  | 192.515 |  | 158.904 |  | 393.331
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0043) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 635520.0 x 70.000 + 317760.0 x 460.000) / 12173280.0
= 269.127 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 90.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 635.520 kN
Pb = 4993.920 + 301.554 - 635.520 = 4659.954 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 301.554 x (480.000 - 90.00)
- 4659.954 x (269.127 - 70.000)
= 975.510 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 209.339 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 123.589 mm, a = k1 x c = 105.051 mm 를 사용.
fs = 600 x (480.000 - 123.589) / 123.589 (≤fy) = 400.000 MPa
fs' = 600 x (123.589 - 90.000) / 123.589 (≤fy) = 163.067 MPa
Cc = 0.85 x 24.0 x 105.051 x 1000.000 = 2143.031 kN
Cs = As' x (fs' - 0.85 x fck) = 113.335 kN
Ts = As x fs = 635.520 kN
Pn = 2143.031 + 113.335 - 635.520 = 1620.846 kN
Mn' = 2143.031 x (480.000 - 105.051/2) + 113.335 x (480.000 - 90.00)
= 960.292 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0061 ＜ 0.0100 (e' = e + Xp - dc = 592.458 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9699.730 kN ≥ Pn = 1620.846 kN
ΦPn = 0.78 x 1620.846 = 1269.663 kN ≥ Pu = 489.448 kN ∴ O.K
ΦMn = ΦPn x 0.393 = 499.397 kN.m ≥ Mu = 192.515 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 312.623 kN
≥ Vu (= 158.904 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 666.667 |  | 596.667 |  | 429.62 |  | 217.065 |  | 174.4 |  | 505.25
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0036) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 666.7 x 1000.0 = 13600000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (13600000.0 x 333.33 + 635520.0 x 70.000 + 317760.0 x 576.667) / 14553280.0
= 327.147 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 358.000 mm, ab = k1 x cb = 304.300 mm
fs' = 600 x (358.000 - 90.000) / 358.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 304.300 x 1000.000 = 6207.720 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 635.520 kN
Pb = 6207.720 + 301.554 - 635.520 = 5873.754 kN
Mb = 6207.720 x (596.667 - 304.300/2) + 301.554 x (596.667 - 90.00)
- 5873.754 x (327.147 - 70.000)
= 1401.804 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 238.656 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 121.334 mm, a = k1 x c = 103.134 mm 를 사용.
fs = 600 x (596.667 - 121.334) / 121.334 (≤fy) = 400.000 MPa
fs' = 600 x (121.334 - 90.000) / 121.334 (≤fy) = 154.949 MPa
Cc = 0.85 x 24.0 x 103.134 x 1000.000 = 2103.940 kN
Cs = As' x (fs' - 0.85 x fck) = 106.886 kN
Ts = As x fs = 635.520 kN
Pn = 2103.940 + 106.886 - 635.520 = 1575.306 kN
Mn' = 2103.940 x (596.667 - 103.134/2) + 106.886 x (596.667 - 90.00)
= 1201.012 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0027 ＜ 0.0100 (e' = e + Xp - dc = 762.397 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 11603.730 kN ≥ Pn = 1575.306 kN
ΦPn = 0.78 x 1575.306 = 1233.990 kN ≥ Pu = 429.620 kN ∴ O.K
ΦMn = ΦPn x 0.505 = 623.473 kN.m ≥ Mu = 217.065 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 310.339 kN
≥ Vu (= 174.400 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 460 |  | 459.534 |  | 79.457 |  | 0 |  | 172.908
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0029) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 317760.0 x 90.000 + 317760.0 x 480.000) / 11855520.0
= 275.536 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 276.000 mm, ab = k1 x cb = 234.600 mm
fs' = 600 x (276.000 - 70.000) / 276.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 234.600 x 1000.000 = 4785.840 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 4785.840 + 301.554 - 317.760 = 4769.634 kN
Mb = 4785.840 x (460.000 - 234.600/2) + 301.554 x (460.000 - 70.00)
- 4769.634 x (275.536 - 90.000)
= 872.774 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 182.986 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 290.167 mm, a = k1 x c = 246.642 mm 를 사용.
fs = 600 x (460.000 - 290.167) / 290.167 (≤fy) = 351.176 MPa
fs' = 600 x (290.167 - 70.000) / 290.167 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 246.642 x 1000.000 = 5031.500 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 278.974 kN
Pn = 5031.500 + 301.554 - 278.974 = 5054.080 kN
Mn' = 5031.500 x (460.000 - 246.642/2) + 301.554 x (460.000 - 70.00)
= 1811.606 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0004 ＜ 0.0100 (e' = e + Xp - dc = 358.444 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 90.00 = 460.000 mm
c = 600.00 / (600.00+400.00) x 460.000 = 276.000 mm, a = k1 x c = 234.600 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (460.00-276.00) / 276.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9458.487 kN ≥ Pn = 5054.080 kN
ΦPn = 0.78 x 5054.080 = 3959.029 kN ≥ Pu = 459.534 kN ∴ O.K
ΦMn = ΦPn x 0.173 = 684.547 kN.m ≥ Mu = 79.457 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 460.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 460.00 = 298.503 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 459.534 |  | 119.732 |  | 0 |  | 260.551
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0029) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 317760.0 x 70.000 + 317760.0 x 460.000) / 11855520.0
= 274.464 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 90.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 4993.920 + 301.554 - 317.760 = 4977.714 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 301.554 x (480.000 - 90.00)
- 4977.714 x (274.464 - 70.000)
= 885.669 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 177.927 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 153.691 mm, a = k1 x c = 130.638 mm 를 사용.
fs = 600 x (480.000 - 153.691) / 153.691 (≤fy) = 400.000 MPa
fs' = 600 x (153.691 - 90.000) / 153.691 (≤fy) = 248.647 MPa
Cc = 0.85 x 24.0 x 130.638 x 1000.000 = 2665.009 kN
Cs = As' x (fs' - 0.85 x fck) = 181.319 kN
Ts = As x fs = 317.760 kN
Pn = 2665.009 + 181.319 - 317.760 = 2528.568 kN
Mn' = 2665.009 x (480.000 - 130.638/2) + 181.319 x (480.000 - 90.00)
= 1175.843 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0080 ＜ 0.0100 (e' = e + Xp - dc = 465.015 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9458.487 kN ≥ Pn = 2528.568 kN
ΦPn = 0.78 x 2528.568 = 1980.712 kN ≥ Pu = 459.534 kN ∴ O.K
ΦMn = ΦPn x 0.261 = 516.077 kN.m ≥ Mu = 119.732 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 311.481 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 489.449 |  | 192.512 |  | 158.902 |  | 393.325
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 90.00 mm) , 1단 : H16- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0043) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 635520.0 x 70.000 + 317760.0 x 460.000) / 12173280.0
= 269.127 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 90.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 635.520 kN
Pb = 4993.920 + 301.554 - 635.520 = 4659.954 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 301.554 x (480.000 - 90.00)
- 4659.954 x (269.127 - 70.000)
= 975.510 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 209.339 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 123.596 mm, a = k1 x c = 105.057 mm 를 사용.
fs = 600 x (480.000 - 123.596) / 123.596 (≤fy) = 400.000 MPa
fs' = 600 x (123.596 - 90.000) / 123.596 (≤fy) = 163.093 MPa
Cc = 0.85 x 24.0 x 105.057 x 1000.000 = 2143.158 kN
Cs = As' x (fs' - 0.85 x fck) = 113.356 kN
Ts = As x fs = 635.520 kN
Pn = 2143.158 + 113.356 - 635.520 = 1620.994 kN
Mn' = 2143.158 x (480.000 - 105.057/2) + 113.356 x (480.000 - 90.00)
= 960.348 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0080 ＜ 0.0100 (e' = e + Xp - dc = 592.452 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9699.730 kN ≥ Pn = 1620.994 kN
ΦPn = 0.78 x 1620.994 = 1269.778 kN ≥ Pu = 489.449 kN ∴ O.K
ΦMn = ΦPn x 0.393 = 499.436 kN.m ≥ Mu = 192.512 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 312.623 kN
≥ Vu (= 158.902 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
2) 상부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
3) 상부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
4) 상부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
5) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
6) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
7) 하부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
8) 하부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 2292 |  | × | 0.2 |  | = | 458.4 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 458.400 ----------> O.K !!!
9) 하부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
10) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
11) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
12) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
13) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
14) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
15) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
16) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
17) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
18) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!

## 거더,기둥검토,내측벽체
21. 거더,기둥,내측벽체 검토
(1) 내측벽체 검토
(단위 : kN,m)
|  | 기둥부재 |  | 폭 | 두께 | 높이 |  | 길이 | 축력 |  | 모멘트 |  | 축력×길이 | 모멘트×길이 | Load Case
|  | P1 |  | 1 | 0.4 | 2.65 |  | 1 | 977.68 |  | 0 |  | 977.68 | 0 | 3
[9 empty] | 542.06 |  | 24.14 |  | 542.06 | 24.14 | 1
* 벽체와 기둥의 판별 (P1)
0.4Agfck = 0.4 × 1000 × 400 × 24
|  |  | = 3840000 N = 3840.00 kN | [6 empty] | ≥ 977.68 kN
∴ 벽체로 검토한다
1)벽체 1
① 축력 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 310 |  | 977.684 |  |  | 0.003 |  | 0 |  | 0.003
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 90.000 + 202720.0 x 310.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 186.000 mm, ab = k1 x cb = 158.100 mm
fs' = 600 x (186.000 - 90.000) / 186.000 (≤fy) = 309.677 MPa
Cc = 0.85 x 24.0 x 158.100 x 1000.000 = 3225.240 kN
Cs = As' x (fs' - 0.85 x fck) = 146.606 kN
Ts = As x fs = 202.720 kN
Pb = 3225.240 + 146.606 - 202.720 = 3169.126 kN
Mb = 3225.240 x (310.000 - 158.100/2) + 146.606 x (310.000 - 90.00)
- 3169.126 x (200.000 - 90.000)
= 428.519 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 135.217 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 473.335 mm, a = k1 x c = 402.334 mm 를 사용.
fs = 600 x (310.000 - 473.335) / 473.335 (≤fy) = 207.043 MPa
fs' = 600 x (473.335 - 90.000) / 473.335 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 402.334 x 1000.000 = 8207.622 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 104.930 kN
Pn = 8207.622 + 192.381 - 104.930 = 8504.933 kN
Mn' = 8207.622 x (310.000 - 402.334/2) + 192.381 x (310.000 - 90.00)
= 935.582 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0012 ＜ 0.0100 (e' = e + Xp - dc = 110.003 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 90.00 = 310.000 mm
c = 600.00 / (600.00+400.00) x 310.000 = 186.000 mm, a = k1 x c = 158.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (310.00-186.00) / 186.00 = 0.0020
εt ≤ εy 이므로 압축지배단면이며, Φ = 0.65 를 적용한다.
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ＜ Pn = 8504.933 kN
ΦPn = 0.65 x 6835.810 = 4443.277 kN ≥ Pu = 977.684 kN ∴ O.K
ΦMn = ΦPn x 0.000 = 0.015 kN.m ≥ Mu = 0.003 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 310.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 310.00 = 222.978 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
② 모멘트 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 310 |  | 542.059 |  |  | 24.14 |  | 0 |  | 44.534
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 90.000 + 202720.0 x 310.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 186.000 mm, ab = k1 x cb = 158.100 mm
fs' = 600 x (186.000 - 90.000) / 186.000 (≤fy) = 309.677 MPa
Cc = 0.85 x 24.0 x 158.100 x 1000.000 = 3225.240 kN
Cs = As' x (fs' - 0.85 x fck) = 146.606 kN
Ts = As x fs = 202.720 kN
Pb = 3225.240 + 146.606 - 202.720 = 3169.126 kN
Mb = 3225.240 x (310.000 - 158.100/2) + 146.606 x (310.000 - 90.00)
- 3169.126 x (200.000 - 90.000)
= 428.519 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 135.217 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 367.731 mm, a = k1 x c = 312.571 mm 를 사용.
fs = 600 x (310.000 - 367.731) / 367.731 (≤fy) = 94.195 MPa
fs' = 600 x (367.731 - 90.000) / 367.731 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 312.571 x 1000.000 = 6376.452 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 47.738 kN
Pn = 6376.452 + 192.381 - 47.738 = 6616.571 kN
Mn' = 6376.452 x (310.000 - 312.571/2) + 192.381 x (310.000 - 90.00)
= 1022.476 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0017 ＜ 0.0100 (e' = e + Xp - dc = 154.534 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 90.00 = 310.000 mm
c = 600.00 / (600.00+400.00) x 310.000 = 186.000 mm, a = k1 x c = 158.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (310.00-186.00) / 186.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ≥ Pn = 6616.571 kN
ΦPn = 0.78 x 6616.571 = 5182.981 kN ≥ Pu = 542.059 kN ∴ O.K
ΦMn = ΦPn x 0.045 = 230.821 kN.m ≥ Mu = 24.140 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 310.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 310.00 = 208.211 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.

## 절점부 검토
22. 절점부 검토
1) 절점 38
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 137.664 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 137.664 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 1131.371 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 137.66 × 10^6 |  |  | = | 0.538 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 1131.371²× 1000
∴ 절점부 보강철근 필요없음 !!!
2) 절점 1
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 120.088 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 120.088 kN.m
R = √(T1² + T2²) = 890.225 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 120.09 × 10^6 |  |  | = | 0.758 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 890.225²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 120.09 × 10^6 |  |  | = | 1498.850 mm²
|  |  |  | R × fsa |  |  | 890.225 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1498.850 mm² - 794.400 mm²
[5 empty] | = | 704.450 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @250 - 4EA
∴ Total As = 1146.000 mm² > Req'd As (= 704.450 mm²) -------------> O.K !!!
3) 절점 26
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 137.666 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 137.666 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 1131.371 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 137.67 × 10^6 |  |  | = | 0.538 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 1131.371²× 1000
∴ 절점부 보강철근 필요없음 !!!
4) 절점 21
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 120.086 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 120.086 kN.m
R = √(T1² + T2²) = 890.225 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 120.09 × 10^6 |  |  | = | 0.758 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 890.225²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 120.09 × 10^6 |  |  | = | 1498.826 mm²
|  |  |  | R × fsa |  |  | 890.225 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1498.826 mm² - 794.400 mm²
[5 empty] | = | 704.426 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @250 - 4EA
∴ Total As = 1146.000 mm² > Req'd As (= 704.426 mm²) -------------> O.K !!!

## 사용성 검토
23. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 746.667 |  | H16 - 8.0EA |  |  | 125 | 487.802 | O.K |  | 3.902
2 | 상부슬래브 : 제 1경간 중앙부 |  | 610 |  | H16 - 8.0EA |  |  | 125 | 442.154 | O.K |  | 3.537
3 | 상부슬래브 : 제 2경간 지점부 |  | 746.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 491.324 | O.K |  | 3.931
4 | 상부슬래브 : 제 2경간 중앙부 |  | 610 |  | H16 - 8.0EA |  |  | 125 | 442.16 | O.K |  | 3.537
5 | 상부슬래브 : 단지점부(우측) |  | 746.667 |  | H16 - 8.0EA |  |  | 125 | 487.793 | O.K |  | 3.902
6 | 하부슬래브 : 단지점부(좌측) |  | 630 |  | H16 - 8.0EA |  |  | 125 | 463.957 | O.K |  | 3.712
7 | 하부슬래브 : 제 1경간 중앙부 |  | 610 |  | H16 - 8.0EA |  |  | 125 | 455.753 | O.K |  | 3.646
8 | 하부슬래브 : 제 2경간 지점부 |  | 630 |  | H19 - 8.0EA |  |  | 125 | 398.474 | O.K |  | 3.188
9 | 하부슬래브 : 제 2경간 중앙부 |  | 610 |  | H16 - 8.0EA |  |  | 125 | 455.636 | O.K |  | 3.645
10 | 하부슬래브 : 단지점부(우측) |  | 630 |  | H16 - 8.0EA |  |  | 125 | 463.967 | O.K |  | 3.712
11 | 좌측벽체 : 상부 |  | 596.667 |  | H16 - 8.0EA |  |  | 125 | 355.596 | O.K |  | 2.845
12 | 좌측벽체 : 중앙부 |  | 460 |  | H16 - 4.0EA |  |  | 250 | 369.088 | O.K |  | 1.476
13 | 좌측벽체 : 중앙부(부모멘트) |  | 480 |  | H16 - 4.0EA |  |  | 250 | 784.192 | O.K |  | 3.137
14 | 좌측벽체 : 하부 |  | 480 |  | H16 - 8.0EA |  |  | 125 | 312.874 | O.K |  | 2.503
15 | 우측벽체 : 상부 |  | 596.667 |  | H16 - 8.0EA |  |  | 125 | 355.589 | O.K |  | 2.845
16 | 우측벽체 : 중앙부 |  | 460 |  | H16 - 4.0EA |  |  | 250 | 369.086 | O.K |  | 1.476
17 | 우측벽체 : 중앙부(부모멘트) |  | 480 |  | H16 - 4.0EA |  |  | 250 | 784.175 | O.K |  | 3.137
18 | 우측벽체 : 하부 |  | 480 |  | H16 - 8.0EA |  |  | 125 | 312.882 | O.K |  | 2.503
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 137.664 x 1000000 / [1588.800 x (746.667 - 118.230/3)]
= 122.511 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x746.7/(7x1588.800)]
= 118.230 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 122.51) - 2.5 x 62.00 = 487.80 mm
300 x (210 / fs) = 300 x (210 / 122.51) = 514.24 mm
Sa는 작은 값인 487.80 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 487.80 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 111.111 x 1000000 / [1588.800 x (610.000 - 105.891/3)]
= 121.687 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x610.0/(7x1588.800)]
= 105.891 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 121.69) - 2.5 x 82.00 = 442.15 mm
300 x (210 / fs) = 300 x (210 / 121.69) = 517.72 mm
Sa는 작은 값인 442.15 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 442.15 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 167.296 x 1000000 / [1940.400 x (746.667 - 129.484/3)]
= 122.554 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x746.7/(7x1940.400)]
= 129.484 mm
Use As = 1940.400 mm² (철근도심 : 70.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 122.55) - 2.5 x 60.50 = 491.32 mm
300 x (210 / fs) = 300 x (210 / 122.55) = 514.06 mm
Sa는 작은 값인 491.32 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 491.32 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 111.110 x 1000000 / [1588.800 x (610.000 - 105.891/3)]
= 121.685 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x610.0/(7x1588.800)]
= 105.891 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 121.69) - 2.5 x 82.00 = 442.16 mm
300 x (210 / fs) = 300 x (210 / 121.69) = 517.73 mm
Sa는 작은 값인 442.16 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 442.16 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 137.666 x 1000000 / [1588.800 x (746.667 - 118.230/3)]
= 122.512 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x746.7/(7x1588.800)]
= 118.230 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 122.51) - 2.5 x 62.00 = 487.79 mm
300 x (210 / fs) = 300 x (210 / 122.51) = 514.23 mm
Sa는 작은 값인 487.79 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 487.79 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 120.088 x 1000000 / [1588.800 x (630.000 - 107.777/3)]
= 127.230 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x630.0/(7x1588.800)]
= 107.777 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 127.23) - 2.5 x 62.00 = 463.96 mm
300 x (210 / fs) = 300 x (210 / 127.23) = 495.17 mm
Sa는 작은 값인 463.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 463.96 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 108.824 x 1000000 / [1588.800 x (610.000 - 105.891/3)]
= 119.182 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x610.0/(7x1588.800)]
= 105.891 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 119.18) - 2.5 x 82.00 = 455.75 mm
300 x (210 / fs) = 300 x (210 / 119.18) = 528.60 mm
Sa는 작은 값인 455.75 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 455.75 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 192.949 x 1000000 / [2292.000 x (630.000 - 127.039/3)]
= 143.254 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x2292.000/1000.0 + 7x2292.000/1000.0 x √[(1 + 2x1000.0x630.0/(7x2292.000)]
= 127.039 mm
Use As = 2292.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 8.0 EA (= 2292.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 143.25) - 2.5 x 60.50 = 398.47 mm
300 x (210 / fs) = 300 x (210 / 143.25) = 439.78 mm
Sa는 작은 값인 398.47 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 398.47 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 108.843 x 1000000 / [1588.800 x (610.000 - 105.891/3)]
= 119.203 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x610.0/(7x1588.800)]
= 105.891 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 119.20) - 2.5 x 82.00 = 455.64 mm
300 x (210 / fs) = 300 x (210 / 119.20) = 528.51 mm
Sa는 작은 값인 455.64 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 455.64 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 120.086 x 1000000 / [1588.800 x (630.000 - 107.777/3)]
= 127.228 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x630.0/(7x1588.800)]
= 107.777 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 127.23) - 2.5 x 62.00 = 463.97 mm
300 x (210 / fs) = 300 x (210 / 127.23) = 495.17 mm
Sa는 작은 값인 463.97 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 463.97 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 137.664 x 1000000 / [1588.800 x (596.667 - 104.617/3)]
= 154.232 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x596.7/(7x1588.800)]
= 104.617 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.23) - 2.5 x 62.00 = 355.60 mm
300 x (210 / fs) = 300 x (210 / 154.23) = 408.48 mm
Sa는 작은 값인 355.60 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 355.60 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 47.723 x 1000000 / [794.400 x (460.000 - 66.181/3)]
= 137.174 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x460.0/(7x794.400)]
= 66.181 mm
Use As = 794.400 mm² (철근도심 : 90.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 137.17) - 2.5 x 82.00 = 369.09 mm
300 x (210 / fs) = 300 x (210 / 137.17) = 459.27 mm
Sa는 작은 값인 369.09 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 369.09 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 29.193 x 1000000 / [794.400 x (480.000 - 67.715/3)]
= 80.337 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x480.0/(7x794.400)]
= 67.715 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 80.34) - 2.5 x 62.00 = 825.24 mm
300 x (210 / fs) = 300 x (210 / 80.34) = 784.19 mm
Sa는 작은 값인 784.19 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 784.19 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 120.088 x 1000000 / [1588.800 x (480.000 - 92.803/3)]
= 168.314 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x480.0/(7x1588.800)]
= 92.803 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 168.31) - 2.5 x 62.00 = 312.87 mm
300 x (210 / fs) = 300 x (210 / 168.31) = 374.30 mm
Sa는 작은 값인 312.87 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 312.87 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 137.666 x 1000000 / [1588.800 x (596.667 - 104.617/3)]
= 154.234 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x596.7/(7x1588.800)]
= 104.617 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.23) - 2.5 x 62.00 = 355.59 mm
300 x (210 / fs) = 300 x (210 / 154.23) = 408.47 mm
Sa는 작은 값인 355.59 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 355.59 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 47.723 x 1000000 / [794.400 x (460.000 - 66.181/3)]
= 137.175 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x460.0/(7x794.400)]
= 66.181 mm
Use As = 794.400 mm² (철근도심 : 90.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 137.17) - 2.5 x 82.00 = 369.09 mm
300 x (210 / fs) = 300 x (210 / 137.17) = 459.27 mm
Sa는 작은 값인 369.09 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 369.09 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 29.194 x 1000000 / [794.400 x (480.000 - 67.715/3)]
= 80.339 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x480.0/(7x794.400)]
= 67.715 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 80.34) - 2.5 x 62.00 = 825.22 mm
300 x (210 / fs) = 300 x (210 / 80.34) = 784.18 mm
Sa는 작은 값인 784.18 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 784.18 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 120.086 x 1000000 / [1588.800 x (480.000 - 92.803/3)]
= 168.312 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x480.0/(7x1588.800)]
= 92.803 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 168.31) - 2.5 x 62.00 = 312.88 mm
300 x (210 / fs) = 300 x (210 / 168.31) = 374.31 mm
Sa는 작은 값인 312.88 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 312.88 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 3.475 m
- fy = 400 MPa
- 부재두께(T) = 0.70 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 3.475 / 28
T = 0.124 m < 0.700 m -----------> O.K

## 기초 지지력 검토
24. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  | = | 373.503 |  | / | 7.5 |  | = | 49.8 |  | kN/m²
|  |  | - 상부연직하중 |  |  | = | 152 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  | 10 |  | kN/m²
3) 내부 수압
|  |  | - 암거내부수압 |  |  | = | 24 |  | kN/m²
4) 최대 지반 반력
|  |  | Qmax | = | 49.8 |  | + | 152 |  | + | 10 |  | + | 24
|  |  |  | = | 235.8 |  | kN/m²

## 주철근 조립도
25. 주철근 조립도