## 표지
H3-34A 구조계산서
| ▣ 구조형식 |  | : | 지중 3 련 암거
( 내공 : 3@(4M ⅹ 4M) )
| ▣ 토 피(FH) |  | = | 7.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 거더,기둥,내측벽체 검토
[5 empty] | 22. | 절점부 검토
[5 empty] | 23. | 사용성 검토
[5 empty] | 24. | 기초 지지력 검토
[5 empty] | 25. | 주철근 조립도

## 설계요약표
1. 설계 요약표
H3-34A (토피=7.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 7.0m
안정(지지력)검토 | Qmax = 225.793 kN/m²
단면 위치 | 내구성검토 |  |  | 단 면 검 토 | [13 empty] | 절 점 부 보 강
| 균열검토 |  |  | 휨 검 토 | [6 empty] | 전 단 검 토
| 철근간격 mm | 최대간격 mm |  | 사용철근 | Mu kN.m |  | ΦMn kN.m |  | S.F |  | 사용철근 |  | Vu kN |  | ΦVn kN |  | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 375.031 |  | H19 - 4.0EA + H16 - 4.0EA | 328.924 |  | 506.442 |  | 1.54 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.756 | 0.637 | H22 @250 - 4EA
상부슬래브 : 제 1경간 중앙부 | 125 | 337.872 |  | H19 - 4.0EA + H16 - 4.0EA | 270.668 |  | 422.875 |  | 1.56 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 지점부 | 125 | 287.834 |  | H19 - 4.0EA + H16 - 4.0EA | 380.428 |  | 506.442 |  | 1.33 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 중앙부 | 125 | 445.229 |  | H16 - 8.0EA | 226.825 |  | 348.112 |  | 1.53 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 3경간 지점부 | 125 | 287.893 |  | H19 - 4.0EA + H16 - 4.0EA | 380.389 |  | 506.442 |  | 1.33 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 3경간 중앙부 | 125 | 337.85 |  | H19 - 4.0EA + H16 - 4.0EA | 270.678 |  | 422.875 |  | 1.56 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 단지점부(우측) | 125 | 375.01 |  | H19 - 4.0EA + H16 - 4.0EA | 322.989 |  | 506.442 |  | 1.57 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.756 | 0.637 | H22 @250 - 4EA
하부슬래브 : 단지점부(좌측) | 125 | 328.298 |  | H19 - 4.0EA + H16 - 4.0EA | 306.664 |  | 429.473 |  | 1.4 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 1.102 | 0.637 | H25 @250 - 4EA
하부슬래브 : 제 1경간 중앙부 | 125 | 325.448 |  | H19 - 4.0EA + H16 - 4.0EA | 277.76 |  | 422.875 |  | 1.52 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 지점부 | 125 | 313.98 |  | H22 - 4.0EA + H19 - 4.0EA | 429.067 |  | 589.585 |  | 1.37 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 중앙부 | 125 | 498.618 |  | H16 - 8.0EA | 174.601 |  | 348.112 |  | 1.99 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 3경간 지점부 | 125 | 313.958 |  | H22 - 4.0EA + H19 - 4.0EA | 420.892 |  | 589.585 |  | 1.4 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 3경간 중앙부 | 125 | 325.387 |  | H19 - 4.0EA + H16 - 4.0EA | 277.794 |  | 422.875 |  | 1.52 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 단지점부(우측) | 125 | 328.312 |  | H19 - 4.0EA + H16 - 4.0EA | 306.657 |  | 429.473 |  | 1.4 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 1.102 | 0.637 | H25 @250 - 4EA
좌측벽체 : 상부 | 125 | 231.402 |  | H19 - 4.0EA + H16 - 4.0EA | 329.668 |  | 585.623 |  | 1.78 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부 | 250 | 285.558 |  | H19 - 4.0EA | 146.364 |  | 561.719 |  | 3.84 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부(부모멘트) | 250 | 587.604 |  | H19 - 4.0EA | 245.705 |  | 326.279 |  | 1.33 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 하부 | 125 | 173.776 |  | H19 - 4.0EA + H16 - 4.0EA | 306.664 |  | 458.362 |  | 1.5 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 상부 | 125 | 231.386 |  | H19 - 4.0EA + H16 - 4.0EA | 322.989 |  | 592.939 |  | 1.84 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부 | 250 | 285.564 |  | H19 - 4.0EA | 147.357 |  | 557.438 |  | 3.78 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부(부모멘트) | 250 | 587.53 |  | H19 - 4.0EA | 236.335 |  | 331.859 |  | 1.4 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 하부 | 125 | 173.785 |  | H19 - 4.0EA + H16 - 4.0EA | 306.657 |  | 458.369 |  | 1.5 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
기둥단면검토
기둥 위치 | 기둥 형태 |  | 사용 철근 |  |  | e |  | eb |  | Pu |  | ΦPn |  | Mu |  | ΦMn |  | 비 고
[6 empty] | (mm) |  | (mm) |  | (kN) |  | (kN) |  | (kN.m) |  | (kN.m)
P1 | 벽 체 |  | H13 |  |  | 7.751 |  | 135.217 |  | 1090.157 |  | 4443.277 |  | 8.45 |  | 34.44 |  | 축력 최대시
[6 empty] | 143.205 |  | 135.217 |  | 625.558 |  | 2267.103 |  | 89.583 |  | 324.659 |  | 모멘트 최대시
P2 | 벽 체 |  | H13 |  |  | 7.745 |  | 135.217 |  | 1090.13 |  | 4443.277 |  | 8.443 |  | 34.412 |  | 축력 최대시
[6 empty] | 142.771 |  | 135.217 |  | 636.607 |  | 2278.477 |  | 90.889 |  | 325.301 |  | 모멘트 최대시

## 설계조건
2. 설계조건
1) 구조형식
- 지중 3 련 암거 ( 내공 : 3@(4M ⅹ 4M), 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 10 |  | kN/m² |  | (∵ 토피 : | 7 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.750 × 1.000 = 0.750 |  |  |  | 0.03516 |  | 1~36,42~59
| 2 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 37~41,60~64
| 3 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 65~66
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.275 | 0.375 | 46 |  | 10.02 |  | 5.125
| 2 |  | 0.55 | 0.375 | 47 |  | 9.35 |  | 5.125
| 3 |  | 0.834 | 0.375 | 48 |  | 9.15 |  | 5.125
| 4 |  | 1.22 | 0.375 | 49 |  | 8.95 |  | 5.125
| 5 |  | 1.394 | 0.375 | 50 |  | 8.28 |  | 5.125
| 6 |  | 1.953 | 0.375 | 51 |  | 6.95 |  | 5.125
| 7 |  | 2.513 | 0.375 | 52 |  | 5.62 |  | 5.125
| 8 |  | 3.072 | 0.375 | 53 |  | 4.95 |  | 5.125
| 9 |  | 3.631 | 0.375 | 54 |  | 4.75 |  | 5.125
| 10 |  | 3.88 | 0.375 | 55 |  | 4.55 |  | 5.125
| 11 |  | 4.191 | 0.375 | 56 |  | 3.88 |  | 5.125
| 12 |  | 4.55 | 0.375 | 57 |  | 2.55 |  | 5.125
| 13 |  | 4.75 | 0.375 | 58 |  | 1.22 |  | 5.125
| 14 |  | 4.95 | 0.375 | 59 |  | 0.55 |  | 5.125
| 15 |  | 5.3 | 0.375 | 60 |  | 0.275 |  | 5.125
| 16 |  | 5.62 | 0.375 | 61 |  | 0.275 |  | 4.75
| 17 |  | 5.85 | 0.375 | 62 |  | 0.275 |  | 4.28
| 18 |  | 6.4 | 0.375 | 63 |  | 0.275 |  | 1.22
| 19 |  | 6.95 | 0.375 | 64 |  | 0.275 |  | 0.75
| 20 |  | 7.5 | 0.375 | 65 |  | 0.275 |  | -0.125
| 21 |  | 8.05 | 0.375 | 66 |  | 0.834 |  | -0.125
| 22 |  | 8.28 | 0.375 | 67 |  | 1.394 |  | -0.125
| 23 |  | 8.6 | 0.375 | 68 |  | 1.953 |  | -0.125
| 24 |  | 8.95 | 0.375 | 69 |  | 2.513 |  | -0.125
| 25 |  | 9.15 | 0.375 | 70 |  | 3.072 |  | -0.125
| 26 |  | 9.35 | 0.375 | 71 |  | 3.631 |  | -0.125
| 27 |  | 9.709 | 0.375 | 72 |  | 4.191 |  | -0.125
| 28 |  | 10.02 | 0.375 | 73 |  | 4.75 |  | -0.125
| 29 |  | 10.269 | 0.375 | 74 |  | 5.3 |  | -0.125
| 30 |  | 10.828 | 0.375 | 75 |  | 5.85 |  | -0.125
| 31 |  | 11.388 | 0.375 | 76 |  | 6.4 |  | -0.125
| 32 |  | 11.947 | 0.375 | 77 |  | 6.95 |  | -0.125
| 33 |  | 12.506 | 0.375 | 78 |  | 7.5 |  | -0.125
| 34 |  | 12.68 | 0.375 | 79 |  | 8.05 |  | -0.125
| 35 |  | 13.066 | 0.375 | 80 |  | 8.6 |  | -0.125
| 36 |  | 13.35 | 0.375 | 81 |  | 9.15 |  | -0.125
| 37 |  | 13.625 | 0.375 | 82 |  | 9.709 |  | -0.125
| 38 |  | 13.625 | 0.75 | 83 |  | 10.269 |  | -0.125
| 39 |  | 13.625 | 1.22 | 84 |  | 10.828 |  | -0.125
| 40 |  | 13.625 | 4.28 | 85 |  | 11.388 |  | -0.125
| 41 |  | 13.625 | 4.75 | 86 |  | 11.947 |  | -0.125
| 42 |  | 13.625 | 5.125 | 87 |  | 12.506 |  | -0.125
| 43 |  | 13.35 | 5.125 | 88 |  | 13.066 |  | -0.125
| 44 |  | 12.68 | 5.125 | 89 |  | 13.625 |  | -0.125
| 45 |  | 11.35 | 5.125

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.750 × 1.000 = 0.750 |  |  |  | 0.03516 |  | 1~36,51~86
| 2 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 37~50,87~100
| 3 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 101~102
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.275 | 0.375 | 86 |  | 0.55 |  | 5.125
| 2 |  | 0.55 | 0.375 | 87 |  | 0.275 |  | 5.125
| 3 |  | 0.834 | 0.375 | 88 |  | 0.275 |  | 4.75
| 4 |  | 1.22 | 0.375 | 89 |  | 0.275 |  | 4.597
| 5 |  | 1.394 | 0.375 | 90 |  | 0.275 |  | 4.28
| 6 |  | 1.953 | 0.375 | 91 |  | 0.275 |  | 4.069
| 7 |  | 2.513 | 0.375 | 92 |  | 0.275 |  | 3.542
| 8 |  | 3.072 | 0.375 | 93 |  | 0.275 |  | 3.014
| 9 |  | 3.631 | 0.375 | 94 |  | 0.275 |  | 2.75
| 10 |  | 3.88 | 0.375 | 95 |  | 0.275 |  | 2.486
| 11 |  | 4.191 | 0.375 | 96 |  | 0.275 |  | 1.958
| 12 |  | 4.55 | 0.375 | 97 |  | 0.275 |  | 1.431
| 13 |  | 4.75 | 0.375 | 98 |  | 0.275 |  | 1.22
| 14 |  | 4.95 | 0.375 | 99 |  | 0.275 |  | 0.903
| 15 |  | 5.3 | 0.375 | 100 |  | 0.275 |  | 0.75
| 16 |  | 5.62 | 0.375 | 101 |  | 0.275 |  | -0.125
| 17 |  | 5.85 | 0.375 | 102 |  | 0.834 |  | -0.125
| 18 |  | 6.4 | 0.375 | 103 |  | 1.394 |  | -0.125
| 19 |  | 6.95 | 0.375 | 104 |  | 1.953 |  | -0.125
| 20 |  | 7.5 | 0.375 | 105 |  | 2.513 |  | -0.125
| 21 |  | 8.05 | 0.375 | 106 |  | 3.072 |  | -0.125
| 22 |  | 8.28 | 0.375 | 107 |  | 3.631 |  | -0.125
| 23 |  | 8.6 | 0.375 | 108 |  | 4.191 |  | -0.125
| 24 |  | 8.95 | 0.375 | 109 |  | 4.75 |  | -0.125
| 25 |  | 9.15 | 0.375 | 110 |  | 5.3 |  | -0.125
| 26 |  | 9.35 | 0.375 | 111 |  | 5.85 |  | -0.125
| 27 |  | 9.709 | 0.375 | 112 |  | 6.4 |  | -0.125
| 28 |  | 10.02 | 0.375 | 113 |  | 6.95 |  | -0.125
| 29 |  | 10.269 | 0.375 | 114 |  | 7.5 |  | -0.125
| 30 |  | 10.828 | 0.375 | 115 |  | 8.05 |  | -0.125
| 31 |  | 11.388 | 0.375 | 116 |  | 8.6 |  | -0.125
| 32 |  | 11.947 | 0.375 | 117 |  | 9.15 |  | -0.125
| 33 |  | 12.506 | 0.375 | 118 |  | 9.709 |  | -0.125
| 34 |  | 12.68 | 0.375 | 119 |  | 10.269 |  | -0.125
| 35 |  | 13.066 | 0.375 | 120 |  | 10.828 |  | -0.125
| 36 |  | 13.35 | 0.375 | 121 |  | 11.388 |  | -0.125
| 37 |  | 13.625 | 0.375 | 122 |  | 11.947 |  | -0.125
| 38 |  | 13.625 | 0.75 | 123 |  | 12.506 |  | -0.125
| 39 |  | 13.625 | 0.903 | 124 |  | 13.066 |  | -0.125
| 40 |  | 13.625 | 1.22 | 125 |  | 13.625 |  | -0.125
| 41 |  | 13.625 | 1.431 | 126 |  | 14.125 |  | 0.375
| 42 |  | 13.625 | 1.958 | 127 |  | 14.125 |  | 0.903
| 43 |  | 13.625 | 2.486 | 128 |  | 14.125 |  | 1.431
| 44 |  | 13.625 | 2.75 | 129 |  | 14.125 |  | 1.958
| 45 |  | 13.625 | 3.014 | 130 |  | 14.125 |  | 2.486
| 46 |  | 13.625 | 3.542 | 131 |  | 14.125 |  | 3.014
| 47 |  | 13.625 | 4.069 | 132 |  | 14.125 |  | 3.542
| 48 |  | 13.625 | 4.28 | 133 |  | 14.125 |  | 4.069
| 49 |  | 13.625 | 4.597 | 134 |  | 14.125 |  | 4.597
| 50 |  | 13.625 | 4.75 | 135 |  | 14.125 |  | 5.125
| 51 |  | 13.625 | 5.125 | 136 |  | 13.625 |  | 5.625
| 52 |  | 13.35 | 5.125 | 137 |  | 13.066 |  | 5.625
| 53 |  | 13.066 | 5.125 | 138 |  | 12.506 |  | 5.625
| 54 |  | 12.68 | 5.125 | 139 |  | 11.947 |  | 5.625
| 55 |  | 12.506 | 5.125 | 140 |  | 11.387 |  | 5.625
| 56 |  | 11.947 | 5.125 | 141 |  | 10.828 |  | 5.625
| 57 |  | 11.387 | 5.125 | 142 |  | 10.269 |  | 5.625
| 58 |  | 10.828 | 5.125 | 143 |  | 9.709 |  | 5.625
| 59 |  | 10.269 | 5.125 | 144 |  | 9.15 |  | 5.625
| 60 |  | 10.02 | 5.125 | 145 |  | 8.6 |  | 5.625
| 61 |  | 9.709 | 5.125 | 146 |  | 8.05 |  | 5.625
| 62 |  | 9.35 | 5.125 | 147 |  | 7.5 |  | 5.625
| 63 |  | 9.15 | 5.125 | 148 |  | 6.95 |  | 5.625
| 64 |  | 8.95 | 5.125 | 149 |  | 6.4 |  | 5.625
| 65 |  | 8.6 | 5.125 | 150 |  | 5.85 |  | 5.625
| 66 |  | 8.28 | 5.125 | 151 |  | 5.3 |  | 5.625
| 67 |  | 8.05 | 5.125 | 152 |  | 4.75 |  | 5.625
| 68 |  | 7.5 | 5.125 | 153 |  | 4.191 |  | 5.625
| 69 |  | 6.95 | 5.125 | 154 |  | 3.631 |  | 5.625
| 70 |  | 6.4 | 5.125 | 155 |  | 3.072 |  | 5.625
| 71 |  | 5.85 | 5.125 | 156 |  | 2.513 |  | 5.625
| 72 |  | 5.62 | 5.125 | 157 |  | 1.953 |  | 5.625
| 73 |  | 5.3 | 5.125 | 158 |  | 1.394 |  | 5.625
| 74 |  | 4.95 | 5.125 | 159 |  | 0.834 |  | 5.625
| 75 |  | 4.75 | 5.125 | 160 |  | 0.275 |  | 5.625
| 76 |  | 4.55 | 5.125 | 161 |  | -0.225 |  | 5.125
| 77 |  | 4.191 | 5.125 | 162 |  | -0.225 |  | 4.597
| 78 |  | 3.88 | 5.125 | 163 |  | -0.225 |  | 4.069
| 79 |  | 3.631 | 5.125 | 164 |  | -0.225 |  | 3.542
| 80 |  | 3.072 | 5.125 | 165 |  | -0.225 |  | 3.014
| 81 |  | 2.513 | 5.125 | 166 |  | -0.225 |  | 2.486
| 82 |  | 1.953 | 5.125 | 167 |  | -0.225 |  | 1.958
| 83 |  | 1.394 | 5.125 | 168 |  | -0.225 |  | 1.431
| 84 |  | 1.22 | 5.125 | 169 |  | -0.225 |  | 0.903
| 85 |  | 0.834 | 5.125 | 170 |  | -0.225 |  | 0.375

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 13.900 × 13.900 ) |  |  | = | 13.9 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 13.900 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 7883.297 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.550/2 + 0.559/2) = 4371 kN/m |  |  |  |  | 1,13,25,37
| Kv2 |  |  | Kvⅹ(0.559/2 + 0.559/2) = 4407 kN/m |  |  |  |  | 3,5~9,11,27,29~33,35
| Kv3 |  |  | Kvⅹ(0.550/2 + 0.550/2) = 4336 kN/m |  |  |  |  | 15,17~21,23
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 4.750m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 13.900 × 13.900 ) |  |  |  |  | = | 13.9 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 13.900 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 19832.27 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 19832.270 |  |  |  |  | = | 6610.76 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 13.900 × 13.900 ) |  |  |  |  | = | 13.9 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 13.900 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 19832.27 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 19832.270 |  |  |  |  | = | 6610.76 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 5.500 × 5.500 ) |  |  |  |  | = | 5.5 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 5.500 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 39752.24 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 39752.240 |  |  |  |  | = | 13250.75 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.559/2 + 0.550/2) = 10997 kN/m | [8 empty] | 51,63,75,87
|  | Ksb1 |  |  | Ksbⅹ(0.559/2 + 0.550/2) = 3666 kN/m
|  | Kv2 |  |  | Kvⅹ(0.559/2 + 0.559/2) = 11086 kN/m | [8 empty] | 53,55~59,61,77,79~83,85
|  | Ksb2 |  |  | Ksbⅹ(0.559/2 + 0.559/2) = 3695 kN/m
|  | Kv3 |  |  | Kvⅹ(0.550/2 + 0.550/2) = 10908 kN/m | [8 empty] | 65,67~71,73
|  | Ksb3 |  |  | Ksbⅹ(0.550/2 + 0.550/2) = 3636 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(0.528/2 + 0.750/2) = 25402 kN/m | [8 empty] | 1,37,51,87
|  | Kss1 |  |  | Kssⅹ(0.528/2 + 0.750/2) = 8467 kN/m
|  | Kh2 |  |  | Khⅹ(0.528/2 + 0.528/2) = 20989 kN/m | [8 empty] | 39,41~43,45~47,49,89,91~93,95~97,99
|  | Kss2 |  |  | Kssⅹ(0.528/2 + 0.528/2) = 6996 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.550/2 + 0.559/2) = 10997 kN/m | [8 empty] | 1,13,25,37
|  | Ksb1 |  |  | Ksbⅹ(0.550/2 + 0.559/2) = 3666 kN/m
|  | Kv2 |  |  | Kvⅹ(0.559/2 + 0.559/2) = 11086 kN/m | [8 empty] | 3,5~9,11,27,29~33,35
|  | Ksb2 |  |  | Ksbⅹ(0.559/2 + 0.559/2) = 3695 kN/m
|  | Kv3 |  |  | Kvⅹ(0.550/2 + 0.550/2) = 10908 kN/m | [8 empty] | 15,17~21,23
|  | Ksb3 |  |  | Ksbⅹ(0.550/2 + 0.550/2) = 3636 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 7.00 × 19.00 |  |  |  |  | = | 133 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 133 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 상부 슬래브에 작용하는 하중 (Wl1) - 토피 4m 이상
|  |  | - Wl1 |  | = | 10.000 kN/m²
② 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (7.375 × 19.000) × 0.500 | [9 empty] | = | 70.063 | kN/m²
|  | - Wh2 |  | = | 70.063 + 0.375 × 19.000 × 0.500 | [9 empty] | = | 73.625 | kN/m²
|  | - Wh3 |  | = | 73.625 + 0.470 × 19.000 × 0.500 | [9 empty] | = | 78.091 | kN/m²
|  | - Wh4 |  | = | 78.091 + 3.060 × 19.000 × 0.500 | [9 empty] | = | 107.16 | kN/m²
|  | - Wh5 |  | = | 107.160 + 0.470 × 19.000 × 0.500 | [9 empty] | = | 111.626 | kN/m²
|  | - Wh6 |  | = | 111.626 + 0.375 × 19.000 × 0.500 | [9 empty] | = | 115.188 | kN/m²
5) 암거내부수압
- Win = 32.000 kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 11.75 |  | 197.3 |  |  |  | 19 |  |  | 0.238
|  | 계 | [11 empty] | 0.238
Tg = 1.25 Tg' = 1.25 × 0.238 = 0.298 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.298 / 2π × 2.617 = 0.124 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 7.375 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 12.125 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.124 × 0.298 × cos(π× 7.375 / (2 × 30.000)) = 0.006937
U(Zb) = 2 / π²× 0.124 × 0.298 × cos(π× 12.125 / (2 × 30.000)) = 0.006029
Po = Ksb,top × (U(Zu) - U(Zb))
= 6610.760 × (0.006937 - 0.006029) = 6.003 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 7.375 |  | 39752.24 |  |  |  | 0.006937 |  |  |  |  | 0.000908 |  | 36.095
|  | 7.75 |  | 39752.24 |  |  |  | 0.00688 |  |  |  |  | 0.000851 |  | 33.829
|  | 7.903 |  | 39752.24 |  |  |  | 0.006856 |  |  |  |  | 0.000827 |  | 32.875
|  | 8.22 |  | 39752.24 |  |  |  | 0.006805 |  |  |  |  | 0.000776 |  | 30.848
|  | 8.431 |  | 39752.24 |  |  |  | 0.00677 |  |  |  |  | 0.000741 |  | 29.456
|  | 8.958 |  | 39752.24 |  |  |  | 0.006679 |  |  |  |  | 0.00065 |  | 25.839
|  | 9.486 |  | 39752.24 |  |  |  | 0.006583 |  |  |  |  | 0.000554 |  | 22.023
|  | 9.75 |  | 39752.24 |  |  |  | 0.006533 |  |  |  |  | 0.000504 |  | 20.035
|  | 10.014 |  | 39752.24 |  |  |  | 0.006482 |  |  |  |  | 0.000453 |  | 18.008
|  | 10.542 |  | 39752.24 |  |  |  | 0.006376 |  |  |  |  | 0.000347 |  | 13.794
|  | 11.069 |  | 39752.24 |  |  |  | 0.006265 |  |  |  |  | 0.000236 |  | 9.382
|  | 11.28 |  | 39752.24 |  |  |  | 0.00622 |  |  |  |  | 0.000191 |  | 7.593
|  | 11.597 |  | 39752.24 |  |  |  | 0.006149 |  |  |  |  | 0.00012 |  | 4.77
|  | 11.75 |  | 39752.24 |  |  |  | 0.006115 |  |  |  |  | 8.6e-05 |  | 3.419
|  | 12.125 |  | 39752.24 |  |  |  | 0.006029 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000148 = 2.790 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000233 = 4.400 kN/m²
Vs = (Vu - Vb) / 2 = (2.790 + 4.400) / 2 = 3.600 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.750 × 24.500 × 0.160 × (1 - 0.015 × 7.375) = 2.615 kN/m²
② 하부슬래브
fb = 0.750 × 24.500 × 0.160 × (1 - 0.015 × 12.125) = 2.405 kN/m²
③ 중간벽체
fu1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 7.375) = 1.395 kN/m²
fb1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 12.125) = 1.283 kN/m²
fu2 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 7.375) = 1.395 kN/m²
fb2 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 12.125) = 1.283 kN/m²
④ 측벽
f1 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 7.375) = 1.917 kN/m²
f2 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 7.750) = 1.905 kN/m²
f3 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 7.903) = 1.900 kN/m²
f4 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.220) = 1.890 kN/m²
f5 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.431) = 1.883 kN/m²
f6 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.958) = 1.866 kN/m²
f7 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.486) = 1.849 kN/m²
f8 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.750) = 1.841 kN/m²
f9 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.014) = 1.832 kN/m²
f10 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.542) = 1.815 kN/m²
f11 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.069) = 1.798 kN/m²
f12 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.280) = 1.791 kN/m²
f13 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.597) = 1.781 kN/m²
f14 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.750) = 1.776 kN/m²
f15 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 12.125) = 1.764 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)
6) CASE6 - 암거내부수압

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 0.875, h = 7.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
2) 극한하중 기둥최대편심 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
3) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1
| 2 |  | 1 | 0.875 |  | 1 | 1
| 3 |  | 1 | 0.875 | 1 | 0.5 | 0.5
4) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | 80 X= 8.600 Y= 0.000 Z= -0.125
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 81 X= 9.150 Y= 0.000 Z= -0.125
82 X= 9.709 Y= 0.000 Z= -0.125
| JOINT | 83 X= 10.269 Y= 0.000 Z= -0.125
| 1 X= 0.275 Y= 0.000 Z= 0.375 | 84 X= 10.828 Y= 0.000 Z= -0.125
| 2 X= 0.550 Y= 0.000 Z= 0.375 | 85 X= 11.388 Y= 0.000 Z= -0.125
| 3 X= 0.834 Y= 0.000 Z= 0.375 | 86 X= 11.947 Y= 0.000 Z= -0.125
| 4 X= 1.220 Y= 0.000 Z= 0.375 | 87 X= 12.506 Y= 0.000 Z= -0.125
| 5 X= 1.394 Y= 0.000 Z= 0.375 | 88 X= 13.066 Y= 0.000 Z= -0.125
| 6 X= 1.953 Y= 0.000 Z= 0.375 | 89 X= 13.625 Y= 0.000 Z= -0.125
7 X= 2.513 Y= 0.000 Z= 0.375
| 8 X= 3.072 Y= 0.000 Z= 0.375 | RESTRAINT
| 9 X= 3.631 Y= 0.000 Z= 0.375 | ADD=65 DOF=U1, U2, U3, R1, R2, R3
| 10 X= 3.880 Y= 0.000 Z= 0.375 | ADD=66 DOF=U1, U2, U3, R1, R2, R3
| 11 X= 4.191 Y= 0.000 Z= 0.375 | ADD=67 DOF=U1, U2, U3, R1, R2, R3
| 12 X= 4.550 Y= 0.000 Z= 0.375 | ADD=68 DOF=U1, U2, U3, R1, R2, R3
| 13 X= 4.750 Y= 0.000 Z= 0.375 | ADD=69 DOF=U1, U2, U3, R1, R2, R3
| 14 X= 4.950 Y= 0.000 Z= 0.375 | ADD=70 DOF=U1, U2, U3, R1, R2, R3
| 15 X= 5.300 Y= 0.000 Z= 0.375 | ADD=71 DOF=U1, U2, U3, R1, R2, R3
| 16 X= 5.620 Y= 0.000 Z= 0.375 | ADD=72 DOF=U1, U2, U3, R1, R2, R3
| 17 X= 5.850 Y= 0.000 Z= 0.375 | ADD=73 DOF=U1, U2, U3, R1, R2, R3
| 18 X= 6.400 Y= 0.000 Z= 0.375 | ADD=74 DOF=U1, U2, U3, R1, R2, R3
| 19 X= 6.950 Y= 0.000 Z= 0.375 | ADD=75 DOF=U1, U2, U3, R1, R2, R3
| 20 X= 7.500 Y= 0.000 Z= 0.375 | ADD=76 DOF=U1, U2, U3, R1, R2, R3
| 21 X= 8.050 Y= 0.000 Z= 0.375 | ADD=77 DOF=U1, U2, U3, R1, R2, R3
| 22 X= 8.280 Y= 0.000 Z= 0.375 | ADD=78 DOF=U1, U2, U3, R1, R2, R3
| 23 X= 8.600 Y= 0.000 Z= 0.375 | ADD=79 DOF=U1, U2, U3, R1, R2, R3
| 24 X= 8.950 Y= 0.000 Z= 0.375 | ADD=80 DOF=U1, U2, U3, R1, R2, R3
| 25 X= 9.150 Y= 0.000 Z= 0.375 | ADD=81 DOF=U1, U2, U3, R1, R2, R3
| 26 X= 9.350 Y= 0.000 Z= 0.375 | ADD=82 DOF=U1, U2, U3, R1, R2, R3
| 27 X= 9.709 Y= 0.000 Z= 0.375 | ADD=83 DOF=U1, U2, U3, R1, R2, R3
| 28 X= 10.020 Y= 0.000 Z= 0.375 | ADD=84 DOF=U1, U2, U3, R1, R2, R3
| 29 X= 10.269 Y= 0.000 Z= 0.375 | ADD=85 DOF=U1, U2, U3, R1, R2, R3
| 30 X= 10.828 Y= 0.000 Z= 0.375 | ADD=86 DOF=U1, U2, U3, R1, R2, R3
| 31 X= 11.388 Y= 0.000 Z= 0.375 | ADD=87 DOF=U1, U2, U3, R1, R2, R3
| 32 X= 11.947 Y= 0.000 Z= 0.375 | ADD=88 DOF=U1, U2, U3, R1, R2, R3
| 33 X= 12.506 Y= 0.000 Z= 0.375 | ADD=89 DOF=U1, U2, U3, R1, R2, R3
34 X= 12.680 Y= 0.000 Z= 0.375
| 35 X= 13.066 Y= 0.000 Z= 0.375 | SPRING
| 36 X= 13.350 Y= 0.000 Z= 0.375 | ADD=1 U1=1e+010
37 X= 13.625 Y= 0.000 Z= 0.375
| 38 X= 13.625 Y= 0.000 Z= 0.750 | MATERIAL
| 39 X= 13.625 Y= 0.000 Z= 1.220 | NAME=CONC IDES=C M=0.0001 W=24.5
| 40 X= 13.625 Y= 0.000 Z= 4.280 | T=0 E=2.7e+007 U=0.17 A=9.99e-006
41 X= 13.625 Y= 0.000 Z= 4.750
| 42 X= 13.625 Y= 0.000 Z= 5.125 | NLPROP
| 43 X= 13.350 Y= 0.000 Z= 5.125 | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 44 X= 12.680 Y= 0.000 Z= 5.125 | DOF=U1 KE=4371.29 CE=0.99999 K=4371.29 OPEN=0
| 45 X= 11.350 Y= 0.000 Z= 5.125 | NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 46 X= 10.020 Y= 0.000 Z= 5.125 | DOF=U1 KE=4406.77 CE=0.99999 K=4406.77 OPEN=0
| 47 X= 9.350 Y= 0.000 Z= 5.125 | NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 48 X= 9.150 Y= 0.000 Z= 5.125 | DOF=U1 KE=4335.81 CE=0.99999 K=4335.81 OPEN=0
49 X= 8.950 Y= 0.000 Z= 5.125
| 50 X= 8.280 Y= 0.000 Z= 5.125 | FRAME SECTION
| 51 X= 6.950 Y= 0.000 Z= 5.125 | NAME=1 MAT=CONC SH=R T=0.75, 1
| 52 X= 5.620 Y= 0.000 Z= 5.125 | NAME=2 MAT=CONC SH=R T=0.55, 1
| 53 X= 4.950 Y= 0.000 Z= 5.125 | NAME=3 MAT=CONC SH=R T=0.4, 1
54 X= 4.750 Y= 0.000 Z= 5.125
| 55 X= 4.550 Y= 0.000 Z= 5.125 | FRAME
| 56 X= 3.880 Y= 0.000 Z= 5.125 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 57 X= 2.550 Y= 0.000 Z= 5.125 | 2 J= 2, 3 SEC=1 NSEG=1 ANG=180
| 58 X= 1.220 Y= 0.000 Z= 5.125 | 3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 59 X= 0.550 Y= 0.000 Z= 5.125 | 4 J= 4, 5 SEC=1 NSEG=1 ANG=180
| 60 X= 0.275 Y= 0.000 Z= 5.125 | 5 J= 5, 6 SEC=1 NSEG=2 ANG=180
| 61 X= 0.275 Y= 0.000 Z= 4.750 | 6 J= 6, 7 SEC=1 NSEG=2 ANG=180
| 62 X= 0.275 Y= 0.000 Z= 4.280 | 7 J= 7, 8 SEC=1 NSEG=2 ANG=180
| 63 X= 0.275 Y= 0.000 Z= 1.220 | 8 J= 8, 9 SEC=1 NSEG=2 ANG=180
| 64 X= 0.275 Y= 0.000 Z= 0.750 | 9 J= 9, 10 SEC=1 NSEG=1 ANG=180
| 65 X= 0.275 Y= 0.000 Z= -0.125 | 10 J= 10, 11 SEC=1 NSEG=1 ANG=180
| 66 X= 0.834 Y= 0.000 Z= -0.125 | 11 J= 11, 12 SEC=1 NSEG=1 ANG=180
| 67 X= 1.394 Y= 0.000 Z= -0.125 | 12 J= 12, 13 SEC=1 NSEG=1 ANG=180
| 68 X= 1.953 Y= 0.000 Z= -0.125 | 13 J= 13, 14 SEC=1 NSEG=1 ANG=180
| 69 X= 2.513 Y= 0.000 Z= -0.125 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=180
| 70 X= 3.072 Y= 0.000 Z= -0.125 | 15 J= 15, 16 SEC=1 NSEG=1 ANG=180
| 71 X= 3.631 Y= 0.000 Z= -0.125 | 16 J= 16, 17 SEC=1 NSEG=1 ANG=180
| 72 X= 4.191 Y= 0.000 Z= -0.125 | 17 J= 17, 18 SEC=1 NSEG=2 ANG=180
| 73 X= 4.750 Y= 0.000 Z= -0.125 | 18 J= 18, 19 SEC=1 NSEG=2 ANG=180
| 74 X= 5.300 Y= 0.000 Z= -0.125 | 19 J= 19, 20 SEC=1 NSEG=2 ANG=180
| 75 X= 5.850 Y= 0.000 Z= -0.125 | 20 J= 20, 21 SEC=1 NSEG=2 ANG=180
| 76 X= 6.400 Y= 0.000 Z= -0.125 | 21 J= 21, 22 SEC=1 NSEG=1 ANG=180
| 77 X= 6.950 Y= 0.000 Z= -0.125 | 22 J= 22, 23 SEC=1 NSEG=1 ANG=180
| 78 X= 7.500 Y= 0.000 Z= -0.125 | 23 J= 23, 24 SEC=1 NSEG=1 ANG=180
| 79 X= 8.050 Y= 0.000 Z= -0.125 | 24 J= 24, 25 SEC=1 NSEG=1 ANG=180
| 25 J= 25, 26 SEC=1 NSEG=1 ANG=180 | ADD=54 RD=0,1 UZ=-133,-133
| 26 J= 26, 27 SEC=1 NSEG=1 ANG=180 | ADD=55 RD=0,1 UZ=-133,-133
| 27 J= 27, 28 SEC=1 NSEG=1 ANG=180 | ADD=56 RD=0,1 UZ=-133,-133
| 28 J= 28, 29 SEC=1 NSEG=1 ANG=180 | ADD=57 RD=0,1 UZ=-133,-133
| 29 J= 29, 30 SEC=1 NSEG=2 ANG=180 | ADD=58 RD=0,1 UZ=-133,-133
| 30 J= 30, 31 SEC=1 NSEG=2 ANG=180 | ADD=59 RD=0,1 UZ=-133,-133
| 31 J= 31, 32 SEC=1 NSEG=2 ANG=180 | NAME=LIVEFULL
| 32 J= 32, 33 SEC=1 NSEG=2 ANG=180 | TYPE=Distributed Span
| 33 J= 33, 34 SEC=1 NSEG=1 ANG=180 | ADD=42 RD=0,1 UZ=-10,-10
| 34 J= 34, 35 SEC=1 NSEG=1 ANG=180 | ADD=43 RD=0,1 UZ=-10,-10
| 35 J= 35, 36 SEC=1 NSEG=1 ANG=180 | ADD=44 RD=0,1 UZ=-10,-10
| 36 J= 36, 37 SEC=1 NSEG=1 ANG=180 | ADD=45 RD=0,1 UZ=-10,-10
| 37 J= 37, 38 SEC=2 NSEG=1 ANG=0 | ADD=46 RD=0,1 UZ=-10,-10
| 38 J= 38, 39 SEC=2 NSEG=1 ANG=0 | ADD=47 RD=0,1 UZ=-10,-10
| 39 J= 39, 40 SEC=2 NSEG=4 ANG=0 | ADD=48 RD=0,1 UZ=-10,-10
| 40 J= 40, 41 SEC=2 NSEG=1 ANG=0 | ADD=49 RD=0,1 UZ=-10,-10
| 41 J= 41, 42 SEC=2 NSEG=1 ANG=0 | ADD=50 RD=0,1 UZ=-10,-10
| 42 J= 42, 43 SEC=1 NSEG=1 ANG=0 | ADD=51 RD=0,1 UZ=-10,-10
| 43 J= 43, 44 SEC=1 NSEG=2 ANG=0 | ADD=52 RD=0,1 UZ=-10,-10
| 44 J= 44, 45 SEC=1 NSEG=4 ANG=0 | ADD=53 RD=0,1 UZ=-10,-10
| 45 J= 45, 46 SEC=1 NSEG=4 ANG=0 | ADD=54 RD=0,1 UZ=-10,-10
| 46 J= 46, 47 SEC=1 NSEG=2 ANG=0 | ADD=55 RD=0,1 UZ=-10,-10
| 47 J= 47, 48 SEC=1 NSEG=1 ANG=0 | ADD=56 RD=0,1 UZ=-10,-10
| 48 J= 48, 49 SEC=1 NSEG=1 ANG=0 | ADD=57 RD=0,1 UZ=-10,-10
| 49 J= 49, 50 SEC=1 NSEG=2 ANG=0 | ADD=58 RD=0,1 UZ=-10,-10
| 50 J= 50, 51 SEC=1 NSEG=4 ANG=0 | ADD=59 RD=0,1 UZ=-10,-10
| 51 J= 51, 52 SEC=1 NSEG=4 ANG=0 | NAME=HORLIVE
| 52 J= 52, 53 SEC=1 NSEG=2 ANG=0 | TYPE=Distributed Span
| 53 J= 53, 54 SEC=1 NSEG=1 ANG=0 | ADD=37 RD=0,1 UX=-5,-5
| 54 J= 54, 55 SEC=1 NSEG=1 ANG=0 | ADD=38 RD=0,1 UX=-5,-5
| 55 J= 55, 56 SEC=1 NSEG=2 ANG=0 | ADD=39 RD=0,1 UX=-5,-5
| 56 J= 56, 57 SEC=1 NSEG=4 ANG=0 | ADD=40 RD=0,1 UX=-5,-5
| 57 J= 57, 58 SEC=1 NSEG=4 ANG=0 | ADD=41 RD=0,1 UX=-5,-5
| 58 J= 58, 59 SEC=1 NSEG=2 ANG=0 | ADD=60 RD=0,1 UX=5,5
| 59 J= 59, 60 SEC=1 NSEG=1 ANG=0 | ADD=61 RD=0,1 UX=5,5
| 60 J= 60, 61 SEC=2 NSEG=1 ANG=180 | ADD=62 RD=0,1 UX=5,5
| 61 J= 61, 62 SEC=2 NSEG=1 ANG=180 | ADD=63 RD=0,1 UX=5,5
| 62 J= 62, 63 SEC=2 NSEG=4 ANG=180 | ADD=64 RD=0,1 UX=5,5
| 63 J= 63, 64 SEC=2 NSEG=1 ANG=180 | NAME=NWSOFULL
| 64 J= 64, 1 SEC=2 NSEG=1 ANG=180 | TYPE=Distributed Span
| 65 J= 54, 13 SEC=3 NSEG=4 ANG=0 | ADD=37 RD=0,1 UX=-115.188,-111.626
| 66 J= 48, 25 SEC=3 NSEG=4 ANG=0 | ADD=38 RD=0,1 UX=-111.626,-107.16
ADD=39 RD=0,1 UX=-107.16,-78.091
| NLLINK | ADD=40 RD=0,1 UX=-78.091,-73.625
| 1 J=1,65 NLP=SP1 ANG=0 | ADD=41 RD=0,1 UX=-73.625,-70.063
| 2 J=3,66 NLP=SP2 ANG=0 | ADD=60 RD=0,1 UX=70.063,73.625
| 3 J=5,67 NLP=SP2 ANG=0 | ADD=61 RD=0,1 UX=73.625,78.091
| 4 J=6,68 NLP=SP2 ANG=0 | ADD=62 RD=0,1 UX=78.091,107.16
| 5 J=7,69 NLP=SP2 ANG=0 | ADD=63 RD=0,1 UX=107.16,111.626
| 6 J=8,70 NLP=SP2 ANG=0 | ADD=64 RD=0,1 UX=111.626,115.188
| 7 J=9,71 NLP=SP2 ANG=0 | NAME=INWATER
| 8 J=11,72 NLP=SP2 ANG=0 | TYPE=Distributed Span
| 9 J=13,73 NLP=SP1 ANG=0 | ADD=2 RD=0,1 UZ=-32,-32
| 10 J=15,74 NLP=SP3 ANG=0 | ADD=3 RD=0,1 UZ=-32,-32
| 11 J=17,75 NLP=SP3 ANG=0 | ADD=4 RD=0,1 UZ=-32,-32
| 12 J=18,76 NLP=SP3 ANG=0 | ADD=5 RD=0,1 UZ=-32,-32
| 13 J=19,77 NLP=SP3 ANG=0 | ADD=6 RD=0,1 UZ=-32,-32
| 14 J=20,78 NLP=SP3 ANG=0 | ADD=7 RD=0,1 UZ=-32,-32
| 15 J=21,79 NLP=SP3 ANG=0 | ADD=8 RD=0,1 UZ=-32,-32
| 16 J=23,80 NLP=SP3 ANG=0 | ADD=9 RD=0,1 UZ=-32,-32
| 17 J=25,81 NLP=SP1 ANG=0 | ADD=10 RD=0,1 UZ=-32,-32
| 18 J=27,82 NLP=SP2 ANG=0 | ADD=11 RD=0,1 UZ=-32,-32
| 19 J=29,83 NLP=SP2 ANG=0 | ADD=14 RD=0,1 UZ=-32,-32
| 20 J=30,84 NLP=SP2 ANG=0 | ADD=15 RD=0,1 UZ=-32,-32
| 21 J=31,85 NLP=SP2 ANG=0 | ADD=16 RD=0,1 UZ=-32,-32
| 22 J=32,86 NLP=SP2 ANG=0 | ADD=17 RD=0,1 UZ=-32,-32
| 23 J=33,87 NLP=SP2 ANG=0 | ADD=18 RD=0,1 UZ=-32,-32
| 24 J=35,88 NLP=SP2 ANG=0 | ADD=19 RD=0,1 UZ=-32,-32
| 25 J=37,89 NLP=SP1 ANG=0 | ADD=20 RD=0,1 UZ=-32,-32
ADD=21 RD=0,1 UZ=-32,-32
| LOAD | ADD=22 RD=0,1 UZ=-32,-32
| NAME=SELFWGT SW=1 | ADD=23 RD=0,1 UZ=-32,-32
| NAME=NWDEAD | ADD=26 RD=0,1 UZ=-32,-32
| TYPE=Distributed Span | ADD=27 RD=0,1 UZ=-32,-32
| ADD=42 RD=0,1 UZ=-133,-133 | ADD=28 RD=0,1 UZ=-32,-32
| ADD=43 RD=0,1 UZ=-133,-133 | ADD=29 RD=0,1 UZ=-32,-32
| ADD=44 RD=0,1 UZ=-133,-133 | ADD=30 RD=0,1 UZ=-32,-32
| ADD=45 RD=0,1 UZ=-133,-133 | ADD=31 RD=0,1 UZ=-32,-32
| ADD=46 RD=0,1 UZ=-133,-133 | ADD=32 RD=0,1 UZ=-32,-32
| ADD=47 RD=0,1 UZ=-133,-133 | ADD=33 RD=0,1 UZ=-32,-32
| ADD=48 RD=0,1 UZ=-133,-133 | ADD=34 RD=0,1 UZ=-32,-32
| ADD=49 RD=0,1 UZ=-133,-133 | ADD=35 RD=0,1 UZ=-32,-32
ADD=50 RD=0,1 UZ=-133,-133
| ADD=51 RD=0,1 UZ=-133,-133 | MODE
| ADD=52 RD=0,1 UZ=-133,-133 | TYPE=RITZ N=50
| ADD=53 RD=0,1 UZ=-133,-133 | LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=HORLIVE
LOAD=NWSOFULL
LOAD=INWATER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST7 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
LOAD=INWATER SF=1 AT=1
NAME=HIST8 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
LOAD=INWATER SF=1 AT=1
NAME=HIST9 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=0.5 AT=1
LOAD=NWSOFULL SF=0.5 AT=1
LOAD=INWATER SF=1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
HIST=HIST3 SF=1
HIST=HIST4 SF=1
HIST=HIST5 SF=1
HIST=HIST6 SF=1
NAME=SERVICE TYPE=ENVE
HIST=HIST7 SF=1
HIST=HIST8 SF=1
HIST=HIST9 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | 80 X= 3.072 Y= 0.000 Z= 5.125
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 81 X= 2.513 Y= 0.000 Z= 5.125
82 X= 1.953 Y= 0.000 Z= 5.125
| JOINT | 83 X= 1.394 Y= 0.000 Z= 5.125
| 1 X= 0.275 Y= 0.000 Z= 0.375 | 84 X= 1.220 Y= 0.000 Z= 5.125
| 2 X= 0.550 Y= 0.000 Z= 0.375 | 85 X= 0.834 Y= 0.000 Z= 5.125
| 3 X= 0.834 Y= 0.000 Z= 0.375 | 86 X= 0.550 Y= 0.000 Z= 5.125
| 4 X= 1.220 Y= 0.000 Z= 0.375 | 87 X= 0.275 Y= 0.000 Z= 5.125
| 5 X= 1.394 Y= 0.000 Z= 0.375 | 88 X= 0.275 Y= 0.000 Z= 4.750
| 6 X= 1.953 Y= 0.000 Z= 0.375 | 89 X= 0.275 Y= 0.000 Z= 4.597
| 7 X= 2.513 Y= 0.000 Z= 0.375 | 90 X= 0.275 Y= 0.000 Z= 4.280
| 8 X= 3.072 Y= 0.000 Z= 0.375 | 91 X= 0.275 Y= 0.000 Z= 4.069
| 9 X= 3.631 Y= 0.000 Z= 0.375 | 92 X= 0.275 Y= 0.000 Z= 3.542
| 10 X= 3.880 Y= 0.000 Z= 0.375 | 93 X= 0.275 Y= 0.000 Z= 3.014
| 11 X= 4.191 Y= 0.000 Z= 0.375 | 94 X= 0.275 Y= 0.000 Z= 2.750
| 12 X= 4.550 Y= 0.000 Z= 0.375 | 95 X= 0.275 Y= 0.000 Z= 2.486
| 13 X= 4.750 Y= 0.000 Z= 0.375 | 96 X= 0.275 Y= 0.000 Z= 1.958
| 14 X= 4.950 Y= 0.000 Z= 0.375 | 97 X= 0.275 Y= 0.000 Z= 1.431
| 15 X= 5.300 Y= 0.000 Z= 0.375 | 98 X= 0.275 Y= 0.000 Z= 1.220
| 16 X= 5.620 Y= 0.000 Z= 0.375 | 99 X= 0.275 Y= 0.000 Z= 0.903
| 17 X= 5.850 Y= 0.000 Z= 0.375 | 100 X= 0.275 Y= 0.000 Z= 0.750
| 18 X= 6.400 Y= 0.000 Z= 0.375 | 101 X= 0.275 Y= 0.000 Z= -0.125
| 19 X= 6.950 Y= 0.000 Z= 0.375 | 102 X= 0.834 Y= 0.000 Z= -0.125
| 20 X= 7.500 Y= 0.000 Z= 0.375 | 103 X= 1.394 Y= 0.000 Z= -0.125
| 21 X= 8.050 Y= 0.000 Z= 0.375 | 104 X= 1.953 Y= 0.000 Z= -0.125
| 22 X= 8.280 Y= 0.000 Z= 0.375 | 105 X= 2.513 Y= 0.000 Z= -0.125
| 23 X= 8.600 Y= 0.000 Z= 0.375 | 106 X= 3.072 Y= 0.000 Z= -0.125
| 24 X= 8.950 Y= 0.000 Z= 0.375 | 107 X= 3.631 Y= 0.000 Z= -0.125
| 25 X= 9.150 Y= 0.000 Z= 0.375 | 108 X= 4.191 Y= 0.000 Z= -0.125
| 26 X= 9.350 Y= 0.000 Z= 0.375 | 109 X= 4.750 Y= 0.000 Z= -0.125
| 27 X= 9.709 Y= 0.000 Z= 0.375 | 110 X= 5.300 Y= 0.000 Z= -0.125
| 28 X= 10.020 Y= 0.000 Z= 0.375 | 111 X= 5.850 Y= 0.000 Z= -0.125
| 29 X= 10.269 Y= 0.000 Z= 0.375 | 112 X= 6.400 Y= 0.000 Z= -0.125
| 30 X= 10.828 Y= 0.000 Z= 0.375 | 113 X= 6.950 Y= 0.000 Z= -0.125
| 31 X= 11.388 Y= 0.000 Z= 0.375 | 114 X= 7.500 Y= 0.000 Z= -0.125
| 32 X= 11.947 Y= 0.000 Z= 0.375 | 115 X= 8.050 Y= 0.000 Z= -0.125
| 33 X= 12.506 Y= 0.000 Z= 0.375 | 116 X= 8.600 Y= 0.000 Z= -0.125
| 34 X= 12.680 Y= 0.000 Z= 0.375 | 117 X= 9.150 Y= 0.000 Z= -0.125
| 35 X= 13.066 Y= 0.000 Z= 0.375 | 118 X= 9.709 Y= 0.000 Z= -0.125
| 36 X= 13.350 Y= 0.000 Z= 0.375 | 119 X= 10.269 Y= 0.000 Z= -0.125
| 37 X= 13.625 Y= 0.000 Z= 0.375 | 120 X= 10.828 Y= 0.000 Z= -0.125
| 38 X= 13.625 Y= 0.000 Z= 0.750 | 121 X= 11.388 Y= 0.000 Z= -0.125
| 39 X= 13.625 Y= 0.000 Z= 0.903 | 122 X= 11.947 Y= 0.000 Z= -0.125
| 40 X= 13.625 Y= 0.000 Z= 1.220 | 123 X= 12.506 Y= 0.000 Z= -0.125
| 41 X= 13.625 Y= 0.000 Z= 1.431 | 124 X= 13.066 Y= 0.000 Z= -0.125
| 42 X= 13.625 Y= 0.000 Z= 1.958 | 125 X= 13.625 Y= 0.000 Z= -0.125
| 43 X= 13.625 Y= 0.000 Z= 2.486 | 126 X= 14.125 Y= 0.000 Z= 0.375
| 44 X= 13.625 Y= 0.000 Z= 2.750 | 127 X= 14.125 Y= 0.000 Z= 0.903
| 45 X= 13.625 Y= 0.000 Z= 3.014 | 128 X= 14.125 Y= 0.000 Z= 1.431
| 46 X= 13.625 Y= 0.000 Z= 3.542 | 129 X= 14.125 Y= 0.000 Z= 1.958
| 47 X= 13.625 Y= 0.000 Z= 4.069 | 130 X= 14.125 Y= 0.000 Z= 2.486
| 48 X= 13.625 Y= 0.000 Z= 4.280 | 131 X= 14.125 Y= 0.000 Z= 3.014
| 49 X= 13.625 Y= 0.000 Z= 4.597 | 132 X= 14.125 Y= 0.000 Z= 3.542
| 50 X= 13.625 Y= 0.000 Z= 4.750 | 133 X= 14.125 Y= 0.000 Z= 4.069
| 51 X= 13.625 Y= 0.000 Z= 5.125 | 134 X= 14.125 Y= 0.000 Z= 4.597
| 52 X= 13.350 Y= 0.000 Z= 5.125 | 135 X= 14.125 Y= 0.000 Z= 5.125
| 53 X= 13.066 Y= 0.000 Z= 5.125 | 136 X= 13.625 Y= 0.000 Z= 5.625
| 54 X= 12.680 Y= 0.000 Z= 5.125 | 137 X= 13.066 Y= 0.000 Z= 5.625
| 55 X= 12.506 Y= 0.000 Z= 5.125 | 138 X= 12.506 Y= 0.000 Z= 5.625
| 56 X= 11.947 Y= 0.000 Z= 5.125 | 139 X= 11.947 Y= 0.000 Z= 5.625
| 57 X= 11.387 Y= 0.000 Z= 5.125 | 140 X= 11.387 Y= 0.000 Z= 5.625
| 58 X= 10.828 Y= 0.000 Z= 5.125 | 141 X= 10.828 Y= 0.000 Z= 5.625
| 59 X= 10.269 Y= 0.000 Z= 5.125 | 142 X= 10.269 Y= 0.000 Z= 5.625
| 60 X= 10.020 Y= 0.000 Z= 5.125 | 143 X= 9.709 Y= 0.000 Z= 5.625
| 61 X= 9.709 Y= 0.000 Z= 5.125 | 144 X= 9.150 Y= 0.000 Z= 5.625
| 62 X= 9.350 Y= 0.000 Z= 5.125 | 145 X= 8.600 Y= 0.000 Z= 5.625
| 63 X= 9.150 Y= 0.000 Z= 5.125 | 146 X= 8.050 Y= 0.000 Z= 5.625
| 64 X= 8.950 Y= 0.000 Z= 5.125 | 147 X= 7.500 Y= 0.000 Z= 5.625
| 65 X= 8.600 Y= 0.000 Z= 5.125 | 148 X= 6.950 Y= 0.000 Z= 5.625
| 66 X= 8.280 Y= 0.000 Z= 5.125 | 149 X= 6.400 Y= 0.000 Z= 5.625
| 67 X= 8.050 Y= 0.000 Z= 5.125 | 150 X= 5.850 Y= 0.000 Z= 5.625
| 68 X= 7.500 Y= 0.000 Z= 5.125 | 151 X= 5.300 Y= 0.000 Z= 5.625
| 69 X= 6.950 Y= 0.000 Z= 5.125 | 152 X= 4.750 Y= 0.000 Z= 5.625
| 70 X= 6.400 Y= 0.000 Z= 5.125 | 153 X= 4.191 Y= 0.000 Z= 5.625
| 71 X= 5.850 Y= 0.000 Z= 5.125 | 154 X= 3.631 Y= 0.000 Z= 5.625
| 72 X= 5.620 Y= 0.000 Z= 5.125 | 155 X= 3.072 Y= 0.000 Z= 5.625
| 73 X= 5.300 Y= 0.000 Z= 5.125 | 156 X= 2.513 Y= 0.000 Z= 5.625
| 74 X= 4.950 Y= 0.000 Z= 5.125 | 157 X= 1.953 Y= 0.000 Z= 5.625
| 75 X= 4.750 Y= 0.000 Z= 5.125 | 158 X= 1.394 Y= 0.000 Z= 5.625
| 76 X= 4.550 Y= 0.000 Z= 5.125 | 159 X= 0.834 Y= 0.000 Z= 5.625
| 77 X= 4.191 Y= 0.000 Z= 5.125 | 160 X= 0.275 Y= 0.000 Z= 5.625
| 78 X= 3.880 Y= 0.000 Z= 5.125 | 161 X= -0.225 Y= 0.000 Z= 5.125
| 79 X= 3.631 Y= 0.000 Z= 5.125 | 162 X= -0.225 Y= 0.000 Z= 4.597
| 163 X= -0.225 Y= 0.000 Z= 4.069 | ADD=7 U1=3695.42
| 164 X= -0.225 Y= 0.000 Z= 3.542 | ADD=8 U1=3695.42
| 165 X= -0.225 Y= 0.000 Z= 3.014 | ADD=9 U1=3695.42
| 166 X= -0.225 Y= 0.000 Z= 2.486 | ADD=11 U1=3695.42
| 167 X= -0.225 Y= 0.000 Z= 1.958 | ADD=13 U1=3665.67
| 168 X= -0.225 Y= 0.000 Z= 1.431 | ADD=15 U1=3635.92
| 169 X= -0.225 Y= 0.000 Z= 0.903 | ADD=17 U1=3635.92
| 170 X= -0.225 Y= 0.000 Z= 0.375 | ADD=18 U1=3635.92
ADD=19 U1=3635.92
| RESTRAINT | ADD=20 U1=3635.92
| ADD=101 DOF=U1, U2, U3, R1, R2, R3 | ADD=21 U1=3635.92
| ADD=102 DOF=U1, U2, U3, R1, R2, R3 | ADD=23 U1=3635.92
| ADD=103 DOF=U1, U2, U3, R1, R2, R3 | ADD=25 U1=3665.67
| ADD=104 DOF=U1, U2, U3, R1, R2, R3 | ADD=27 U1=3695.42
| ADD=105 DOF=U1, U2, U3, R1, R2, R3 | ADD=29 U1=3695.42
| ADD=106 DOF=U1, U2, U3, R1, R2, R3 | ADD=30 U1=3695.42
| ADD=107 DOF=U1, U2, U3, R1, R2, R3 | ADD=31 U1=3695.42
| ADD=108 DOF=U1, U2, U3, R1, R2, R3 | ADD=32 U1=3695.42
| ADD=109 DOF=U1, U2, U3, R1, R2, R3 | ADD=33 U1=3695.42
| ADD=110 DOF=U1, U2, U3, R1, R2, R3 | ADD=35 U1=3695.42
| ADD=111 DOF=U1, U2, U3, R1, R2, R3 | ADD=37 U1=3665.67 U3=8467.23
| ADD=112 DOF=U1, U2, U3, R1, R2, R3 | ADD=39 U3=6996.4
| ADD=113 DOF=U1, U2, U3, R1, R2, R3 | ADD=41 U3=6996.4
| ADD=114 DOF=U1, U2, U3, R1, R2, R3 | ADD=42 U3=6996.4
| ADD=115 DOF=U1, U2, U3, R1, R2, R3 | ADD=43 U3=6996.4
| ADD=116 DOF=U1, U2, U3, R1, R2, R3 | ADD=45 U3=6996.4
| ADD=117 DOF=U1, U2, U3, R1, R2, R3 | ADD=46 U3=6996.4
| ADD=118 DOF=U1, U2, U3, R1, R2, R3 | ADD=47 U3=6996.4
| ADD=119 DOF=U1, U2, U3, R1, R2, R3 | ADD=49 U3=6996.4
| ADD=120 DOF=U1, U2, U3, R1, R2, R3 | ADD=51 U1=3665.67 U3=8467.23
| ADD=121 DOF=U1, U2, U3, R1, R2, R3 | ADD=53 U1=3695.42
| ADD=122 DOF=U1, U2, U3, R1, R2, R3 | ADD=55 U1=3695.42
| ADD=123 DOF=U1, U2, U3, R1, R2, R3 | ADD=56 U1=3695.42
| ADD=124 DOF=U1, U2, U3, R1, R2, R3 | ADD=57 U1=3695.42
| ADD=125 DOF=U1, U2, U3, R1, R2, R3 | ADD=58 U1=3695.42
| ADD=126 DOF=U1, U2, U3, R1, R2, R3 | ADD=59 U1=3695.42
| ADD=127 DOF=U1, U2, U3, R1, R2, R3 | ADD=61 U1=3695.42
| ADD=128 DOF=U1, U2, U3, R1, R2, R3 | ADD=63 U1=3665.67
| ADD=129 DOF=U1, U2, U3, R1, R2, R3 | ADD=65 U1=3635.92
| ADD=130 DOF=U1, U2, U3, R1, R2, R3 | ADD=67 U1=3635.92
| ADD=131 DOF=U1, U2, U3, R1, R2, R3 | ADD=68 U1=3635.92
| ADD=132 DOF=U1, U2, U3, R1, R2, R3 | ADD=69 U1=3635.92
| ADD=133 DOF=U1, U2, U3, R1, R2, R3 | ADD=70 U1=3635.92
| ADD=134 DOF=U1, U2, U3, R1, R2, R3 | ADD=71 U1=3635.92
| ADD=135 DOF=U1, U2, U3, R1, R2, R3 | ADD=73 U1=3635.92
| ADD=136 DOF=U1, U2, U3, R1, R2, R3 | ADD=75 U1=3665.67
| ADD=137 DOF=U1, U2, U3, R1, R2, R3 | ADD=77 U1=3695.42
| ADD=138 DOF=U1, U2, U3, R1, R2, R3 | ADD=79 U1=3695.42
| ADD=139 DOF=U1, U2, U3, R1, R2, R3 | ADD=80 U1=3695.42
| ADD=140 DOF=U1, U2, U3, R1, R2, R3 | ADD=81 U1=3695.42
| ADD=141 DOF=U1, U2, U3, R1, R2, R3 | ADD=82 U1=3695.42
| ADD=142 DOF=U1, U2, U3, R1, R2, R3 | ADD=83 U1=3695.42
| ADD=143 DOF=U1, U2, U3, R1, R2, R3 | ADD=85 U1=3695.42
| ADD=144 DOF=U1, U2, U3, R1, R2, R3 | ADD=87 U1=3665.67 U3=8467.23
| ADD=145 DOF=U1, U2, U3, R1, R2, R3 | ADD=89 U3=6996.4
| ADD=146 DOF=U1, U2, U3, R1, R2, R3 | ADD=91 U3=6996.4
| ADD=147 DOF=U1, U2, U3, R1, R2, R3 | ADD=92 U3=6996.4
| ADD=148 DOF=U1, U2, U3, R1, R2, R3 | ADD=93 U3=6996.4
| ADD=149 DOF=U1, U2, U3, R1, R2, R3 | ADD=95 U3=6996.4
| ADD=150 DOF=U1, U2, U3, R1, R2, R3 | ADD=96 U3=6996.4
| ADD=151 DOF=U1, U2, U3, R1, R2, R3 | ADD=97 U3=6996.4
| ADD=152 DOF=U1, U2, U3, R1, R2, R3 | ADD=99 U3=6996.4
ADD=153 DOF=U1, U2, U3, R1, R2, R3
| ADD=154 DOF=U1, U2, U3, R1, R2, R3 | MATERIAL
| ADD=155 DOF=U1, U2, U3, R1, R2, R3 | NAME=CONC IDES=C M=0.0001 W=24.5
| ADD=156 DOF=U1, U2, U3, R1, R2, R3 | T=0 E=2.7e+007 U=0.17 A=9.99e-006
ADD=157 DOF=U1, U2, U3, R1, R2, R3
| ADD=158 DOF=U1, U2, U3, R1, R2, R3 | NLPROP
| ADD=159 DOF=U1, U2, U3, R1, R2, R3 | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| ADD=160 DOF=U1, U2, U3, R1, R2, R3 | DOF=U1 KE=10997 CE=0.99999 K=10997 OPEN=0
| ADD=161 DOF=U1, U2, U3, R1, R2, R3 | NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| ADD=162 DOF=U1, U2, U3, R1, R2, R3 | DOF=U1 KE=11086.2 CE=0.99999 K=11086.2 OPEN=0
| ADD=163 DOF=U1, U2, U3, R1, R2, R3 | NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| ADD=164 DOF=U1, U2, U3, R1, R2, R3 | DOF=U1 KE=10907.7 CE=0.99999 K=10907.7 OPEN=0
| ADD=165 DOF=U1, U2, U3, R1, R2, R3 | NAME=SP4 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| ADD=166 DOF=U1, U2, U3, R1, R2, R3 | DOF=U1 KE=25401.7 CE=0.99999 K=25401.7 OPEN=0
| ADD=167 DOF=U1, U2, U3, R1, R2, R3 | NAME=SP5 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| ADD=168 DOF=U1, U2, U3, R1, R2, R3 | DOF=U1 KE=20989.2 CE=0.99999 K=20989.2 OPEN=0
ADD=169 DOF=U1, U2, U3, R1, R2, R3
| ADD=170 DOF=U1, U2, U3, R1, R2, R3 | FRAME SECTION
NAME=1 MAT=CONC SH=R T=0.75, 1
| SPRING | NAME=2 MAT=CONC SH=R T=0.55, 1
| ADD=1 U1=3665.67 U3=8467.23 | NAME=3 MAT=CONC SH=R T=0.4, 1
ADD=3 U1=3695.42
| ADD=5 U1=3695.42 | FRAME
| ADD=6 U1=3695.42 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | 88 J= 88, 89 SEC=2 NSEG=1 ANG=180
| 3 J= 3, 4 SEC=1 NSEG=1 ANG=180 | 89 J= 89, 90 SEC=2 NSEG=1 ANG=180
| 4 J= 4, 5 SEC=1 NSEG=1 ANG=180 | 90 J= 90, 91 SEC=2 NSEG=1 ANG=180
| 5 J= 5, 6 SEC=1 NSEG=2 ANG=180 | 91 J= 91, 92 SEC=2 NSEG=2 ANG=180
| 6 J= 6, 7 SEC=1 NSEG=2 ANG=180 | 92 J= 92, 93 SEC=2 NSEG=2 ANG=180
| 7 J= 7, 8 SEC=1 NSEG=2 ANG=180 | 93 J= 93, 94 SEC=2 NSEG=1 ANG=180
| 8 J= 8, 9 SEC=1 NSEG=2 ANG=180 | 94 J= 94, 95 SEC=2 NSEG=1 ANG=180
| 9 J= 9, 10 SEC=1 NSEG=1 ANG=180 | 95 J= 95, 96 SEC=2 NSEG=2 ANG=180
| 10 J= 10, 11 SEC=1 NSEG=1 ANG=180 | 96 J= 96, 97 SEC=2 NSEG=2 ANG=180
| 11 J= 11, 12 SEC=1 NSEG=1 ANG=180 | 97 J= 97, 98 SEC=2 NSEG=1 ANG=180
| 12 J= 12, 13 SEC=1 NSEG=1 ANG=180 | 98 J= 98, 99 SEC=2 NSEG=1 ANG=180
| 13 J= 13, 14 SEC=1 NSEG=1 ANG=180 | 99 J= 99, 100 SEC=2 NSEG=1 ANG=180
| 14 J= 14, 15 SEC=1 NSEG=1 ANG=180 | 100 J=100, 1 SEC=2 NSEG=1 ANG=180
| 15 J= 15, 16 SEC=1 NSEG=1 ANG=180 | 101 J= 75, 13 SEC=3 NSEG=4 ANG=0
| 16 J= 16, 17 SEC=1 NSEG=1 ANG=180 | 102 J= 63, 25 SEC=3 NSEG=4 ANG=0
17 J= 17, 18 SEC=1 NSEG=2 ANG=180
| 18 J= 18, 19 SEC=1 NSEG=2 ANG=180 | NLLINK
| 19 J= 19, 20 SEC=1 NSEG=2 ANG=180 | 1 J=1,101 NLP=SP1 ANG=0
| 20 J= 20, 21 SEC=1 NSEG=2 ANG=180 | 2 J=3,102 NLP=SP2 ANG=0
| 21 J= 21, 22 SEC=1 NSEG=1 ANG=180 | 3 J=5,103 NLP=SP2 ANG=0
| 22 J= 22, 23 SEC=1 NSEG=1 ANG=180 | 4 J=6,104 NLP=SP2 ANG=0
| 23 J= 23, 24 SEC=1 NSEG=1 ANG=180 | 5 J=7,105 NLP=SP2 ANG=0
| 24 J= 24, 25 SEC=1 NSEG=1 ANG=180 | 6 J=8,106 NLP=SP2 ANG=0
| 25 J= 25, 26 SEC=1 NSEG=1 ANG=180 | 7 J=9,107 NLP=SP2 ANG=0
| 26 J= 26, 27 SEC=1 NSEG=1 ANG=180 | 8 J=11,108 NLP=SP2 ANG=0
| 27 J= 27, 28 SEC=1 NSEG=1 ANG=180 | 9 J=13,109 NLP=SP1 ANG=0
| 28 J= 28, 29 SEC=1 NSEG=1 ANG=180 | 10 J=15,110 NLP=SP3 ANG=0
| 29 J= 29, 30 SEC=1 NSEG=2 ANG=180 | 11 J=17,111 NLP=SP3 ANG=0
| 30 J= 30, 31 SEC=1 NSEG=2 ANG=180 | 12 J=18,112 NLP=SP3 ANG=0
| 31 J= 31, 32 SEC=1 NSEG=2 ANG=180 | 13 J=19,113 NLP=SP3 ANG=0
| 32 J= 32, 33 SEC=1 NSEG=2 ANG=180 | 14 J=20,114 NLP=SP3 ANG=0
| 33 J= 33, 34 SEC=1 NSEG=1 ANG=180 | 15 J=21,115 NLP=SP3 ANG=0
| 34 J= 34, 35 SEC=1 NSEG=1 ANG=180 | 16 J=23,116 NLP=SP3 ANG=0
| 35 J= 35, 36 SEC=1 NSEG=1 ANG=180 | 17 J=25,117 NLP=SP1 ANG=0
| 36 J= 36, 37 SEC=1 NSEG=1 ANG=180 | 18 J=27,118 NLP=SP2 ANG=0
| 37 J= 37, 38 SEC=2 NSEG=1 ANG=0 | 19 J=29,119 NLP=SP2 ANG=0
| 38 J= 38, 39 SEC=2 NSEG=1 ANG=0 | 20 J=30,120 NLP=SP2 ANG=0
| 39 J= 39, 40 SEC=2 NSEG=1 ANG=0 | 21 J=31,121 NLP=SP2 ANG=0
| 40 J= 40, 41 SEC=2 NSEG=1 ANG=0 | 22 J=32,122 NLP=SP2 ANG=0
| 41 J= 41, 42 SEC=2 NSEG=2 ANG=0 | 23 J=33,123 NLP=SP2 ANG=0
| 42 J= 42, 43 SEC=2 NSEG=2 ANG=0 | 24 J=35,124 NLP=SP2 ANG=0
| 43 J= 43, 44 SEC=2 NSEG=1 ANG=0 | 25 J=37,125 NLP=SP1 ANG=0
| 44 J= 44, 45 SEC=2 NSEG=1 ANG=0 | 26 J=37,126 NLP=SP4 ANG=180
| 45 J= 45, 46 SEC=2 NSEG=2 ANG=0 | 27 J=39,127 NLP=SP5 ANG=180
| 46 J= 46, 47 SEC=2 NSEG=2 ANG=0 | 28 J=41,128 NLP=SP5 ANG=180
| 47 J= 47, 48 SEC=2 NSEG=1 ANG=0 | 29 J=42,129 NLP=SP5 ANG=180
| 48 J= 48, 49 SEC=2 NSEG=1 ANG=0 | 30 J=43,130 NLP=SP5 ANG=180
| 49 J= 49, 50 SEC=2 NSEG=1 ANG=0 | 31 J=45,131 NLP=SP5 ANG=180
| 50 J= 50, 51 SEC=2 NSEG=1 ANG=0 | 32 J=46,132 NLP=SP5 ANG=180
| 51 J= 51, 52 SEC=1 NSEG=1 ANG=0 | 33 J=47,133 NLP=SP5 ANG=180
| 52 J= 52, 53 SEC=1 NSEG=1 ANG=0 | 34 J=49,134 NLP=SP5 ANG=180
| 53 J= 53, 54 SEC=1 NSEG=1 ANG=0 | 35 J=51,135 NLP=SP4 ANG=180
| 54 J= 54, 55 SEC=1 NSEG=1 ANG=0 | 36 J=51,136 NLP=SP1 ANG=0
| 55 J= 55, 56 SEC=1 NSEG=2 ANG=0 | 37 J=53,137 NLP=SP2 ANG=0
| 56 J= 56, 57 SEC=1 NSEG=2 ANG=0 | 38 J=55,138 NLP=SP2 ANG=0
| 57 J= 57, 58 SEC=1 NSEG=2 ANG=0 | 39 J=56,139 NLP=SP2 ANG=0
| 58 J= 58, 59 SEC=1 NSEG=2 ANG=0 | 40 J=57,140 NLP=SP2 ANG=0
| 59 J= 59, 60 SEC=1 NSEG=1 ANG=0 | 41 J=58,141 NLP=SP2 ANG=0
| 60 J= 60, 61 SEC=1 NSEG=1 ANG=0 | 42 J=59,142 NLP=SP2 ANG=0
| 61 J= 61, 62 SEC=1 NSEG=1 ANG=0 | 43 J=61,143 NLP=SP2 ANG=0
| 62 J= 62, 63 SEC=1 NSEG=1 ANG=0 | 44 J=63,144 NLP=SP1 ANG=0
| 63 J= 63, 64 SEC=1 NSEG=1 ANG=0 | 45 J=65,145 NLP=SP3 ANG=0
| 64 J= 64, 65 SEC=1 NSEG=1 ANG=0 | 46 J=67,146 NLP=SP3 ANG=0
| 65 J= 65, 66 SEC=1 NSEG=1 ANG=0 | 47 J=68,147 NLP=SP3 ANG=0
| 66 J= 66, 67 SEC=1 NSEG=1 ANG=0 | 48 J=69,148 NLP=SP3 ANG=0
| 67 J= 67, 68 SEC=1 NSEG=2 ANG=0 | 49 J=70,149 NLP=SP3 ANG=0
| 68 J= 68, 69 SEC=1 NSEG=2 ANG=0 | 50 J=71,150 NLP=SP3 ANG=0
| 69 J= 69, 70 SEC=1 NSEG=2 ANG=0 | 51 J=73,151 NLP=SP3 ANG=0
| 70 J= 70, 71 SEC=1 NSEG=2 ANG=0 | 52 J=75,152 NLP=SP1 ANG=0
| 71 J= 71, 72 SEC=1 NSEG=1 ANG=0 | 53 J=77,153 NLP=SP2 ANG=0
| 72 J= 72, 73 SEC=1 NSEG=1 ANG=0 | 54 J=79,154 NLP=SP2 ANG=0
| 73 J= 73, 74 SEC=1 NSEG=1 ANG=0 | 55 J=80,155 NLP=SP2 ANG=0
| 74 J= 74, 75 SEC=1 NSEG=1 ANG=0 | 56 J=81,156 NLP=SP2 ANG=0
| 75 J= 75, 76 SEC=1 NSEG=1 ANG=0 | 57 J=82,157 NLP=SP2 ANG=0
| 76 J= 76, 77 SEC=1 NSEG=1 ANG=0 | 58 J=83,158 NLP=SP2 ANG=0
| 77 J= 77, 78 SEC=1 NSEG=1 ANG=0 | 59 J=85,159 NLP=SP2 ANG=0
| 78 J= 78, 79 SEC=1 NSEG=1 ANG=0 | 60 J=87,160 NLP=SP1 ANG=0
| 79 J= 79, 80 SEC=1 NSEG=2 ANG=0 | 61 J=87,161 NLP=SP4 ANG=180
| 80 J= 80, 81 SEC=1 NSEG=2 ANG=0 | 62 J=89,162 NLP=SP5 ANG=180
| 81 J= 81, 82 SEC=1 NSEG=2 ANG=0 | 63 J=91,163 NLP=SP5 ANG=180
| 82 J= 82, 83 SEC=1 NSEG=2 ANG=0 | 64 J=92,164 NLP=SP5 ANG=180
| 83 J= 83, 84 SEC=1 NSEG=1 ANG=0 | 65 J=93,165 NLP=SP5 ANG=180
| 84 J= 84, 85 SEC=1 NSEG=1 ANG=0 | 66 J=95,166 NLP=SP5 ANG=180
| 85 J= 85, 86 SEC=1 NSEG=1 ANG=0 | 67 J=96,167 NLP=SP5 ANG=180
| 86 J= 86, 87 SEC=1 NSEG=1 ANG=0 | 68 J=97,168 NLP=SP5 ANG=180
| 87 J= 87, 88 SEC=2 NSEG=1 ANG=180 | 69 J=99,169 NLP=SP5 ANG=180
| 70 J=1,170 NLP=SP4 ANG=180 | ADD=55 RD=0,1 UX=6.0026,6.0026
ADD=56 RD=0,1 UX=6.0026,6.0026
| LOAD | ADD=57 RD=0,1 UX=6.0026,6.0026
| NAME=SELFWGT SW=1 | ADD=58 RD=0,1 UX=6.0026,6.0026
| NAME=NWDEAD | ADD=59 RD=0,1 UX=6.0026,6.0026
| TYPE=Distributed Span | ADD=60 RD=0,1 UX=6.0026,6.0026
| ADD=51 RD=0,1 UZ=-133,-133 | ADD=61 RD=0,1 UX=6.0026,6.0026
| ADD=52 RD=0,1 UZ=-133,-133 | ADD=62 RD=0,1 UX=6.0026,6.0026
| ADD=53 RD=0,1 UZ=-133,-133 | ADD=63 RD=0,1 UX=6.0026,6.0026
| ADD=54 RD=0,1 UZ=-133,-133 | ADD=64 RD=0,1 UX=6.0026,6.0026
| ADD=55 RD=0,1 UZ=-133,-133 | ADD=65 RD=0,1 UX=6.0026,6.0026
| ADD=56 RD=0,1 UZ=-133,-133 | ADD=66 RD=0,1 UX=6.0026,6.0026
| ADD=57 RD=0,1 UZ=-133,-133 | ADD=67 RD=0,1 UX=6.0026,6.0026
| ADD=58 RD=0,1 UZ=-133,-133 | ADD=68 RD=0,1 UX=6.0026,6.0026
| ADD=59 RD=0,1 UZ=-133,-133 | ADD=69 RD=0,1 UX=6.0026,6.0026
| ADD=60 RD=0,1 UZ=-133,-133 | ADD=70 RD=0,1 UX=6.0026,6.0026
| ADD=61 RD=0,1 UZ=-133,-133 | ADD=71 RD=0,1 UX=6.0026,6.0026
| ADD=62 RD=0,1 UZ=-133,-133 | ADD=72 RD=0,1 UX=6.0026,6.0026
| ADD=63 RD=0,1 UZ=-133,-133 | ADD=73 RD=0,1 UX=6.0026,6.0026
| ADD=64 RD=0,1 UZ=-133,-133 | ADD=74 RD=0,1 UX=6.0026,6.0026
| ADD=65 RD=0,1 UZ=-133,-133 | ADD=75 RD=0,1 UX=6.0026,6.0026
| ADD=66 RD=0,1 UZ=-133,-133 | ADD=76 RD=0,1 UX=6.0026,6.0026
| ADD=67 RD=0,1 UZ=-133,-133 | ADD=77 RD=0,1 UX=6.0026,6.0026
| ADD=68 RD=0,1 UZ=-133,-133 | ADD=78 RD=0,1 UX=6.0026,6.0026
| ADD=69 RD=0,1 UZ=-133,-133 | ADD=79 RD=0,1 UX=6.0026,6.0026
| ADD=70 RD=0,1 UZ=-133,-133 | ADD=80 RD=0,1 UX=6.0026,6.0026
| ADD=71 RD=0,1 UZ=-133,-133 | ADD=81 RD=0,1 UX=6.0026,6.0026
| ADD=72 RD=0,1 UZ=-133,-133 | ADD=82 RD=0,1 UX=6.0026,6.0026
| ADD=73 RD=0,1 UZ=-133,-133 | ADD=83 RD=0,1 UX=6.0026,6.0026
| ADD=74 RD=0,1 UZ=-133,-133 | ADD=84 RD=0,1 UX=6.0026,6.0026
| ADD=75 RD=0,1 UZ=-133,-133 | ADD=85 RD=0,1 UX=6.0026,6.0026
| ADD=76 RD=0,1 UZ=-133,-133 | ADD=86 RD=0,1 UX=6.0026,6.0026
| ADD=77 RD=0,1 UZ=-133,-133 | NAME=SEWALL
| ADD=78 RD=0,1 UZ=-133,-133 | TYPE=Distributed Span
| ADD=79 RD=0,1 UZ=-133,-133 | ADD=37 RD=0,1 UX=0,3.4187
| ADD=80 RD=0,1 UZ=-133,-133 | ADD=38 RD=0,1 UX=3.4187,4.7703
| ADD=81 RD=0,1 UZ=-133,-133 | ADD=39 RD=0,1 UX=4.7703,7.5927
| ADD=82 RD=0,1 UZ=-133,-133 | ADD=40 RD=0,1 UX=7.5927,9.3815
| ADD=83 RD=0,1 UZ=-133,-133 | ADD=41 RD=0,1 UX=9.3815,13.794
| ADD=84 RD=0,1 UZ=-133,-133 | ADD=42 RD=0,1 UX=13.794,18.0078
| ADD=85 RD=0,1 UZ=-133,-133 | ADD=43 RD=0,1 UX=18.0078,20.0351
| ADD=86 RD=0,1 UZ=-133,-133 | ADD=44 RD=0,1 UX=20.0351,22.0227
| NAME=LIVEFULL | ADD=45 RD=0,1 UX=22.0227,25.839
| TYPE=Distributed Span | ADD=46 RD=0,1 UX=25.839,29.4564
| ADD=51 RD=0,1 UZ=-10,-10 | ADD=47 RD=0,1 UX=29.4564,30.8477
| ADD=52 RD=0,1 UZ=-10,-10 | ADD=48 RD=0,1 UX=30.8477,32.8751
| ADD=53 RD=0,1 UZ=-10,-10 | ADD=49 RD=0,1 UX=32.8751,33.8292
| ADD=54 RD=0,1 UZ=-10,-10 | ADD=50 RD=0,1 UX=33.8292,36.095
| ADD=55 RD=0,1 UZ=-10,-10 | ADD=87 RD=0,1 UX=36.095,33.8292
| ADD=56 RD=0,1 UZ=-10,-10 | ADD=88 RD=0,1 UX=33.8292,32.8751
| ADD=57 RD=0,1 UZ=-10,-10 | ADD=89 RD=0,1 UX=32.8751,30.8477
| ADD=58 RD=0,1 UZ=-10,-10 | ADD=90 RD=0,1 UX=30.8477,29.4564
| ADD=59 RD=0,1 UZ=-10,-10 | ADD=91 RD=0,1 UX=29.4564,25.839
| ADD=60 RD=0,1 UZ=-10,-10 | ADD=92 RD=0,1 UX=25.839,22.0227
| ADD=61 RD=0,1 UZ=-10,-10 | ADD=93 RD=0,1 UX=22.0227,20.0351
| ADD=62 RD=0,1 UZ=-10,-10 | ADD=94 RD=0,1 UX=20.0351,18.0078
| ADD=63 RD=0,1 UZ=-10,-10 | ADD=95 RD=0,1 UX=18.0078,13.794
| ADD=64 RD=0,1 UZ=-10,-10 | ADD=96 RD=0,1 UX=13.794,9.3815
| ADD=65 RD=0,1 UZ=-10,-10 | ADD=97 RD=0,1 UX=9.3815,7.5927
| ADD=66 RD=0,1 UZ=-10,-10 | ADD=98 RD=0,1 UX=7.5927,4.7703
| ADD=67 RD=0,1 UZ=-10,-10 | ADD=99 RD=0,1 UX=4.7703,3.4187
| ADD=68 RD=0,1 UZ=-10,-10 | ADD=100 RD=0,1 UX=3.4187,0
| ADD=69 RD=0,1 UZ=-10,-10 | NAME=SEPRINSH
| ADD=70 RD=0,1 UZ=-10,-10 | TYPE=Distributed Span
| ADD=71 RD=0,1 UZ=-10,-10 | ADD=1 RD=0,1 UX=-4.4,-4.4
| ADD=72 RD=0,1 UZ=-10,-10 | ADD=2 RD=0,1 UX=-4.4,-4.4
| ADD=73 RD=0,1 UZ=-10,-10 | ADD=3 RD=0,1 UX=-4.4,-4.4
| ADD=74 RD=0,1 UZ=-10,-10 | ADD=4 RD=0,1 UX=-4.4,-4.4
| ADD=75 RD=0,1 UZ=-10,-10 | ADD=5 RD=0,1 UX=-4.4,-4.4
| ADD=76 RD=0,1 UZ=-10,-10 | ADD=6 RD=0,1 UX=-4.4,-4.4
| ADD=77 RD=0,1 UZ=-10,-10 | ADD=7 RD=0,1 UX=-4.4,-4.4
| ADD=78 RD=0,1 UZ=-10,-10 | ADD=8 RD=0,1 UX=-4.4,-4.4
| ADD=79 RD=0,1 UZ=-10,-10 | ADD=9 RD=0,1 UX=-4.4,-4.4
| ADD=80 RD=0,1 UZ=-10,-10 | ADD=10 RD=0,1 UX=-4.4,-4.4
| ADD=81 RD=0,1 UZ=-10,-10 | ADD=11 RD=0,1 UX=-4.4,-4.4
| ADD=82 RD=0,1 UZ=-10,-10 | ADD=12 RD=0,1 UX=-4.4,-4.4
| ADD=83 RD=0,1 UZ=-10,-10 | ADD=13 RD=0,1 UX=-4.4,-4.4
| ADD=84 RD=0,1 UZ=-10,-10 | ADD=14 RD=0,1 UX=-4.4,-4.4
| ADD=85 RD=0,1 UZ=-10,-10 | ADD=15 RD=0,1 UX=-4.4,-4.4
| ADD=86 RD=0,1 UZ=-10,-10 | ADD=16 RD=0,1 UX=-4.4,-4.4
| NAME=SEUPSLAB | ADD=17 RD=0,1 UX=-4.4,-4.4
| TYPE=Distributed Span | ADD=18 RD=0,1 UX=-4.4,-4.4
| ADD=51 RD=0,1 UX=6.0026,6.0026 | ADD=19 RD=0,1 UX=-4.4,-4.4
| ADD=52 RD=0,1 UX=6.0026,6.0026 | ADD=20 RD=0,1 UX=-4.4,-4.4
| ADD=53 RD=0,1 UX=6.0026,6.0026 | ADD=21 RD=0,1 UX=-4.4,-4.4
| ADD=54 RD=0,1 UX=6.0026,6.0026 | ADD=22 RD=0,1 UX=-4.4,-4.4
| ADD=23 RD=0,1 UX=-4.4,-4.4 | ADD=7 RD=0,1 UX=2.40529,2.40529
| ADD=24 RD=0,1 UX=-4.4,-4.4 | ADD=8 RD=0,1 UX=2.40529,2.40529
| ADD=25 RD=0,1 UX=-4.4,-4.4 | ADD=9 RD=0,1 UX=2.40529,2.40529
| ADD=26 RD=0,1 UX=-4.4,-4.4 | ADD=10 RD=0,1 UX=2.40529,2.40529
| ADD=27 RD=0,1 UX=-4.4,-4.4 | ADD=11 RD=0,1 UX=2.40529,2.40529
| ADD=28 RD=0,1 UX=-4.4,-4.4 | ADD=12 RD=0,1 UX=2.40529,2.40529
| ADD=29 RD=0,1 UX=-4.4,-4.4 | ADD=13 RD=0,1 UX=2.40529,2.40529
| ADD=30 RD=0,1 UX=-4.4,-4.4 | ADD=14 RD=0,1 UX=2.40529,2.40529
| ADD=31 RD=0,1 UX=-4.4,-4.4 | ADD=15 RD=0,1 UX=2.40529,2.40529
| ADD=32 RD=0,1 UX=-4.4,-4.4 | ADD=16 RD=0,1 UX=2.40529,2.40529
| ADD=33 RD=0,1 UX=-4.4,-4.4 | ADD=17 RD=0,1 UX=2.40529,2.40529
| ADD=34 RD=0,1 UX=-4.4,-4.4 | ADD=18 RD=0,1 UX=2.40529,2.40529
| ADD=35 RD=0,1 UX=-4.4,-4.4 | ADD=19 RD=0,1 UX=2.40529,2.40529
| ADD=36 RD=0,1 UX=-4.4,-4.4 | ADD=20 RD=0,1 UX=2.40529,2.40529
| ADD=37 RD=0,1 UZ=3.6,3.6 | ADD=21 RD=0,1 UX=2.40529,2.40529
| ADD=38 RD=0,1 UZ=3.6,3.6 | ADD=22 RD=0,1 UX=2.40529,2.40529
| ADD=39 RD=0,1 UZ=3.6,3.6 | ADD=23 RD=0,1 UX=2.40529,2.40529
| ADD=40 RD=0,1 UZ=3.6,3.6 | ADD=24 RD=0,1 UX=2.40529,2.40529
| ADD=41 RD=0,1 UZ=3.6,3.6 | ADD=25 RD=0,1 UX=2.40529,2.40529
| ADD=42 RD=0,1 UZ=3.6,3.6 | ADD=26 RD=0,1 UX=2.40529,2.40529
| ADD=43 RD=0,1 UZ=3.6,3.6 | ADD=27 RD=0,1 UX=2.40529,2.40529
| ADD=44 RD=0,1 UZ=3.6,3.6 | ADD=28 RD=0,1 UX=2.40529,2.40529
| ADD=45 RD=0,1 UZ=3.6,3.6 | ADD=29 RD=0,1 UX=2.40529,2.40529
| ADD=46 RD=0,1 UZ=3.6,3.6 | ADD=30 RD=0,1 UX=2.40529,2.40529
| ADD=47 RD=0,1 UZ=3.6,3.6 | ADD=31 RD=0,1 UX=2.40529,2.40529
| ADD=48 RD=0,1 UZ=3.6,3.6 | ADD=32 RD=0,1 UX=2.40529,2.40529
| ADD=49 RD=0,1 UZ=3.6,3.6 | ADD=33 RD=0,1 UX=2.40529,2.40529
| ADD=50 RD=0,1 UZ=3.6,3.6 | ADD=34 RD=0,1 UX=2.40529,2.40529
| ADD=51 RD=0,1 UX=2.79,2.79 | ADD=35 RD=0,1 UX=2.40529,2.40529
| ADD=52 RD=0,1 UX=2.79,2.79 | ADD=36 RD=0,1 UX=2.40529,2.40529
| ADD=53 RD=0,1 UX=2.79,2.79 | ADD=37 RD=0,1 UX=1.76388,1.77601
| ADD=54 RD=0,1 UX=2.79,2.79 | ADD=38 RD=0,1 UX=1.77601,1.78095
| ADD=55 RD=0,1 UX=2.79,2.79 | ADD=39 RD=0,1 UX=1.78095,1.7912
| ADD=56 RD=0,1 UX=2.79,2.79 | ADD=40 RD=0,1 UX=1.7912,1.79803
| ADD=57 RD=0,1 UX=2.79,2.79 | ADD=41 RD=0,1 UX=1.79803,1.81507
| ADD=58 RD=0,1 UX=2.79,2.79 | ADD=42 RD=0,1 UX=1.81507,1.83215
| ADD=59 RD=0,1 UX=2.79,2.79 | ADD=43 RD=0,1 UX=1.83215,1.84069
| ADD=60 RD=0,1 UX=2.79,2.79 | ADD=44 RD=0,1 UX=1.84069,1.84922
| ADD=61 RD=0,1 UX=2.79,2.79 | ADD=45 RD=0,1 UX=1.84922,1.8663
| ADD=62 RD=0,1 UX=2.79,2.79 | ADD=46 RD=0,1 UX=1.8663,1.88334
| ADD=63 RD=0,1 UX=2.79,2.79 | ADD=47 RD=0,1 UX=1.88334,1.89017
| ADD=64 RD=0,1 UX=2.79,2.79 | ADD=48 RD=0,1 UX=1.89017,1.90042
| ADD=65 RD=0,1 UX=2.79,2.79 | ADD=49 RD=0,1 UX=1.90042,1.90537
| ADD=66 RD=0,1 UX=2.79,2.79 | ADD=50 RD=0,1 UX=1.90537,1.91749
| ADD=67 RD=0,1 UX=2.79,2.79 | ADD=51 RD=0,1 UX=2.61476,2.61476
| ADD=68 RD=0,1 UX=2.79,2.79 | ADD=52 RD=0,1 UX=2.61476,2.61476
| ADD=69 RD=0,1 UX=2.79,2.79 | ADD=53 RD=0,1 UX=2.61476,2.61476
| ADD=70 RD=0,1 UX=2.79,2.79 | ADD=54 RD=0,1 UX=2.61476,2.61476
| ADD=71 RD=0,1 UX=2.79,2.79 | ADD=55 RD=0,1 UX=2.61476,2.61476
| ADD=72 RD=0,1 UX=2.79,2.79 | ADD=56 RD=0,1 UX=2.61476,2.61476
| ADD=73 RD=0,1 UX=2.79,2.79 | ADD=57 RD=0,1 UX=2.61476,2.61476
| ADD=74 RD=0,1 UX=2.79,2.79 | ADD=58 RD=0,1 UX=2.61476,2.61476
| ADD=75 RD=0,1 UX=2.79,2.79 | ADD=59 RD=0,1 UX=2.61476,2.61476
| ADD=76 RD=0,1 UX=2.79,2.79 | ADD=60 RD=0,1 UX=2.61476,2.61476
| ADD=77 RD=0,1 UX=2.79,2.79 | ADD=61 RD=0,1 UX=2.61476,2.61476
| ADD=78 RD=0,1 UX=2.79,2.79 | ADD=62 RD=0,1 UX=2.61476,2.61476
| ADD=79 RD=0,1 UX=2.79,2.79 | ADD=63 RD=0,1 UX=2.61476,2.61476
| ADD=80 RD=0,1 UX=2.79,2.79 | ADD=64 RD=0,1 UX=2.61476,2.61476
| ADD=81 RD=0,1 UX=2.79,2.79 | ADD=65 RD=0,1 UX=2.61476,2.61476
| ADD=82 RD=0,1 UX=2.79,2.79 | ADD=66 RD=0,1 UX=2.61476,2.61476
| ADD=83 RD=0,1 UX=2.79,2.79 | ADD=67 RD=0,1 UX=2.61476,2.61476
| ADD=84 RD=0,1 UX=2.79,2.79 | ADD=68 RD=0,1 UX=2.61476,2.61476
| ADD=85 RD=0,1 UX=2.79,2.79 | ADD=69 RD=0,1 UX=2.61476,2.61476
| ADD=86 RD=0,1 UX=2.79,2.79 | ADD=70 RD=0,1 UX=2.61476,2.61476
| ADD=87 RD=0,1 UZ=-3.6,-3.6 | ADD=71 RD=0,1 UX=2.61476,2.61476
| ADD=88 RD=0,1 UZ=-3.6,-3.6 | ADD=72 RD=0,1 UX=2.61476,2.61476
| ADD=89 RD=0,1 UZ=-3.6,-3.6 | ADD=73 RD=0,1 UX=2.61476,2.61476
| ADD=90 RD=0,1 UZ=-3.6,-3.6 | ADD=74 RD=0,1 UX=2.61476,2.61476
| ADD=91 RD=0,1 UZ=-3.6,-3.6 | ADD=75 RD=0,1 UX=2.61476,2.61476
| ADD=92 RD=0,1 UZ=-3.6,-3.6 | ADD=76 RD=0,1 UX=2.61476,2.61476
| ADD=93 RD=0,1 UZ=-3.6,-3.6 | ADD=77 RD=0,1 UX=2.61476,2.61476
| ADD=94 RD=0,1 UZ=-3.6,-3.6 | ADD=78 RD=0,1 UX=2.61476,2.61476
| ADD=95 RD=0,1 UZ=-3.6,-3.6 | ADD=79 RD=0,1 UX=2.61476,2.61476
| ADD=96 RD=0,1 UZ=-3.6,-3.6 | ADD=80 RD=0,1 UX=2.61476,2.61476
| ADD=97 RD=0,1 UZ=-3.6,-3.6 | ADD=81 RD=0,1 UX=2.61476,2.61476
| ADD=98 RD=0,1 UZ=-3.6,-3.6 | ADD=82 RD=0,1 UX=2.61476,2.61476
| ADD=99 RD=0,1 UZ=-3.6,-3.6 | ADD=83 RD=0,1 UX=2.61476,2.61476
| ADD=100 RD=0,1 UZ=-3.6,-3.6 | ADD=84 RD=0,1 UX=2.61476,2.61476
| NAME=SEINER | ADD=85 RD=0,1 UX=2.61476,2.61476
| TYPE=Distributed Span | ADD=86 RD=0,1 UX=2.61476,2.61476
| ADD=1 RD=0,1 UX=2.40529,2.40529 | ADD=87 RD=0,1 UX=1.91749,1.90537
| ADD=2 RD=0,1 UX=2.40529,2.40529 | ADD=88 RD=0,1 UX=1.90537,1.90042
| ADD=3 RD=0,1 UX=2.40529,2.40529 | ADD=89 RD=0,1 UX=1.90042,1.89017
| ADD=4 RD=0,1 UX=2.40529,2.40529 | ADD=90 RD=0,1 UX=1.89017,1.88334
| ADD=5 RD=0,1 UX=2.40529,2.40529 | ADD=91 RD=0,1 UX=1.88334,1.8663
| ADD=6 RD=0,1 UX=2.40529,2.40529 | ADD=92 RD=0,1 UX=1.8663,1.84922
ADD=93 RD=0,1 UX=1.84922,1.84069
ADD=94 RD=0,1 UX=1.84069,1.83215
ADD=95 RD=0,1 UX=1.83215,1.81507
ADD=96 RD=0,1 UX=1.81507,1.79803
ADD=97 RD=0,1 UX=1.79803,1.7912
ADD=98 RD=0,1 UX=1.7912,1.78095
ADD=99 RD=0,1 UX=1.78095,1.77601
ADD=100 RD=0,1 UX=1.77601,1.76388
ADD=101 RD=0,1 UX=1.39454,1.28282
ADD=102 RD=0,1 UX=1.39454,1.28282
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=SEUPSLAB
LOAD=SEWALL
LOAD=SEPRINSH
LOAD=SEINER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=1 AT=1
LOAD=SEWALL SF=1 AT=1
LOAD=SEPRINSH SF=1 AT=1
LOAD=SEINER SF=1 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=-1 AT=1
LOAD=SEWALL SF=-1 AT=1
LOAD=SEPRINSH SF=-1 AT=1
LOAD=SEINER SF=-1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 18 | ULTIMATE MAX | 0 | 0 | 0 | 139.3034
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 18 | ULTIMATE MAX | 0.5 | 0 | 0 | 156.1184
| 1 | ULTIMATE MIN | 0 | -396.1235 | -429.1425 | -306.6638 | 18 | ULTIMATE MAX | 1 | 0 | 0 | 174.601
| 1 | ULTIMATE MIN | 1 | -396.1235 | -435.2062 | -187.8159 | 18 | ULTIMATE MIN | 0 | -393.9405 | -58.2772 | 0
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 18 | ULTIMATE MIN | 0.5 | -393.9405 | -64.341 | 0
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 38.8712 | 18 | ULTIMATE MIN | 1 | -393.9405 | -70.4047 | 0
| 2 | ULTIMATE MIN | 0 | -396.1235 | -435.2062 | -187.8159 | 19 | ULTIMATE MAX | 0 | 0 | 70.4159 | 174.601
| 2 | ULTIMATE MIN | 1 | -396.1235 | -441.4684 | -75.0873 | 19 | ULTIMATE MAX | 0.5 | 0 | 64.3522 | 156.1153
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 38.8712 | 19 | ULTIMATE MAX | 1 | 0 | 58.2884 | 139.2972
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 143.1307 | 19 | ULTIMATE MIN | 0 | -393.9405 | 0 | 0
| 3 | ULTIMATE MIN | 0 | -396.1235 | -298.3628 | -75.0872 | 19 | ULTIMATE MIN | 0.5 | -393.9405 | 0 | 0
| 3 | ULTIMATE MIN | 1 | -396.1235 | -306.8741 | 0 | 19 | ULTIMATE MIN | 1 | -393.9405 | 0 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 143.1307 | 20 | ULTIMATE MAX | 0 | 0 | 199.2295 | 139.2972
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 191.2028 | 20 | ULTIMATE MAX | 0.5 | 0 | 193.1658 | 85.4741
| 4 | ULTIMATE MIN | 0 | -396.1235 | -306.8741 | 0 | 20 | ULTIMATE MAX | 1 | 0 | 187.102 | 33.3186
| 4 | ULTIMATE MIN | 1 | -396.1235 | -310.7108 | 0 | 20 | ULTIMATE MIN | 0 | -393.9405 | 0 | 0
| 5 | ULTIMATE MAX | 0 | 0 | 0 | 191.2028 | 20 | ULTIMATE MIN | 0.5 | -393.9405 | 0 | 0
| 5 | ULTIMATE MAX | 0.5 | 0 | 0 | 230.0613 | 20 | ULTIMATE MIN | 1 | -393.9405 | 0 | 0
| 5 | ULTIMATE MAX | 1 | 0 | 0 | 270.6422 | 21 | ULTIMATE MAX | 0 | 0 | 328.3558 | 33.3186
| 5 | ULTIMATE MIN | 0 | -396.1235 | -168.2085 | 0 | 21 | ULTIMATE MAX | 1 | 0 | 323.2843 | 0
| 5 | ULTIMATE MIN | 0.5 | -396.1235 | -174.3715 | 0 | 21 | ULTIMATE MIN | 0 | -393.9405 | 0 | 0
| 5 | ULTIMATE MIN | 1 | -396.1235 | -180.5345 | 0 | 21 | ULTIMATE MIN | 1 | -393.9405 | 0 | -60.5216
| 6 | ULTIMATE MAX | 0 | 0 | 0 | 270.6422 | 22 | ULTIMATE MAX | 0 | 0 | 323.2843 | 0
| 6 | ULTIMATE MAX | 0.5 | 0 | 0 | 273.3368 | 22 | ULTIMATE MAX | 1 | 0 | 316.2283 | 0
| 6 | ULTIMATE MAX | 1 | 0 | 0 | 277.76 | 22 | ULTIMATE MIN | 0 | -393.9405 | 0 | -60.5216
| 6 | ULTIMATE MIN | 0 | -396.1235 | -39.8602 | 0 | 22 | ULTIMATE MIN | 1 | -393.9405 | 0 | -162.8433
| 6 | ULTIMATE MIN | 0.5 | -396.1235 | -44.627 | 0 | 23 | ULTIMATE MAX | 0 | 0 | 457.8402 | 0
| 6 | ULTIMATE MIN | 1 | -396.1235 | -50.801 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 450.1227 | 0
| 7 | ULTIMATE MAX | 0 | 0 | 122.7591 | 277.76 | 23 | ULTIMATE MIN | 0 | -393.9405 | 0 | -162.8433
| 7 | ULTIMATE MAX | 0.5 | 0 | 116.5962 | 244.3101 | 23 | ULTIMATE MIN | 1 | -393.9405 | 0 | -321.7368
| 7 | ULTIMATE MAX | 1 | 0 | 110.4332 | 212.5828 | 24 | ULTIMATE MAX | 0 | 0 | 450.1227 | 0
| 7 | ULTIMATE MIN | 0 | -396.1235 | 0 | 0 | 24 | ULTIMATE MAX | 1 | 0 | 445.7127 | 0
| 7 | ULTIMATE MIN | 0.5 | -396.1235 | 0 | 0 | 24 | ULTIMATE MIN | 0 | -393.9405 | 0 | -321.7368
| 7 | ULTIMATE MIN | 1 | -396.1235 | 0 | 0 | 24 | ULTIMATE MIN | 1 | -393.9405 | 0 | -411.3204
| 8 | ULTIMATE MAX | 0 | 0 | 252.4132 | 212.5828 | 25 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 8 | ULTIMATE MAX | 0.5 | 0 | 246.2502 | 142.8946 | 25 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 8 | ULTIMATE MAX | 1 | 0 | 240.0872 | 74.9289 | 25 | ULTIMATE MIN | 0 | -396.1203 | -501.4861 | -419.7577
| 8 | ULTIMATE MIN | 0 | -396.1235 | 0 | 0 | 25 | ULTIMATE MIN | 1 | -396.1203 | -505.8961 | -319.0194
| 8 | ULTIMATE MIN | 0.5 | -396.1235 | 0 | 0 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 8 | ULTIMATE MIN | 1 | -396.1235 | 0 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 9 | ULTIMATE MAX | 0 | 0 | 382.7379 | 74.9289 | 26 | ULTIMATE MIN | 0 | -396.1203 | -505.8961 | -319.0194
| 9 | ULTIMATE MAX | 1 | 0 | 377.2475 | 0 | 26 | ULTIMATE MIN | 1 | -396.1203 | -513.812 | -135.9818
| 9 | ULTIMATE MIN | 0 | -396.1235 | 0 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 9 | ULTIMATE MIN | 1 | -396.1235 | 0 | -26.5303 | 27 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 10 | ULTIMATE MAX | 0 | 0 | 377.2475 | 0 | 27 | ULTIMATE MIN | 0 | -396.1203 | -370.3559 | -135.9818
| 10 | ULTIMATE MAX | 1 | 0 | 370.3899 | 0 | 27 | ULTIMATE MIN | 1 | -396.1203 | -377.2134 | -26.57
| 10 | ULTIMATE MIN | 0 | -396.1235 | 0 | -26.5303 | 28 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 10 | ULTIMATE MIN | 1 | -396.1235 | 0 | -135.9469 | 28 | ULTIMATE MAX | 1 | 0 | 0 | 74.8749
| 11 | ULTIMATE MAX | 0 | 0 | 513.8475 | 0 | 28 | ULTIMATE MIN | 0 | -396.1203 | -377.2134 | -26.57
| 11 | ULTIMATE MAX | 1 | 0 | 505.9316 | 0 | 28 | ULTIMATE MIN | 1 | -396.1203 | -382.7039 | 0
| 11 | ULTIMATE MIN | 0 | -396.1235 | 0 | -135.9469 | 29 | ULTIMATE MAX | 0 | 0 | 0 | 74.8749
| 11 | ULTIMATE MIN | 1 | -396.1235 | 0 | -318.9972 | 29 | ULTIMATE MAX | 0.5 | 0 | 0 | 142.8315
| 12 | ULTIMATE MAX | 0 | 0 | 505.9316 | 0 | 29 | ULTIMATE MAX | 1 | 0 | 0 | 212.5108
| 12 | ULTIMATE MAX | 1 | 0 | 501.5216 | 0 | 29 | ULTIMATE MIN | 0 | -396.1203 | -240.055 | 0
| 12 | ULTIMATE MIN | 0 | -396.1235 | 0 | -318.9972 | 29 | ULTIMATE MIN | 0.5 | -396.1203 | -246.218 | 0
| 12 | ULTIMATE MIN | 1 | -396.1235 | 0 | -419.7425 | 29 | ULTIMATE MIN | 1 | -396.1203 | -252.381 | 0
| 13 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 30 | ULTIMATE MAX | 0 | 0 | 0 | 212.5108
| 13 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 30 | ULTIMATE MAX | 0.5 | 0 | 0 | 244.288
| 13 | ULTIMATE MIN | 0 | -393.9405 | -445.7031 | -411.2972 | 30 | ULTIMATE MAX | 1 | 0 | 0 | 277.7941
| 13 | ULTIMATE MIN | 1 | -393.9405 | -450.1131 | -321.7155 | 30 | ULTIMATE MIN | 0 | -396.1203 | -110.4034 | 0
| 14 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 30 | ULTIMATE MIN | 0.5 | -396.1203 | -116.5774 | 0
| 14 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 30 | ULTIMATE MIN | 1 | -396.1203 | -122.7514 | 0
| 14 | ULTIMATE MIN | 0 | -393.9405 | -450.1131 | -321.7155 | 31 | ULTIMATE MAX | 0 | 0 | 50.8057 | 277.7941
| 14 | ULTIMATE MIN | 1 | -393.9405 | -457.8306 | -162.8254 | 31 | ULTIMATE MAX | 0.5 | 0 | 44.6427 | 273.3759
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 31 | ULTIMATE MAX | 1 | 0 | 39.8838 | 270.6802
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 31 | ULTIMATE MIN | 0 | -396.1203 | 0 | 0
| 15 | ULTIMATE MIN | 0 | -393.9405 | -316.2179 | -162.8254 | 31 | ULTIMATE MIN | 0.5 | -396.1203 | 0 | 0
| 15 | ULTIMATE MIN | 1 | -393.9405 | -323.2739 | -60.5074 | 31 | ULTIMATE MIN | 1 | -396.1203 | 0 | 0
| 16 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 32 | ULTIMATE MAX | 0 | 0 | 180.5576 | 270.6802
| 16 | ULTIMATE MAX | 1 | 0 | 0 | 33.3308 | 32 | ULTIMATE MAX | 0.5 | 0 | 174.3946 | 230.0928
| 16 | ULTIMATE MIN | 0 | -393.9405 | -323.2739 | -60.5074 | 32 | ULTIMATE MAX | 1 | 0 | 168.2317 | 191.228
| 16 | ULTIMATE MIN | 1 | -393.9405 | -328.3454 | 0 | 32 | ULTIMATE MIN | 0 | -396.1203 | 0 | 0
| 17 | ULTIMATE MAX | 0 | 0 | 0 | 33.3308 | 32 | ULTIMATE MIN | 0.5 | -396.1203 | 0 | 0
| 17 | ULTIMATE MAX | 0.5 | 0 | 0 | 85.4833 | 32 | ULTIMATE MIN | 1 | -396.1203 | 0 | 0
| 17 | ULTIMATE MAX | 1 | 0 | 0 | 139.3034 | 33 | ULTIMATE MAX | 0 | 0 | 310.7297 | 191.228
| 17 | ULTIMATE MIN | 0 | -393.9405 | -187.0911 | 0 | 33 | ULTIMATE MAX | 1 | 0 | 306.893 | 143.1526
| 17 | ULTIMATE MIN | 0.5 | -393.9405 | -193.1548 | 0 | 33 | ULTIMATE MIN | 0 | -396.1203 | 0 | 0
| 17 | ULTIMATE MIN | 1 | -393.9405 | -199.2186 | 0 | 33 | ULTIMATE MIN | 1 | -396.1203 | 0 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 34 | ULTIMATE MAX | 0 | 0 | 306.893 | 143.1526 | 49 | ULTIMATE MIN | 0 | -350.1956 | -448.4911 | -286.2055
| 34 | ULTIMATE MAX | 1 | 0 | 298.3817 | 38.8857 | 49 | ULTIMATE MIN | 0.5 | -350.1956 | -373.3673 | -148.5442
| 34 | ULTIMATE MIN | 0 | -396.1203 | 0 | 0 | 49 | ULTIMATE MIN | 1 | -350.1956 | -298.2436 | -36.0494
| 34 | ULTIMATE MIN | 1 | -396.1203 | 0 | -75.0712 | 50 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 35 | ULTIMATE MAX | 0 | 0 | 441.4827 | 38.8857 | 50 | ULTIMATE MAX | 0.25 | 0 | 0 | 73.9907
| 35 | ULTIMATE MAX | 1 | 0 | 435.2205 | 0 | 50 | ULTIMATE MAX | 0.5 | 0 | 0 | 135.0986
| 35 | ULTIMATE MIN | 0 | -396.1203 | 0 | -75.0716 | 50 | ULTIMATE MAX | 0.75 | 0 | 0 | 172.2765
| 35 | ULTIMATE MIN | 1 | -396.1203 | 0 | -187.8054 | 50 | ULTIMATE MAX | 1 | 0 | 0.031349 | 184.6695
| 36 | ULTIMATE MAX | 0 | 0 | 435.2205 | 0 | 50 | ULTIMATE MIN | 0 | -350.1953 | -298.2436 | -36.0494
| 36 | ULTIMATE MAX | 1 | 0 | 429.1567 | 0 | 50 | ULTIMATE MIN | 0.25 | -350.1953 | -223.6804 | 0
| 36 | ULTIMATE MIN | 0 | -396.1203 | 0 | -187.8054 | 50 | ULTIMATE MIN | 0.5 | -350.1953 | -149.1173 | 0
| 36 | ULTIMATE MIN | 1 | -396.1203 | 0 | -306.6572 | 50 | ULTIMATE MIN | 0.75 | -350.1953 | -74.5542 | 0
| 37 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 50 | ULTIMATE MIN | 1 | -350.1953 | 0 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 51 | ULTIMATE MAX | 0 | 0 | 0.008959 | 184.6695
| 37 | ULTIMATE MIN | 0 | -571.6374 | -396.1203 | -306.6572 | 51 | ULTIMATE MAX | 0.25 | 0 | 74.5721 | 172.2709
| 37 | ULTIMATE MIN | 1 | -565.5737 | -325.0761 | -171.4997 | 51 | ULTIMATE MAX | 0.5 | 0 | 149.1352 | 135.0873
| 38 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 51 | ULTIMATE MAX | 0.75 | 0 | 223.6983 | 73.9759
| 38 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 51 | ULTIMATE MAX | 1 | 0 | 298.2615 | 0
| 38 | ULTIMATE MIN | 0 | -565.5737 | -325.0761 | -171.4997 | 51 | ULTIMATE MIN | 0 | -350.1952 | -0.014393 | 0
| 38 | ULTIMATE MIN | 1 | -557.9738 | -239.0526 | -54.3112 | 51 | ULTIMATE MIN | 0.25 | -350.1952 | 0 | 0
| 39 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 51 | ULTIMATE MIN | 0.5 | -350.1952 | 0 | 0
| 39 | ULTIMATE MAX | 0.25 | 0 | 0 | 101.6052 | 51 | ULTIMATE MIN | 0.75 | -350.1952 | 0 | 0
| 39 | ULTIMATE MAX | 0.5 | 0 | 19.5119 | 133.519 | 51 | ULTIMATE MIN | 1 | -350.1952 | 0 | -36.0731
| 39 | ULTIMATE MAX | 0.75 | 0 | 134.5579 | 74.0203 | 52 | ULTIMATE MAX | 0 | 0 | 298.2615 | 0
| 39 | ULTIMATE MAX | 1 | 0 | 240.7089 | 0 | 52 | ULTIMATE MAX | 0.5 | 0 | 373.3852 | 0
| 39 | ULTIMATE MIN | 0 | -557.9738 | -239.0526 | -54.3112 | 52 | ULTIMATE MAX | 1 | 0 | 448.509 | 0
| 39 | ULTIMATE MIN | 0.25 | -545.6037 | -106.2163 | 0 | 52 | ULTIMATE MIN | 0 | -350.1953 | 0 | -36.0731
| 39 | ULTIMATE MIN | 0.5 | -533.2337 | 0 | 0 | 52 | ULTIMATE MIN | 0.5 | -350.1953 | 0 | -148.574
| 39 | ULTIMATE MIN | 0.75 | -520.8636 | 0 | -6.0142 | 52 | ULTIMATE MIN | 1 | -350.1953 | 0 | -286.2412
| 39 | ULTIMATE MIN | 1 | -508.4936 | 0 | -79.0657 | 53 | ULTIMATE MAX | 0 | 0 | 448.509 | 0
| 40 | ULTIMATE MAX | 0 | 0 | 240.7029 | 0 | 53 | ULTIMATE MAX | 1 | 0 | 493.359 | 0
| 40 | ULTIMATE MAX | 1 | 0 | 301.5081 | 0 | 53 | ULTIMATE MIN | 0 | -350.1954 | 0 | -286.2412
| 40 | ULTIMATE MIN | 0 | -508.4936 | 0 | -79.0654 | 53 | ULTIMATE MIN | 1 | -350.1954 | 0 | -380.428
| 40 | ULTIMATE MIN | 1 | -500.8937 | 0 | -201.8776 | 54 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 41 | ULTIMATE MAX | 0 | 0 | 301.5067 | 0 | 54 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 41 | ULTIMATE MAX | 1 | 0 | 347.6131 | 0 | 54 | ULTIMATE MIN | 0 | -347.6072 | -540.9377 | -380.1363
| 41 | ULTIMATE MIN | 0 | -500.8937 | 0 | -201.8775 | 54 | ULTIMATE MIN | 1 | -347.6072 | -496.0877 | -276.4338
| 41 | ULTIMATE MIN | 1 | -494.8299 | 0 | -322.989 | 55 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 42 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 55 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 42 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 55 | ULTIMATE MAX | 1 | 0 | 0 | 6.0249
| 42 | ULTIMATE MIN | 0 | -347.6124 | -494.8299 | -322.989 | 55 | ULTIMATE MIN | 0 | -347.6073 | -496.0877 | -276.4338
| 42 | ULTIMATE MIN | 1 | -347.6124 | -433.1612 | -201.7703 | 55 | ULTIMATE MIN | 0.5 | -347.6073 | -420.9639 | -122.8276
| 43 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 55 | ULTIMATE MIN | 1 | -347.6073 | -345.8402 | 0
| 43 | ULTIMATE MAX | 0.5 | 0 | 0 | 35.6363 | 56 | ULTIMATE MAX | 0 | 0 | 0 | 6.025
| 43 | ULTIMATE MAX | 1 | 0 | 0 | 132.1954 | 56 | ULTIMATE MAX | 0.25 | 0 | 0 | 108.2078
| 43 | ULTIMATE MIN | 0 | -347.612 | -433.1612 | -201.7703 | 56 | ULTIMATE MAX | 0.5 | 0 | 0 | 186.0113
| 43 | ULTIMATE MIN | 0.5 | -347.612 | -358.0374 | -79.1703 | 56 | ULTIMATE MAX | 0.75 | 0 | 0 | 239.0226
| 43 | ULTIMATE MIN | 1 | -347.612 | -282.9137 | 0 | 56 | ULTIMATE MAX | 1 | 0 | 0 | 267.2416
| 44 | ULTIMATE MAX | 0 | 0 | 0 | 132.1954 | 56 | ULTIMATE MIN | 0 | -347.6076 | -345.8402 | 0
| 44 | ULTIMATE MAX | 0.25 | 0 | 0 | 203.1483 | 56 | ULTIMATE MIN | 0.25 | -347.6076 | -271.277 | 0
| 44 | ULTIMATE MAX | 0.5 | 0 | 0 | 249.3091 | 56 | ULTIMATE MIN | 0.5 | -347.6076 | -196.7139 | 0
| 44 | ULTIMATE MAX | 0.75 | 0 | 0 | 270.6776 | 56 | ULTIMATE MIN | 0.75 | -347.6076 | -122.1508 | 0
| 44 | ULTIMATE MAX | 1 | 0 | 47.5785 | 267.2538 | 56 | ULTIMATE MIN | 1 | -347.6076 | -47.5877 | 0
| 44 | ULTIMATE MIN | 0 | -347.6112 | -282.9137 | 0 | 57 | ULTIMATE MAX | 0 | 0 | 0 | 267.2416
| 44 | ULTIMATE MIN | 0.25 | -347.6112 | -208.3506 | 0 | 57 | ULTIMATE MAX | 0.25 | 0 | 61.8828 | 270.6683
| 44 | ULTIMATE MIN | 0.5 | -347.6112 | -133.7874 | 0 | 57 | ULTIMATE MAX | 0.5 | 0 | 133.7783 | 249.3029
| 44 | ULTIMATE MIN | 0.75 | -347.6112 | -61.8909 | 0 | 57 | ULTIMATE MAX | 0.75 | 0 | 208.3414 | 203.1452
| 44 | ULTIMATE MIN | 1 | -347.6112 | 0 | 0 | 57 | ULTIMATE MAX | 1 | 0 | 282.9045 | 132.1952
| 45 | ULTIMATE MAX | 0 | 0 | 47.5785 | 267.2538 | 57 | ULTIMATE MIN | 0 | -347.6082 | -47.5877 | 0
| 45 | ULTIMATE MAX | 0.25 | 0 | 122.1417 | 239.0378 | 57 | ULTIMATE MIN | 0.25 | -347.6082 | 0 | 0
| 45 | ULTIMATE MAX | 0.5 | 0 | 196.7048 | 186.0296 | 57 | ULTIMATE MIN | 0.5 | -347.6082 | 0 | 0
| 45 | ULTIMATE MAX | 0.75 | 0 | 271.2679 | 108.2292 | 57 | ULTIMATE MIN | 0.75 | -347.6082 | 0 | 0
| 45 | ULTIMATE MAX | 1 | 0 | 345.831 | 6.0461 | 57 | ULTIMATE MIN | 1 | -347.6082 | 0 | 0
| 45 | ULTIMATE MIN | 0 | -347.6104 | 0 | 0 | 58 | ULTIMATE MAX | 0 | 0 | 282.9045 | 132.1952
| 45 | ULTIMATE MIN | 0.25 | -347.6104 | 0 | 0 | 58 | ULTIMATE MAX | 0.5 | 0 | 358.0283 | 35.6393
| 45 | ULTIMATE MIN | 0.5 | -347.6104 | 0 | 0 | 58 | ULTIMATE MAX | 1 | 0 | 433.152 | 0
| 45 | ULTIMATE MIN | 0.75 | -347.6104 | 0 | 0 | 58 | ULTIMATE MIN | 0 | -347.6088 | 0 | 0
| 45 | ULTIMATE MIN | 1 | -347.6104 | 0 | 0 | 58 | ULTIMATE MIN | 0.5 | -347.6088 | 0 | -79.1657
| 46 | ULTIMATE MAX | 0 | 0 | 345.831 | 6.0459 | 58 | ULTIMATE MIN | 1 | -347.6088 | 0 | -201.7628
| 46 | ULTIMATE MAX | 0.5 | 0 | 420.9548 | 0 | 59 | ULTIMATE MAX | 0 | 0 | 433.152 | 0
| 46 | ULTIMATE MAX | 1 | 0 | 496.0785 | 0 | 59 | ULTIMATE MAX | 1 | 0 | 494.8208 | 0
| 46 | ULTIMATE MIN | 0 | -347.6099 | 0 | 0 | 59 | ULTIMATE MIN | 0 | -347.6091 | 0 | -201.7629
| 46 | ULTIMATE MIN | 0.5 | -347.6099 | 0 | -122.8002 | 59 | ULTIMATE MIN | 1 | -347.6091 | 0 | -322.9782
| 46 | ULTIMATE MIN | 1 | -347.6099 | 0 | -276.4032 | 60 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 47 | ULTIMATE MAX | 0 | 0 | 496.0785 | 0 | 60 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 47 | ULTIMATE MAX | 1 | 0 | 540.9285 | 0 | 60 | ULTIMATE MIN | 0 | -494.8208 | -347.6098 | -322.9782
| 47 | ULTIMATE MIN | 0 | -347.6097 | 0 | -276.4032 | 60 | ULTIMATE MIN | 1 | -500.8845 | -301.5034 | -201.8681
| 47 | ULTIMATE MIN | 1 | -347.6097 | 0 | -380.1039 | 61 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 48 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 61 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 48 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 61 | ULTIMATE MIN | 0 | -500.8845 | -301.5047 | -201.8682
| 48 | ULTIMATE MIN | 0 | -350.1957 | -493.3411 | -380.3887 | 61 | ULTIMATE MIN | 1 | -508.4844 | -240.6995 | -79.0587
| 48 | ULTIMATE MIN | 1 | -350.1957 | -448.4911 | -286.2055 | 62 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 49 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 62 | ULTIMATE MAX | 0.25 | 0 | 0 | 74.0243
| 49 | ULTIMATE MAX | 0.5 | 0 | 0 | 0 | 62 | ULTIMATE MAX | 0.5 | 0 | 0 | 133.5202
| 49 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 62 | ULTIMATE MAX | 0.75 | 0 | 106.2195 | 101.6035
| FRAME | LOAD | DIST | P | V2 | M3
| 62 | ULTIMATE MAX | 1 | 0 | 239.0558 | 0
| 62 | ULTIMATE MIN | 0 | -508.4844 | -240.7051 | -79.059
| 62 | ULTIMATE MIN | 0.25 | -520.8545 | -134.5542 | -6.0107
| 62 | ULTIMATE MIN | 0.5 | -533.2245 | -19.5081 | 0
| 62 | ULTIMATE MIN | 0.75 | -545.5946 | 0 | 0
| 62 | ULTIMATE MIN | 1 | -557.9646 | 0 | -54.3151
| 63 | ULTIMATE MAX | 0 | 0 | 239.0558 | 0
| 63 | ULTIMATE MAX | 1 | 0 | 325.0793 | 0
| 63 | ULTIMATE MIN | 0 | -557.9646 | 0 | -54.3151
| 63 | ULTIMATE MIN | 1 | -565.5645 | 0 | -171.5051
| 64 | ULTIMATE MAX | 0 | 0 | 325.0793 | 0
| 64 | ULTIMATE MAX | 1 | 0 | 396.1235 | 0
| 64 | ULTIMATE MIN | 0 | -565.5645 | 0 | -171.5051
| 64 | ULTIMATE MIN | 1 | -571.6283 | 0 | -306.6638
| 65 | ULTIMATE MAX | 0 | 0 | 2.5884 | 5.7052
| 65 | ULTIMATE MAX | 0.25 | 0 | 2.5884 | 2.6315
| 65 | ULTIMATE MAX | 0.5 | 0 | 2.5884 | 0
| 65 | ULTIMATE MAX | 0.75 | 0 | 2.5884 | 0
| 65 | ULTIMATE MAX | 1 | 0 | 2.5884 | 0
| 65 | ULTIMATE MIN | 0 | -1034.297 | 0 | 0
| 65 | ULTIMATE MIN | 0.25 | -1048.262 | 0 | -1.8926
| 65 | ULTIMATE MIN | 0.5 | -1062.227 | 0 | -4.0768
| 65 | ULTIMATE MIN | 0.75 | -1076.192 | 0 | -6.2626
| 65 | ULTIMATE MIN | 1 | -1090.157 | 0 | -8.4498
| 66 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 66 | ULTIMATE MAX | 0.25 | 0 | 0 | 1.8958
| 66 | ULTIMATE MAX | 0.5 | 0 | 0 | 4.0763
| 66 | ULTIMATE MAX | 0.75 | 0 | 0 | 6.2588
| 66 | ULTIMATE MAX | 1 | 0 | 0 | 8.4427
| 66 | ULTIMATE MIN | 0 | -1034.27 | -2.5865 | -5.7012
| 66 | ULTIMATE MIN | 0.25 | -1048.235 | -2.5865 | -2.6297
| 66 | ULTIMATE MIN | 0.5 | -1062.2 | -2.5865 | 0
| 66 | ULTIMATE MIN | 0.75 | -1076.165 | -2.5865 | 0
| 66 | ULTIMATE MIN | 1 | -1090.13 | -2.5865 | 0
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 18 | SERVICE MIN | 0 | -245.9414 | -27.4491 | 0
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 18 | SERVICE MIN | 0.5 | -245.9414 | -41.3023 | 0
| 1 | SERVICE MIN | 0 | -247.3671 | -271.6325 | -190.5976 | 18 | SERVICE MIN | 1 | -245.9414 | -55.1554 | 0
| 1 | SERVICE MIN | 1 | -247.3671 | -276.6857 | -117.897 | 19 | SERVICE MAX | 0 | 0 | 55.1642 | 110.809
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 19 | SERVICE MAX | 0.5 | 0 | 41.311 | 97.5718
| 2 | SERVICE MAX | 1 | 0 | 0 | 29.281 | 19 | SERVICE MAX | 1 | 0 | 27.4579 | 88.1441
| 2 | SERVICE MIN | 0 | -247.3671 | -276.6857 | -117.897 | 19 | SERVICE MIN | 0 | -245.9414 | 0 | 0
| 2 | SERVICE MIN | 1 | -247.3671 | -290.9922 | -41.4073 | 19 | SERVICE MIN | 0.5 | -245.9414 | 0 | 0
| 3 | SERVICE MAX | 0 | 0 | 0 | 29.281 | 19 | SERVICE MIN | 1 | -245.9414 | 0 | 0
| 3 | SERVICE MAX | 1 | 0 | 0 | 94.2866 | 20 | SERVICE MAX | 0 | 0 | 137.8535 | 88.1441
| 3 | SERVICE MIN | 0 | -247.3671 | -179.0085 | -41.4072 | 20 | SERVICE MAX | 0.5 | 0 | 124.0003 | 52.2213
| 3 | SERVICE MIN | 1 | -247.3671 | -198.4532 | 0 | 20 | SERVICE MAX | 1 | 0 | 110.1472 | 21.3199
| 4 | SERVICE MAX | 0 | 0 | 0 | 94.2866 | 20 | SERVICE MIN | 0 | -245.9414 | 0 | 0
| 4 | SERVICE MAX | 1 | 0 | 0 | 126.0439 | 20 | SERVICE MIN | 0.5 | -245.9414 | 0 | 0
| 4 | SERVICE MIN | 0 | -247.3671 | -198.4532 | 0 | 20 | SERVICE MIN | 1 | -245.9414 | 0 | 0
| 4 | SERVICE MIN | 1 | -247.3671 | -207.2185 | 0 | 21 | SERVICE MAX | 0 | 0 | 220.7396 | 21.3199
| 5 | SERVICE MAX | 0 | 0 | 0 | 126.0439 | 21 | SERVICE MAX | 1 | 0 | 209.1533 | 0
| 5 | SERVICE MAX | 0.5 | 0 | 0 | 149.1 | 21 | SERVICE MIN | 0 | -245.9414 | 0 | 0
| 5 | SERVICE MAX | 1 | 0 | 0 | 176.0915 | 21 | SERVICE MIN | 1 | -245.9414 | 0 | -41.1434
| 5 | SERVICE MIN | 0 | -247.3671 | -95.6142 | 0 | 22 | SERVICE MAX | 0 | 0 | 209.1533 | 0
| 5 | SERVICE MIN | 0.5 | -247.3671 | -109.694 | 0 | 22 | SERVICE MAX | 1 | 0 | 193.0333 | 0
| 5 | SERVICE MIN | 1 | -247.3671 | -123.7738 | 0 | 22 | SERVICE MIN | 0 | -245.9414 | 0 | -41.1435
| 6 | SERVICE MAX | 0 | 0 | 7.5282 | 176.0915 | 22 | SERVICE MIN | 1 | -245.9414 | 0 | -105.4928
| 6 | SERVICE MAX | 0.5 | 0 | 0 | 175.9601 | 23 | SERVICE MAX | 0 | 0 | 303.8491 | 0
| 6 | SERVICE MAX | 1 | 0 | 0 | 179.7781 | 23 | SERVICE MAX | 1 | 0 | 286.2178 | 0
| 6 | SERVICE MIN | 0 | -247.3671 | -13.8554 | 0 | 23 | SERVICE MIN | 0 | -245.9414 | 0 | -105.4928
| 6 | SERVICE MIN | 0.5 | -247.3671 | -27.9604 | 0 | 23 | SERVICE MIN | 1 | -245.9414 | 0 | -208.7545
| 6 | SERVICE MIN | 1 | -247.3671 | -42.0654 | 0 | 24 | SERVICE MAX | 0 | 0 | 286.2178 | 0
| 7 | SERVICE MAX | 0 | 0 | 90.4009 | 179.7781 | 24 | SERVICE MAX | 1 | 0 | 282.5428 | 0
| 7 | SERVICE MAX | 0.5 | 0 | 76.3211 | 156.4787 | 24 | SERVICE MIN | 0 | -245.9414 | 0 | -208.7545
| 7 | SERVICE MAX | 1 | 0 | 62.2413 | 137.1147 | 24 | SERVICE MIN | 1 | -245.9414 | 0 | -265.6306
| 7 | SERVICE MIN | 0 | -247.3671 | 0 | 0 | 25 | SERVICE MAX | 0 | 0 | 0 | 0
| 7 | SERVICE MIN | 0.5 | -247.3671 | 0 | 0 | 25 | SERVICE MAX | 1 | 0 | 0 | 0
| 7 | SERVICE MIN | 1 | -247.3671 | 0 | 0 | 25 | SERVICE MIN | 0 | -247.3647 | -319.4821 | -271.7074
| 8 | SERVICE MAX | 0 | 0 | 173.5641 | 137.1147 | 25 | SERVICE MIN | 1 | -247.3647 | -323.1571 | -207.4434
| 8 | SERVICE MAX | 0.5 | 0 | 159.4843 | 90.5711 | 26 | SERVICE MAX | 0 | 0 | 0 | 0
| 8 | SERVICE MAX | 1 | 0 | 145.4045 | 47.9629 | 26 | SERVICE MAX | 1 | 0 | 0 | 0
| 8 | SERVICE MIN | 0 | -247.3671 | 0 | 0 | 26 | SERVICE MIN | 0 | -247.3647 | -323.1571 | -207.4434
| 8 | SERVICE MIN | 0.5 | -247.3671 | 0 | 0 | 26 | SERVICE MIN | 1 | -247.3647 | -341.2418 | -88.1838
| 8 | SERVICE MIN | 1 | -247.3671 | 0 | 0 | 27 | SERVICE MAX | 0 | 0 | 0 | 0
| 9 | SERVICE MAX | 0 | 0 | 257.1752 | 47.9629 | 27 | SERVICE MAX | 1 | 0 | 0 | 0
| 9 | SERVICE MAX | 1 | 0 | 244.6319 | 0 | 27 | SERVICE MIN | 0 | -247.3647 | -228.9385 | -88.1838
| 9 | SERVICE MIN | 0 | -247.3671 | 0 | 0 | 27 | SERVICE MIN | 1 | -247.3647 | -244.6052 | -17.7891
| 9 | SERVICE MIN | 1 | -247.3671 | 0 | -17.7536 | 28 | SERVICE MAX | 0 | 0 | 0 | 0
| 10 | SERVICE MAX | 0 | 0 | 244.6319 | 0 | 28 | SERVICE MAX | 1 | 0 | 0 | 47.9205
| 10 | SERVICE MAX | 1 | 0 | 228.9652 | 0 | 28 | SERVICE MIN | 0 | -247.3647 | -244.6052 | -17.7891
| 10 | SERVICE MIN | 0 | -247.3671 | 0 | -17.7536 | 28 | SERVICE MIN | 1 | -247.3647 | -257.1485 | 0
| 10 | SERVICE MIN | 1 | -247.3671 | 0 | -88.1564 | 29 | SERVICE MAX | 0 | 0 | 0 | 47.9205
| 11 | SERVICE MAX | 0 | 0 | 341.2696 | 0 | 29 | SERVICE MAX | 0.5 | 0 | 0 | 90.5217
| 11 | SERVICE MAX | 1 | 0 | 323.185 | 0 | 29 | SERVICE MAX | 1 | 0 | 0 | 137.0582
| 11 | SERVICE MIN | 0 | -247.3671 | 0 | -88.1564 | 29 | SERVICE MIN | 0 | -247.3647 | -145.3793 | 0
| 11 | SERVICE MIN | 1 | -247.3671 | 0 | -207.426 | 29 | SERVICE MIN | 0.5 | -247.3647 | -159.4591 | 0
| 12 | SERVICE MAX | 0 | 0 | 323.185 | 0 | 29 | SERVICE MIN | 1 | -247.3647 | -173.5389 | 0
| 12 | SERVICE MAX | 1 | 0 | 319.51 | 0 | 30 | SERVICE MAX | 0 | 0 | 0 | 137.0582
| 12 | SERVICE MIN | 0 | -247.3671 | 0 | -207.426 | 30 | SERVICE MAX | 0.5 | 0 | 0 | 156.4539
| 12 | SERVICE MIN | 1 | -247.3671 | 0 | -271.6955 | 30 | SERVICE MAX | 1 | 0 | 0 | 179.799
| 13 | SERVICE MAX | 0 | 0 | 0 | 0 | 30 | SERVICE MIN | 0 | -247.3647 | -62.2178 | 0
| 13 | SERVICE MAX | 1 | 0 | 0 | 0 | 30 | SERVICE MIN | 0.5 | -247.3647 | -76.3228 | 0
| 13 | SERVICE MIN | 0 | -245.9414 | -282.5353 | -265.6124 | 30 | SERVICE MIN | 1 | -247.3647 | -90.4278 | 0
| 13 | SERVICE MIN | 1 | -245.9414 | -286.2103 | -208.7378 | 31 | SERVICE MAX | 0 | 0 | 42.035 | 179.799
| 14 | SERVICE MAX | 0 | 0 | 0 | 0 | 31 | SERVICE MAX | 0.5 | 0 | 27.9552 | 175.9925
| 14 | SERVICE MAX | 1 | 0 | 0 | 0 | 31 | SERVICE MAX | 1 | 0 | 13.8754 | 176.1213
| 14 | SERVICE MIN | 0 | -245.9414 | -286.2103 | -208.7378 | 31 | SERVICE MIN | 0 | -247.3647 | 0 | 0
| 14 | SERVICE MIN | 1 | -245.9414 | -303.8415 | -105.4787 | 31 | SERVICE MIN | 0.5 | -247.3647 | 0 | 0
| 15 | SERVICE MAX | 0 | 0 | 0 | 0 | 31 | SERVICE MIN | 1 | -247.3647 | -7.5076 | 0
| 15 | SERVICE MAX | 1 | 0 | 0 | 0 | 32 | SERVICE MAX | 0 | 0 | 123.7919 | 176.1213
| 15 | SERVICE MIN | 0 | -245.9414 | -193.0251 | -105.4787 | 32 | SERVICE MAX | 0.5 | 0 | 109.7121 | 149.1248
| 15 | SERVICE MIN | 1 | -245.9414 | -209.1451 | -41.1322 | 32 | SERVICE MAX | 1 | 0 | 95.6323 | 126.0636
| 16 | SERVICE MAX | 0 | 0 | 0 | 0 | 32 | SERVICE MIN | 0 | -247.3647 | 0 | 0
| 16 | SERVICE MAX | 1 | 0 | 0 | 21.329 | 32 | SERVICE MIN | 0.5 | -247.3647 | 0 | 0
| 16 | SERVICE MIN | 0 | -245.9414 | -209.1451 | -41.1322 | 32 | SERVICE MIN | 1 | -247.3647 | 0 | 0
| 16 | SERVICE MIN | 1 | -245.9414 | -220.7314 | 0 | 33 | SERVICE MAX | 0 | 0 | 207.2333 | 126.0636
| 17 | SERVICE MAX | 0 | 0 | 0 | 21.329 | 33 | SERVICE MAX | 1 | 0 | 198.4681 | 94.3037
| 17 | SERVICE MAX | 0.5 | 0 | 0 | 52.2285 | 33 | SERVICE MIN | 0 | -247.3647 | 0 | 0
| 17 | SERVICE MAX | 1 | 0 | 0 | 88.149 | 33 | SERVICE MIN | 1 | -247.3647 | 0 | 0
| 17 | SERVICE MIN | 0 | -245.9414 | -110.1386 | 0 | 34 | SERVICE MAX | 0 | 0 | 198.4681 | 94.3037
| 17 | SERVICE MIN | 0.5 | -245.9414 | -123.9917 | 0 | 34 | SERVICE MAX | 1 | 0 | 179.0233 | 29.2924
| 17 | SERVICE MIN | 1 | -245.9414 | -137.8449 | 0 | 34 | SERVICE MIN | 0 | -247.3647 | 0 | 0
| 18 | SERVICE MAX | 0 | 0 | 0 | 88.149 | 34 | SERVICE MIN | 1 | -247.3647 | 0 | -41.3944
| 18 | SERVICE MAX | 0.5 | 0 | 0 | 97.5742 | 35 | SERVICE MAX | 0 | 0 | 291.0034 | 29.2924
| 18 | SERVICE MAX | 1 | 0 | 0 | 110.809 | 35 | SERVICE MAX | 1 | 0 | 276.6969 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 35 | SERVICE MIN | 0 | -247.3647 | 0 | -41.3946 | 50 | SERVICE MAX | 0.75 | 0 | 0 | 111.909
| 35 | SERVICE MIN | 1 | -247.3647 | 0 | -117.8892 | 50 | SERVICE MAX | 1 | 0 | 0.024026 | 119.9074
| 36 | SERVICE MAX | 0 | 0 | 276.6969 | 0 | 50 | SERVICE MIN | 0 | -218.8407 | -192.5105 | -22.1029
| 36 | SERVICE MAX | 1 | 0 | 271.6437 | 0 | 50 | SERVICE MIN | 0.25 | -218.8407 | -144.3811 | 0
| 36 | SERVICE MIN | 0 | -247.3647 | 0 | -117.8892 | 50 | SERVICE MIN | 0.5 | -218.8407 | -96.2517 | 0
| 36 | SERVICE MIN | 1 | -247.3647 | 0 | -190.5924 | 50 | SERVICE MIN | 0.75 | -218.8407 | -48.1224 | 0
| 37 | SERVICE MAX | 0 | 0 | 0 | 0 | 50 | SERVICE MIN | 1 | -218.8407 | 0 | 0
| 37 | SERVICE MAX | 1 | 0 | 0 | 0 | 51 | SERVICE MAX | 0 | 0 | 0.007024 | 119.9074
| 37 | SERVICE MIN | 0 | -383.0638 | -247.3647 | -190.5924 | 51 | SERVICE MAX | 0.25 | 0 | 48.1364 | 111.9045
| 37 | SERVICE MIN | 1 | -378.0106 | -202.9621 | -106.5095 | 51 | SERVICE MAX | 0.5 | 0 | 96.2658 | 87.9035
| 38 | SERVICE MAX | 0 | 0 | 0 | 0 | 51 | SERVICE MAX | 0.75 | 0 | 144.3951 | 47.8994
| 38 | SERVICE MAX | 1 | 0 | 0 | 0 | 51 | SERVICE MAX | 1 | 0 | 192.5245 | 0
| 38 | SERVICE MIN | 0 | -378.0106 | -202.9621 | -106.5095 | 51 | SERVICE MIN | 0 | -218.8406 | -0.010571 | 0
| 38 | SERVICE MIN | 1 | -371.6774 | -149.1974 | -33.7563 | 51 | SERVICE MIN | 0.25 | -218.8406 | 0 | 0
| 39 | SERVICE MAX | 0 | 0 | 0 | 0 | 51 | SERVICE MIN | 0.5 | -218.8406 | 0 | 0
| 39 | SERVICE MAX | 0.25 | 0 | 0 | 59.8083 | 51 | SERVICE MIN | 0.75 | -218.8406 | 0 | 0
| 39 | SERVICE MAX | 0.5 | 0 | 12.1295 | 80.4406 | 51 | SERVICE MIN | 1 | -218.8406 | 0 | -22.1216
| 39 | SERVICE MAX | 0.75 | 0 | 84.0333 | 43.94 | 52 | SERVICE MAX | 0 | 0 | 192.5245 | 0
| 39 | SERVICE MAX | 1 | 0 | 150.3776 | 0 | 52 | SERVICE MAX | 0.5 | 0 | 241.0158 | 0
| 39 | SERVICE MIN | 0 | -371.6774 | -149.1974 | -33.7563 | 52 | SERVICE MAX | 1 | 0 | 289.507 | 0
| 39 | SERVICE MIN | 0.25 | -361.369 | -66.1747 | 0 | 52 | SERVICE MIN | 0 | -218.8406 | 0 | -22.1216
| 39 | SERVICE MIN | 0.5 | -351.0606 | 0 | 0 | 52 | SERVICE MIN | 0.5 | -218.8406 | 0 | -94.7396
| 39 | SERVICE MIN | 0.75 | -340.7523 | 0 | -5.9609 | 52 | SERVICE MIN | 1 | -218.8406 | 0 | -183.6021
| 39 | SERVICE MIN | 1 | -330.4439 | 0 | -52.4159 | 53 | SERVICE MAX | 0 | 0 | 289.507 | 0
| 40 | SERVICE MAX | 0 | 0 | 150.3739 | 0 | 53 | SERVICE MAX | 1 | 0 | 318.457 | 0
| 40 | SERVICE MAX | 1 | 0 | 188.3772 | 0 | 53 | SERVICE MIN | 0 | -218.8407 | 0 | -183.6021
| 40 | SERVICE MIN | 0 | -330.4439 | 0 | -52.4157 | 53 | SERVICE MIN | 1 | -218.8407 | 0 | -244.3985
| 40 | SERVICE MIN | 1 | -324.1106 | 0 | -129.6637 | 54 | SERVICE MAX | 0 | 0 | 0 | 0
| 41 | SERVICE MAX | 0 | 0 | 188.3763 | 0 | 54 | SERVICE MAX | 1 | 0 | 0 | 0
| 41 | SERVICE MAX | 1 | 0 | 217.1928 | 0 | 54 | SERVICE MIN | 0 | -217.1883 | -348.8557 | -243.6607
| 41 | SERVICE MIN | 0 | -324.1106 | 0 | -129.6637 | 54 | SERVICE MIN | 1 | -217.1883 | -319.9057 | -176.7846
| 41 | SERVICE MIN | 1 | -319.0575 | 0 | -205.7497 | 55 | SERVICE MAX | 0 | 0 | 0 | 0
| 42 | SERVICE MAX | 0 | 0 | 0 | 0 | 55 | SERVICE MAX | 0.5 | 0 | 0 | 0
| 42 | SERVICE MAX | 1 | 0 | 0 | 0 | 55 | SERVICE MAX | 1 | 0 | 0 | 5.0734
| 42 | SERVICE MIN | 0 | -217.1924 | -319.0575 | -205.7497 | 55 | SERVICE MIN | 0 | -217.1884 | -319.9057 | -176.7846
| 42 | SERVICE MIN | 1 | -217.1924 | -279.2513 | -123.4913 | 55 | SERVICE MIN | 0.5 | -217.1884 | -271.4145 | -77.7384
| 43 | SERVICE MAX | 0 | 0 | 0 | 0 | 55 | SERVICE MIN | 1 | -217.1884 | -222.9232 | 0
| 43 | SERVICE MAX | 0.5 | 0 | 0 | 23.5103 | 56 | SERVICE MAX | 0 | 0 | 0 | 5.0734
| 43 | SERVICE MAX | 1 | 0 | 0 | 85.9425 | 56 | SERVICE MAX | 0.25 | 0 | 0 | 71.1836
| 43 | SERVICE MIN | 0 | -217.1921 | -279.2513 | -123.4913 | 56 | SERVICE MAX | 0.5 | 0 | 0 | 121.301
| 43 | SERVICE MIN | 0.5 | -217.1921 | -230.76 | -43.0611 | 56 | SERVICE MAX | 0.75 | 0 | 0 | 155.4155
| 43 | SERVICE MIN | 1 | -217.1921 | -182.2688 | 0 | 56 | SERVICE MAX | 1 | 0 | 0 | 173.5269
| 44 | SERVICE MAX | 0 | 0 | 0 | 85.9425 | 56 | SERVICE MIN | 0 | -217.1886 | -222.9232 | 0
| 44 | SERVICE MAX | 0.25 | 0 | 0 | 131.8455 | 56 | SERVICE MIN | 0.25 | -217.1886 | -174.7939 | 0
| 44 | SERVICE MAX | 0.5 | 0 | 0 | 161.7455 | 56 | SERVICE MIN | 0.5 | -217.1886 | -126.6645 | 0
| 44 | SERVICE MAX | 0.75 | 0 | 0 | 175.6425 | 56 | SERVICE MIN | 0.75 | -217.1886 | -78.5351 | 0
| 44 | SERVICE MAX | 1 | 0 | 30.3986 | 173.5365 | 56 | SERVICE MIN | 1 | -217.1886 | -30.4057 | 0
| 44 | SERVICE MIN | 0 | -217.1916 | -182.2692 | 0 | 57 | SERVICE MAX | 0 | 0 | 0 | 173.5269
| 44 | SERVICE MIN | 0.25 | -217.1916 | -134.1398 | 0 | 57 | SERVICE MAX | 0.25 | 0 | 37.8736 | 175.6353
| 44 | SERVICE MIN | 0.5 | -217.1916 | -86.0105 | 0 | 57 | SERVICE MAX | 0.5 | 0 | 86.003 | 161.7407
| 44 | SERVICE MIN | 0.75 | -217.1916 | -37.8811 | 0 | 57 | SERVICE MAX | 0.75 | 0 | 134.1324 | 131.843
| 44 | SERVICE MIN | 1 | -217.1916 | 0 | 0 | 57 | SERVICE MAX | 1 | 0 | 182.2617 | 85.9424
| 45 | SERVICE MAX | 0 | 0 | 30.3986 | 173.5365 | 57 | SERVICE MIN | 0 | -217.189 | -30.4057 | 0
| 45 | SERVICE MAX | 0.25 | 0 | 78.5279 | 155.4275 | 57 | SERVICE MIN | 0.25 | -217.189 | 0 | 0
| 45 | SERVICE MAX | 0.5 | 0 | 126.6573 | 121.3154 | 57 | SERVICE MIN | 0.5 | -217.189 | 0 | 0
| 45 | SERVICE MAX | 0.75 | 0 | 174.7867 | 71.2003 | 57 | SERVICE MIN | 0.75 | -217.189 | 0 | 0
| 45 | SERVICE MAX | 1 | 0 | 222.9161 | 5.0924 | 57 | SERVICE MIN | 1 | -217.189 | 0 | 0
| 45 | SERVICE MIN | 0 | -217.1911 | 0 | 0 | 58 | SERVICE MAX | 0 | 0 | 182.2616 | 85.9424
| 45 | SERVICE MIN | 0.25 | -217.1911 | 0 | 0 | 58 | SERVICE MAX | 0.5 | 0 | 230.7528 | 23.5126
| 45 | SERVICE MIN | 0.5 | -217.1911 | 0 | 0 | 58 | SERVICE MAX | 1 | 0 | 279.2441 | 0
| 45 | SERVICE MIN | 0.75 | -217.1911 | 0 | 0 | 58 | SERVICE MIN | 0 | -217.1894 | 0 | 0
| 45 | SERVICE MIN | 1 | -217.1911 | 0 | 0 | 58 | SERVICE MIN | 0.5 | -217.1894 | 0 | -43.0577
| 46 | SERVICE MAX | 0 | 0 | 222.9161 | 5.0924 | 58 | SERVICE MIN | 1 | -217.1894 | 0 | -123.4852
| 46 | SERVICE MAX | 0.5 | 0 | 271.4073 | 0 | 59 | SERVICE MAX | 0 | 0 | 279.2441 | 0
| 46 | SERVICE MAX | 1 | 0 | 319.8986 | 0 | 59 | SERVICE MAX | 1 | 0 | 319.0503 | 0
| 46 | SERVICE MIN | 0 | -217.1908 | 0 | 0 | 59 | SERVICE MIN | 0 | -217.1896 | 0 | -123.4852
| 46 | SERVICE MIN | 0.5 | -217.1908 | 0 | -77.7169 | 59 | SERVICE MIN | 1 | -217.1896 | 0 | -205.7416
| 46 | SERVICE MIN | 1 | -217.1908 | 0 | -176.7606 | 60 | SERVICE MAX | 0 | 0 | 0 | 0
| 47 | SERVICE MAX | 0 | 0 | 319.8986 | 0 | 60 | SERVICE MAX | 1 | 0 | 0 | 0
| 47 | SERVICE MAX | 1 | 0 | 348.8486 | 0 | 60 | SERVICE MIN | 0 | -319.0503 | -217.19 | -205.7416
| 47 | SERVICE MIN | 0 | -217.1907 | 0 | -176.7606 | 60 | SERVICE MIN | 1 | -324.1035 | -188.3735 | -129.6567
| 47 | SERVICE MIN | 1 | -217.1907 | 0 | -243.6354 | 61 | SERVICE MAX | 0 | 0 | 0 | 0
| 48 | SERVICE MAX | 0 | 0 | 0 | 0 | 61 | SERVICE MAX | 1 | 0 | 0 | 0
| 48 | SERVICE MAX | 1 | 0 | 0 | 0 | 61 | SERVICE MIN | 0 | -324.1035 | -188.3743 | -129.6567
| 48 | SERVICE MIN | 0 | -218.8409 | -318.443 | -244.3677 | 61 | SERVICE MIN | 1 | -330.4367 | -150.3711 | -52.4106
| 48 | SERVICE MIN | 1 | -218.8409 | -289.493 | -183.5741 | 62 | SERVICE MAX | 0 | 0 | 0 | 0
| 49 | SERVICE MAX | 0 | 0 | 0 | 0 | 62 | SERVICE MAX | 0.25 | 0 | 0 | 43.9431
| 49 | SERVICE MAX | 0.5 | 0 | 0 | 0 | 62 | SERVICE MAX | 0.5 | 0 | 0 | 80.4415
| 49 | SERVICE MAX | 1 | 0 | 0 | 0 | 62 | SERVICE MAX | 0.75 | 0 | 66.1771 | 59.807
| 49 | SERVICE MIN | 0 | -218.8408 | -289.493 | -183.5741 | 62 | SERVICE MAX | 1 | 0 | 149.1997 | 0
| 49 | SERVICE MIN | 0.5 | -218.8408 | -241.0017 | -94.7162 | 62 | SERVICE MIN | 0 | -330.4367 | -150.3745 | -52.4108
| 49 | SERVICE MIN | 1 | -218.8408 | -192.5105 | -22.1029 | 62 | SERVICE MIN | 0.25 | -340.7451 | -84.0302 | -5.9582
| 50 | SERVICE MAX | 0 | 0 | 0 | 0 | 62 | SERVICE MIN | 0.5 | -351.0534 | -12.1264 | 0
| 50 | SERVICE MAX | 0.25 | 0 | 0 | 47.9129 | 62 | SERVICE MIN | 0.75 | -361.3618 | 0 | 0
| 50 | SERVICE MAX | 0.5 | 0 | 0 | 87.9124 | 62 | SERVICE MIN | 1 | -371.6702 | 0 | -33.7593
| FRAME | LOAD | DIST | P | V2 | M3
| 63 | SERVICE MAX | 0 | 0 | 149.1997 | 0
| 63 | SERVICE MAX | 1 | 0 | 202.9644 | 0
| 63 | SERVICE MIN | 0 | -371.6702 | 0 | -33.7593
| 63 | SERVICE MIN | 1 | -378.0034 | 0 | -106.5137
| 64 | SERVICE MAX | 0 | 0 | 202.9644 | 0
| 64 | SERVICE MAX | 1 | 0 | 247.3671 | 0
| 64 | SERVICE MIN | 0 | -378.0034 | 0 | -106.5137
| 64 | SERVICE MIN | 1 | -383.0566 | 0 | -190.5976
| 65 | SERVICE MAX | 0 | 0 | 1.6525 | 3.0713
| 65 | SERVICE MAX | 0.25 | 0 | 1.6525 | 1.1374
| 65 | SERVICE MAX | 0.5 | 0 | 1.6525 | 0
| 65 | SERVICE MAX | 0.75 | 0 | 1.6525 | 0
| 65 | SERVICE MAX | 1 | 0 | 1.6525 | 0
| 65 | SERVICE MIN | 0 | -667.3127 | 0 | 0
| 65 | SERVICE MIN | 0.25 | -678.9502 | 0 | -0.96744
| 65 | SERVICE MIN | 0.5 | -690.5877 | 0 | -2.6727
| 65 | SERVICE MIN | 0.75 | -702.2252 | 0 | -4.3792
| 65 | SERVICE MIN | 1 | -713.8627 | 0 | -6.0867
| 66 | SERVICE MAX | 0 | 0 | 0 | 0
| 66 | SERVICE MAX | 0.25 | 0 | 0 | 0.96996
| 66 | SERVICE MAX | 0.5 | 0 | 0 | 2.6722
| 66 | SERVICE MAX | 0.75 | 0 | 0 | 4.3761
| 66 | SERVICE MAX | 1 | 0 | 0 | 6.081
| 66 | SERVICE MIN | 0 | -667.2916 | -1.6506 | -3.0671
| 66 | SERVICE MIN | 0.25 | -678.9291 | -1.6506 | -1.1356
| 66 | SERVICE MIN | 0.5 | -690.5666 | -1.6506 | 0
| 66 | SERVICE MIN | 0.75 | -702.2041 | -1.6506 | 0
| 66 | SERVICE MIN | 1 | -713.8416 | -1.6506 | 0

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 69.5201 | 0 | 188.363 | 18 | ULTIMATE MAX | 0 | 80.3864 | 0 | 0
| 1 | ULTIMATE MAX | 1 | 68.9715 | 0 | 197.8187 | 18 | ULTIMATE MAX | 0.5 | 80.935 | 0 | 0
| 1 | ULTIMATE MIN | 0 | 0 | -50.7286 | 0 | 18 | ULTIMATE MAX | 1 | 81.4835 | 0 | 0
| 1 | ULTIMATE MIN | 1 | 0 | -55.7817 | 0 | 18 | ULTIMATE MIN | 0 | 0 | -39.6383 | -73.9636
| 2 | ULTIMATE MAX | 0 | 68.4048 | 0 | 197.8175 | 18 | ULTIMATE MIN | 0.5 | 0 | -44.6914 | -62.3682
| 2 | ULTIMATE MAX | 1 | 67.8383 | 0 | 209.2735 | 18 | ULTIMATE MIN | 1 | 0 | -49.7446 | -49.3833
| 2 | ULTIMATE MIN | 0 | 0 | -56.2802 | 0 | 19 | ULTIMATE MAX | 0 | 80.7938 | 49.4568 | 0
| 2 | ULTIMATE MIN | 1 | 0 | -61.4987 | 0 | 19 | ULTIMATE MAX | 0.5 | 81.3424 | 44.4037 | 0
| 3 | ULTIMATE MAX | 0 | 65.6265 | 11.904 | 209.2568 | 19 | ULTIMATE MAX | 1 | 81.8909 | 39.3505 | 0
| 3 | ULTIMATE MAX | 1 | 64.8565 | 4.8112 | 206.0308 | 19 | ULTIMATE MIN | 0 | 0 | 0 | -49.3833
| 3 | ULTIMATE MIN | 0 | 0 | -12.69 | 0 | 19 | ULTIMATE MIN | 0.5 | 0 | 0 | -62.2701
| 3 | ULTIMATE MIN | 1 | 0 | -19.7828 | 0 | 19 | ULTIMATE MIN | 1 | 0 | 0 | -73.7863
| 4 | ULTIMATE MAX | 0 | 64.2888 | 3.992 | 206.0597 | 20 | ULTIMATE MAX | 0 | 81.2093 | 119.5392 | 0
| 4 | ULTIMATE MAX | 1 | 63.9417 | 0.79474 | 205.6433 | 20 | ULTIMATE MAX | 0.5 | 81.7578 | 114.486 | 0
| 4 | ULTIMATE MIN | 0 | 0 | -20.2809 | 0 | 20 | ULTIMATE MAX | 1 | 82.3064 | 109.4329 | 0
| 4 | ULTIMATE MIN | 1 | 0 | -23.4781 | 0 | 20 | ULTIMATE MIN | 0 | 0 | 0 | -73.7863
| 5 | ULTIMATE MAX | 0 | 61.6726 | 57.6528 | 205.5745 | 20 | ULTIMATE MIN | 0.5 | 0 | 0 | -105.9647
| 5 | ULTIMATE MAX | 0.5 | 61.1151 | 52.517 | 190.1782 | 20 | ULTIMATE MIN | 1 | 0 | 0 | -136.7536
| 5 | ULTIMATE MAX | 1 | 61.1904 | 47.3812 | 176.2175 | 21 | ULTIMATE MAX | 0 | 82.2519 | 190.8046 | 0
| 5 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 21 | ULTIMATE MAX | 1 | 82.7106 | 186.5784 | 0
| 5 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 21 | ULTIMATE MIN | 0 | 0 | 0 | -136.6927
| 5 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 21 | ULTIMATE MIN | 1 | 0 | 0 | -180.0918
| 6 | ULTIMATE MAX | 0 | 60.4238 | 106.6464 | 176.2172 | 22 | ULTIMATE MAX | 0 | 81.6466 | 185.7737 | 0
| 6 | ULTIMATE MAX | 0.5 | 60.9823 | 101.5014 | 147.0765 | 22 | ULTIMATE MAX | 1 | 82.2849 | 179.8937 | 0
| 6 | ULTIMATE MAX | 1 | 61.5408 | 96.3564 | 119.3764 | 22 | ULTIMATE MIN | 0 | 0 | 0 | -180.1038
| 6 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 22 | ULTIMATE MIN | 1 | 0 | 0 | -238.6106
| 6 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 0 | 82.4513 | 265.6818 | 0
| 6 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 83.1495 | 259.2505 | 0
| 7 | ULTIMATE MAX | 0 | 60.7804 | 159.3014 | 119.3767 | 23 | ULTIMATE MIN | 0 | 0 | 0 | -238.6155
| 7 | ULTIMATE MAX | 0.5 | 61.3379 | 154.1656 | 75.5697 | 23 | ULTIMATE MIN | 1 | 0 | 0 | -330.4787
| 7 | ULTIMATE MAX | 1 | 61.8954 | 149.0298 | 33.1981 | 24 | ULTIMATE MAX | 0 | 82.0855 | 258.4459 | 0
| 7 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 24 | ULTIMATE MAX | 1 | 82.4844 | 254.7709 | 0
| 7 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 24 | ULTIMATE MIN | 0 | 0 | 0 | -330.4586
| 7 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 24 | ULTIMATE MIN | 1 | 0 | 0 | -381.7802
| 8 | ULTIMATE MAX | 0 | 61.1432 | 216.2083 | 33.1981 | 25 | ULTIMATE MAX | 0 | 63.4695 | 0 | 0
| 8 | ULTIMATE MAX | 0.5 | 61.7007 | 211.0725 | 0 | 25 | ULTIMATE MAX | 1 | 63.0705 | 0 | 0
| 8 | ULTIMATE MAX | 1 | 62.2583 | 205.9366 | 0 | 25 | ULTIMATE MIN | 0 | 0 | -325.4504 | -420.8915
| 8 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 25 | ULTIMATE MIN | 1 | 0 | -329.1254 | -355.4339
| 8 | ULTIMATE MIN | 0.5 | 0 | 0 | -38.5445 | 26 | ULTIMATE MAX | 0 | 62.5038 | 0 | 0
| 8 | ULTIMATE MIN | 1 | 0 | 0 | -90.2436 | 26 | ULTIMATE MAX | 1 | 61.7877 | 0 | 0
| 9 | ULTIMATE MAX | 0 | 62.1121 | 278.5086 | 0 | 26 | ULTIMATE MIN | 0 | 0 | -329.6259 | -355.4472
| 9 | ULTIMATE MAX | 1 | 62.6087 | 273.9332 | 0 | 26 | ULTIMATE MIN | 1 | 0 | -336.2225 | -235.9274
| 9 | ULTIMATE MIN | 0 | 0 | 0 | -90.2063 | 27 | ULTIMATE MAX | 0 | 59.6816 | 0 | 0
| 9 | ULTIMATE MIN | 1 | 0 | 0 | -153.5093 | 27 | ULTIMATE MAX | 1 | 59.0613 | 0 | 0
| 10 | ULTIMATE MAX | 0 | 61.5254 | 273.1139 | 0 | 27 | ULTIMATE MIN | 0 | 0 | -265.2687 | -235.9226
| 10 | ULTIMATE MAX | 1 | 62.1457 | 267.3993 | 0 | 27 | ULTIMATE MIN | 1 | 0 | -270.9833 | -152.5354
| 10 | ULTIMATE MIN | 0 | 0 | 0 | -153.5178 | 28 | ULTIMATE MAX | 0 | 58.4935 | 0 | 0
| 10 | ULTIMATE MIN | 1 | 0 | 0 | -237.5676 | 28 | ULTIMATE MAX | 1 | 57.9969 | 0 | 0
| 11 | ULTIMATE MAX | 0 | 62.2728 | 348.0279 | 0 | 28 | ULTIMATE MIN | 0 | 0 | -271.4847 | -152.5302
| 11 | ULTIMATE MAX | 1 | 62.9889 | 341.4313 | 0 | 28 | ULTIMATE MIN | 1 | 0 | -276.0601 | -89.7863
| 11 | ULTIMATE MIN | 0 | 0 | 0 | -237.5754 | 29 | ULTIMATE MAX | 0 | 55.7569 | 0 | 0
| 11 | ULTIMATE MIN | 1 | 0 | 0 | -361.3334 | 29 | ULTIMATE MAX | 0.5 | 55.1994 | 0 | 0
| 12 | ULTIMATE MAX | 0 | 61.9075 | 340.6135 | 0 | 29 | ULTIMATE MAX | 1 | 54.6419 | 0 | 33.2708
| 12 | ULTIMATE MAX | 1 | 62.3065 | 336.9385 | 0 | 29 | ULTIMATE MIN | 0 | 0 | -205.3635 | -89.8474
| 12 | ULTIMATE MIN | 0 | 0 | 0 | -361.3117 | 29 | ULTIMATE MIN | 0.5 | 0 | -210.4994 | -38.3261
| 12 | ULTIMATE MIN | 1 | 0 | 0 | -429.0669 | 29 | ULTIMATE MIN | 1 | 0 | -215.6352 | 0
| 13 | ULTIMATE MAX | 0 | 89.7565 | 0 | 0 | 30 | ULTIMATE MAX | 0 | 53.3979 | 0 | 33.2707
| 13 | ULTIMATE MAX | 1 | 89.3576 | 0 | 0 | 30 | ULTIMATE MAX | 0.5 | 53.9564 | 0 | 75.6605
| 13 | ULTIMATE MIN | 0 | 0 | -243.9345 | -375.0071 | 30 | ULTIMATE MAX | 1 | 54.5149 | 0 | 119.491
| 13 | ULTIMATE MIN | 1 | 0 | -247.6095 | -325.8527 | 30 | ULTIMATE MIN | 0 | 0 | -148.8198 | 0
| 14 | ULTIMATE MAX | 0 | 88.8 | 0 | 0 | 30 | ULTIMATE MIN | 0.5 | 0 | -153.9648 | 0
| 14 | ULTIMATE MAX | 1 | 88.1018 | 0 | 0 | 30 | ULTIMATE MIN | 1 | 0 | -159.1098 | 0
| 14 | ULTIMATE MIN | 0 | 0 | -248.102 | -325.865 | 31 | ULTIMATE MAX | 0 | 53.8667 | 0 | 119.4911
| 14 | ULTIMATE MIN | 1 | 0 | -254.5332 | -237.9038 | 31 | ULTIMATE MAX | 0.5 | 54.4242 | 0 | 147.1278
| 15 | ULTIMATE MAX | 0 | 85.9612 | 0 | 0 | 31 | ULTIMATE MAX | 1 | 54.9817 | 0 | 176.1999
| 15 | ULTIMATE MAX | 1 | 85.3228 | 0 | 0 | 31 | ULTIMATE MIN | 0 | 0 | -96.311 | 0
| 15 | ULTIMATE MIN | 0 | 0 | -178.368 | -237.9008 | 31 | ULTIMATE MIN | 0.5 | 0 | -101.4468 | 0
| 15 | ULTIMATE MIN | 1 | 0 | -184.248 | -179.8822 | 31 | ULTIMATE MIN | 1 | 0 | -106.5826 | 0
| 16 | ULTIMATE MAX | 0 | 84.7652 | 0 | 0 | 32 | ULTIMATE MAX | 0 | 54.341 | 0 | 176.1999
| 16 | ULTIMATE MAX | 1 | 84.3064 | 0 | 0 | 32 | ULTIMATE MAX | 0.5 | 54.8985 | 0 | 190.1734
| 16 | ULTIMATE MIN | 0 | 0 | -184.7405 | -179.8749 | 32 | ULTIMATE MAX | 1 | 55.456 | 0 | 205.5823
| 16 | ULTIMATE MIN | 1 | 0 | -188.9667 | -136.8985 | 32 | ULTIMATE MIN | 0 | 0 | -47.4267 | 0
| 17 | ULTIMATE MAX | 0 | 82.0627 | 0 | 0 | 32 | ULTIMATE MIN | 0.5 | 0 | -52.5625 | 0
| 17 | ULTIMATE MAX | 0.5 | 81.5141 | 0 | 0 | 32 | ULTIMATE MIN | 1 | 0 | -57.6983 | 0
| 17 | ULTIMATE MAX | 1 | 81.0841 | 0 | 0 | 33 | ULTIMATE MAX | 0 | 55.5657 | 24.7473 | 205.6244
| 17 | ULTIMATE MIN | 0 | 0 | -109.4418 | -136.9358 | 33 | ULTIMATE MAX | 1 | 55.9128 | 21.5501 | 206.1086
| 17 | ULTIMATE MIN | 0.5 | 0 | -114.4949 | -106.1445 | 33 | ULTIMATE MIN | 0 | 0 | -1.1839 | 0
| 17 | ULTIMATE MIN | 1 | 0 | -119.548 | -73.9636 | 33 | ULTIMATE MIN | 1 | 0 | -4.3812 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 34 | ULTIMATE MAX | 0 | 54.8294 | 20.7341 | 206.0909 | 53 | ULTIMATE MAX | 1 | 0 | 0 | 41.142
| 34 | ULTIMATE MAX | 1 | 55.5994 | 13.6413 | 209.3444 | 53 | ULTIMATE MIN | 0 | -161.7636 | -314.9758 | -121.5236
| 34 | ULTIMATE MIN | 0 | 0 | -4.8826 | 0 | 53 | ULTIMATE MIN | 1 | -157.3604 | -259.1023 | -10.7265
| 34 | ULTIMATE MIN | 1 | 0 | -11.9753 | 0 | 54 | ULTIMATE MAX | 0 | 0 | 0 | 39.7649
| 35 | ULTIMATE MAX | 0 | 55.8366 | 67.9931 | 209.3546 | 54 | ULTIMATE MAX | 1 | 0 | 0 | 72.7343
| 35 | ULTIMATE MAX | 1 | 56.4031 | 62.7746 | 198.0529 | 54 | ULTIMATE MIN | 0 | -157.1494 | -219.8043 | -12.115
| 35 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 54 | ULTIMATE MIN | 1 | -155.1646 | -194.6178 | 0
| 35 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 55 | ULTIMATE MAX | 0 | 0 | 0 | 76.008
| 36 | ULTIMATE MAX | 0 | 55.3217 | 61.9568 | 198.0536 | 55 | ULTIMATE MAX | 0.5 | 0 | 0 | 127.4685
| 36 | ULTIMATE MAX | 1 | 55.8702 | 56.9037 | 188.66 | 55 | ULTIMATE MAX | 1 | 0 | 0 | 167.6211
| 36 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 55 | ULTIMATE MIN | 0 | -159.1116 | -222.408 | 0
| 36 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 55 | ULTIMATE MIN | 0.5 | -155.9233 | -181.9503 | 0
| 37 | ULTIMATE MAX | 0 | 0 | 79.037 | 188.6957 | 55 | ULTIMATE MIN | 1 | -152.7349 | -141.4927 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 77.7323 | 159.2613 | 56 | ULTIMATE MAX | 0 | 0 | 0 | 167.6341
| 37 | ULTIMATE MIN | 0 | -171.2278 | 0 | 0 | 56 | ULTIMATE MAX | 0.5 | 0 | 0 | 196.5563
| 37 | ULTIMATE MIN | 1 | -164.8247 | 0 | 0 | 56 | ULTIMATE MAX | 1 | 0 | 0 | 214.1301
| 38 | ULTIMATE MAX | 0 | 0 | 77.7702 | 159.2345 | 56 | ULTIMATE MIN | 0 | -156.5525 | -141.6442 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 76.8716 | 147.4017 | 56 | ULTIMATE MIN | 0.5 | -153.3584 | -101.1142 | 0
| 38 | ULTIMATE MIN | 0 | -161.9122 | 0 | 0 | 56 | ULTIMATE MIN | 1 | -150.1644 | -60.5842 | 0
| 38 | ULTIMATE MIN | 1 | -159.2997 | 0 | 0 | 57 | ULTIMATE MAX | 0 | 0 | 0 | 214.1172
| 39 | ULTIMATE MAX | 0 | 0 | 85.7626 | 147.3565 | 57 | ULTIMATE MAX | 0.5 | 0 | 0 | 220.4013
| 39 | ULTIMATE MAX | 1 | 0 | 83.2369 | 120.5464 | 57 | ULTIMATE MAX | 1 | 0 | 38.2141 | 215.3776
| 39 | ULTIMATE MIN | 0 | -189.1026 | 0 | 0 | 57 | ULTIMATE MIN | 0 | -153.9976 | -60.7831 | 0
| 39 | ULTIMATE MIN | 1 | -183.6898 | 0 | 0 | 57 | ULTIMATE MIN | 0.5 | -150.8093 | -20.3255 | 0
| 40 | ULTIMATE MAX | 0 | 0 | 81.1459 | 120.5595 | 57 | ULTIMATE MIN | 1 | -147.6209 | 0 | 0
| 40 | ULTIMATE MAX | 1 | 0 | 78.9765 | 103.6599 | 58 | ULTIMATE MAX | 0 | 0 | 37.1093 | 215.3776
| 40 | ULTIMATE MIN | 0 | -180.7773 | 0 | 0 | 58 | ULTIMATE MAX | 0.5 | 0 | 77.5669 | 199.3516
| 40 | ULTIMATE MIN | 1 | -177.1745 | 0 | 0 | 58 | ULTIMATE MAX | 1 | 0 | 118.0245 | 172.0177
| 41 | ULTIMATE MAX | 0 | 0 | 90.3649 | 103.3404 | 58 | ULTIMATE MIN | 0 | -151.4699 | 0 | 0
| 41 | ULTIMATE MAX | 0.5 | 0 | 87.1273 | 79.943 | 58 | ULTIMATE MIN | 0.5 | -148.2816 | 0 | 0
| 41 | ULTIMATE MAX | 1 | 0 | 83.3061 | 57.4756 | 58 | ULTIMATE MIN | 1 | -145.0932 | 0 | 0
| 41 | ULTIMATE MIN | 0 | -205.5447 | 0 | 0 | 59 | ULTIMATE MAX | 0 | 0 | 89.9842 | 169.1111
| 41 | ULTIMATE MIN | 0.5 | -201.0454 | 0 | 0 | 59 | ULTIMATE MAX | 1 | 0 | 126.0269 | 142.2177
| 41 | ULTIMATE MIN | 1 | -196.5462 | 0 | 0 | 59 | ULTIMATE MIN | 0 | -149.0741 | 0 | 0
| 42 | ULTIMATE MAX | 0 | 0 | 96.8864 | 57.3043 | 59 | ULTIMATE MIN | 1 | -146.2337 | 0 | 0
| 42 | ULTIMATE MAX | 0.5 | 0 | 92.4863 | 32.2949 | 60 | ULTIMATE MAX | 0 | 0 | 165.0171 | 142.6206
| 42 | ULTIMATE MAX | 1 | 0 | 87.5278 | 8.5207 | 60 | ULTIMATE MAX | 1 | 0 | 210.0343 | 85.5757
| 42 | ULTIMATE MIN | 0 | -223.2177 | 0 | 0 | 60 | ULTIMATE MIN | 0 | -146.0227 | 0 | 0
| 42 | ULTIMATE MIN | 0.5 | -218.7099 | 0 | 0 | 60 | ULTIMATE MIN | 1 | -143.3364 | 0 | 0
| 42 | ULTIMATE MIN | 1 | -214.2021 | 0 | 0 | 61 | ULTIMATE MAX | 0 | 0 | 142.026 | 85.9519
| 43 | ULTIMATE MAX | 0 | 0 | 109.4967 | 8.899 | 61 | ULTIMATE MAX | 1 | 0 | 193.9913 | 30.5609
| 43 | ULTIMATE MAX | 1 | 0 | 103.9902 | 0 | 61 | ULTIMATE MIN | 0 | -146.5228 | 0 | 0
| 43 | ULTIMATE MIN | 0 | -242.3787 | 0 | 0 | 61 | ULTIMATE MIN | 1 | -142.9957 | 0 | 0
| 43 | ULTIMATE MIN | 1 | -237.8709 | 0 | -19.2932 | 62 | ULTIMATE MAX | 0 | 0 | 232.9118 | 29.5213
| 44 | ULTIMATE MAX | 0 | 0 | 95.8937 | 0 | 62 | ULTIMATE MAX | 1 | 0 | 261.8618 | 0
| 44 | ULTIMATE MAX | 1 | 0 | 89.855 | 0 | 62 | ULTIMATE MIN | 0 | -143.0329 | 0 | 0
| 44 | ULTIMATE MIN | 0 | -234.9584 | 0 | -19.3136 | 62 | ULTIMATE MIN | 1 | -145.3143 | 0 | -26.1779
| 44 | ULTIMATE MIN | 1 | -230.4506 | 0 | -43.844 | 63 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 45 | ULTIMATE MAX | 0 | 0 | 116.3351 | 0 | 63 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 45 | ULTIMATE MAX | 0.5 | 0 | 109.7799 | 0 | 63 | ULTIMATE MIN | 0 | -186.3905 | -324.6221 | -106.0405
| 45 | ULTIMATE MAX | 1 | 0 | 102.7187 | 0 | 63 | ULTIMATE MIN | 1 | -184.109 | -295.6721 | -44.0199
| 45 | ULTIMATE MIN | 0 | -258.8484 | 0 | -44.5255 | 64 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 45 | ULTIMATE MIN | 0.5 | -256.2414 | 0 | -74.3838 | 64 | ULTIMATE MAX | 1 | 0 | 0 | 68.7023
| 45 | ULTIMATE MIN | 1 | -253.6344 | 0 | -102.4448 | 64 | ULTIMATE MIN | 0 | -183.9018 | -257.0759 | -43.0553
| 46 | ULTIMATE MAX | 0 | 0 | 128.9266 | 0 | 64 | ULTIMATE MIN | 1 | -179.9093 | -206.4134 | 0
| 46 | ULTIMATE MAX | 0.5 | 0 | 121.3868 | 0 | 65 | ULTIMATE MAX | 0 | 0 | 0 | 68.4691
| 46 | ULTIMATE MAX | 1 | 0 | 113.3682 | 0 | 65 | ULTIMATE MAX | 1 | 0 | 0 | 131.7971
| 46 | ULTIMATE MIN | 0 | -281.7249 | 0 | -102.5871 | 65 | ULTIMATE MIN | 0 | -183.9203 | -241.5011 | 0
| 46 | ULTIMATE MIN | 0.5 | -279.1228 | 0 | -135.5764 | 65 | ULTIMATE MIN | 1 | -180.2699 | -195.1811 | 0
| 46 | ULTIMATE MIN | 1 | -276.5208 | 0 | -166.5159 | 66 | ULTIMATE MAX | 0 | 0 | 0 | 131.2227
| 47 | ULTIMATE MAX | 0 | 0 | 149.916 | 0 | 66 | ULTIMATE MAX | 1 | 0 | 0 | 158.7766
| 47 | ULTIMATE MAX | 1 | 0 | 143.1558 | 0 | 66 | ULTIMATE MIN | 0 | -180.0627 | -156.5848 | 0
| 47 | ULTIMATE MIN | 0 | -306.2839 | 0 | -165.6689 | 66 | ULTIMATE MIN | 1 | -177.4391 | -123.2923 | 0
| 47 | ULTIMATE MIN | 1 | -304.2003 | 0 | -196.5932 | 67 | ULTIMATE MAX | 0 | 0 | 0 | 161.673
| 48 | ULTIMATE MAX | 0 | 0 | 129.8692 | 0 | 67 | ULTIMATE MAX | 0.5 | 0 | 0 | 192.8444
| 48 | ULTIMATE MAX | 1 | 0 | 119.1683 | 0 | 67 | ULTIMATE MAX | 1 | 0 | 0 | 213.069
| 48 | ULTIMATE MIN | 0 | -301.5297 | 0 | -196.8454 | 67 | ULTIMATE MIN | 0 | -181.4265 | -152.4966 | 0
| 48 | ULTIMATE MIN | 1 | -298.3994 | 0 | -236.335 | 67 | ULTIMATE MIN | 0.5 | -178.2895 | -112.6904 | 0
| 49 | ULTIMATE MAX | 0 | 0 | 165.7734 | 0 | 67 | ULTIMATE MIN | 1 | -177.9778 | -72.8841 | 0
| 49 | ULTIMATE MAX | 1 | 0 | 160.3794 | 0 | 68 | ULTIMATE MAX | 0 | 0 | 0 | 213.069
| 49 | ULTIMATE MIN | 0 | -329.5932 | 0 | -236.0074 | 68 | ULTIMATE MAX | 0.5 | 0 | 0 | 224.789
| 49 | ULTIMATE MIN | 1 | -328.0823 | 0 | -260.96 | 68 | ULTIMATE MAX | 1 | 0 | 17.0934 | 226.8248
| 50 | ULTIMATE MAX | 0 | 0 | 145.5885 | 0 | 68 | ULTIMATE MIN | 0 | -179.0369 | -80.9238 | 0
| 50 | ULTIMATE MAX | 1 | 0 | 138.3754 | 0 | 68 | ULTIMATE MIN | 0.5 | -176.845 | -41.1175 | 0
| 50 | ULTIMATE MIN | 0 | -325.4117 | 0 | -261.5242 | 68 | ULTIMATE MIN | 1 | -179.9821 | -1.3113 | 0
| 50 | ULTIMATE MIN | 1 | -321.7086 | 0 | -313.554 | 69 | ULTIMATE MAX | 0 | 0 | 7.9405 | 226.8248
| 51 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 69 | ULTIMATE MAX | 0.5 | 0 | 47.7467 | 224.0693
| 51 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 69 | ULTIMATE MAX | 1 | 0 | 87.553 | 210.3671
| 51 | ULTIMATE MIN | 0 | -164.3963 | -399.593 | -311.9977 | 69 | ULTIMATE MIN | 0 | -176.6647 | -9.888 | 0
| 51 | ULTIMATE MIN | 1 | -161.2593 | -359.7868 | -207.583 | 69 | ULTIMATE MIN | 0.5 | -178.8668 | 0 | 0
| 52 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 69 | ULTIMATE MIN | 1 | -182.0038 | 0 | 0
| 52 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 70 | ULTIMATE MAX | 0 | 0 | 78.9646 | 210.3671
| 52 | ULTIMATE MIN | 0 | -161.0487 | -320.559 | -207.5242 | 70 | ULTIMATE MAX | 0.5 | 0 | 118.7708 | 187.9913
| 52 | ULTIMATE MIN | 1 | -157.809 | -279.45 | -122.3229 | 70 | ULTIMATE MAX | 1 | 0 | 158.5771 | 154.6689
| 53 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 70 | ULTIMATE MIN | 0 | -177.7692 | 0 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 70 | ULTIMATE MIN | 0.5 | -180.9062 | 0 | 0 | 89 | ULTIMATE MIN | 1 | -339.4619 | -146.829 | -200.8397
| 70 | ULTIMATE MIN | 1 | -184.0432 | 0 | 0 | 90 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 71 | ULTIMATE MAX | 0 | 0 | 129.0129 | 151.7496 | 90 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 71 | ULTIMATE MAX | 1 | 0 | 162.3054 | 122.2899 | 90 | ULTIMATE MIN | 0 | -337.6824 | -144.3494 | -200.8885
| 71 | ULTIMATE MIN | 0 | -179.8052 | 0 | 0 | 90 | ULTIMATE MIN | 1 | -339.766 | -151.1096 | -169.7124
| 71 | ULTIMATE MIN | 1 | -182.4289 | 0 | 0 | 91 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 72 | ULTIMATE MAX | 0 | 0 | 200.5993 | 122.8689 | 91 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 72 | ULTIMATE MAX | 1 | 0 | 246.9193 | 56.7927 | 91 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 72 | ULTIMATE MIN | 0 | -182.4655 | 0 | 0 | 91 | ULTIMATE MIN | 0 | -303.706 | -119.6446 | -169.5673
| 72 | ULTIMATE MIN | 1 | -186.1158 | 0 | 0 | 91 | ULTIMATE MIN | 0.5 | -306.3081 | -127.6632 | -136.974
| 73 | ULTIMATE MAX | 0 | 0 | 211.5161 | 57.0278 | 91 | ULTIMATE MIN | 1 | -308.9101 | -135.2029 | -102.3309
| 73 | ULTIMATE MAX | 1 | 0 | 262.1786 | 0 | 92 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 73 | ULTIMATE MIN | 0 | -181.8885 | 0 | 0 | 92 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 73 | ULTIMATE MIN | 1 | -185.8811 | 0 | -56.1219 | 92 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 74 | ULTIMATE MAX | 0 | 0 | 300.4725 | 0 | 92 | ULTIMATE MIN | 0 | -271.8578 | -105.4456 | -102.372
| 74 | ULTIMATE MAX | 1 | 0 | 329.4225 | 0 | 92 | ULTIMATE MIN | 0.5 | -275.533 | -112.5068 | -73.5912
| 74 | ULTIMATE MIN | 0 | -185.9177 | 0 | -57.0788 | 92 | ULTIMATE MIN | 1 | -280.0408 | -119.062 | -43.0129
| 74 | ULTIMATE MIN | 1 | -188.1992 | 0 | -120.0591 | 93 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 75 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 93 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 75 | ULTIMATE MAX | 1 | 0 | 0 | 7.1281 | 93 | ULTIMATE MIN | 0 | -244.405 | -94.6496 | -43.1208
| 75 | ULTIMATE MIN | 0 | -163.404 | -316.3506 | -61.083 | 93 | ULTIMATE MIN | 1 | -248.9128 | -100.6883 | -17.3254
| 75 | ULTIMATE MIN | 1 | -165.6855 | -287.4006 | -0.71576 | 94 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 76 | ULTIMATE MAX | 0 | 0 | 0 | 8.1594 | 94 | ULTIMATE MAX | 1 | 0 | 0 | 9.7269
| 76 | ULTIMATE MAX | 1 | 0 | 0 | 81.7232 | 94 | ULTIMATE MIN | 0 | -246.9356 | -99.692 | -17.3313
| 76 | ULTIMATE MIN | 0 | -165.7226 | -248.1728 | 0 | 94 | ULTIMATE MIN | 1 | -251.4434 | -105.1985 | 0
| 76 | ULTIMATE MIN | 1 | -169.8179 | -196.2076 | 0 | 95 | ULTIMATE MAX | 0 | 0 | 0 | 9.7479
| 77 | ULTIMATE MAX | 0 | 0 | 0 | 81.35 | 95 | ULTIMATE MAX | 0.5 | 0 | 0 | 33.212
| 77 | ULTIMATE MAX | 1 | 0 | 0 | 144.1955 | 95 | ULTIMATE MAX | 1 | 0 | 0 | 57.9114
| 77 | ULTIMATE MIN | 0 | -165.5563 | -229.7802 | 0 | 95 | ULTIMATE MIN | 0 | -215.8694 | -86.3532 | 0
| 77 | ULTIMATE MIN | 1 | -169.1039 | -184.7629 | 0 | 95 | ULTIMATE MIN | 0.5 | -220.3772 | -91.3117 | 0
| 78 | ULTIMATE MAX | 0 | 0 | 0 | 143.7894 | 95 | ULTIMATE MIN | 1 | -224.885 | -95.7117 | 0
| 78 | ULTIMATE MAX | 1 | 0 | 0 | 175.5229 | 96 | ULTIMATE MAX | 0 | 0 | 0 | 57.8627
| 78 | ULTIMATE MIN | 0 | -169.1412 | -145.465 | 0 | 96 | ULTIMATE MAX | 0.5 | 0 | 0 | 79.947
| 78 | ULTIMATE MIN | 1 | -171.9816 | -109.4222 | 0 | 96 | ULTIMATE MAX | 1 | 0 | 0 | 102.9614
| 79 | ULTIMATE MAX | 0 | 0 | 0 | 178.4524 | 96 | ULTIMATE MIN | 0 | -188.3809 | -81.8523 | 0
| 79 | ULTIMATE MAX | 0.5 | 0 | 0 | 209.5389 | 96 | ULTIMATE MIN | 0.5 | -192.8802 | -85.6735 | 0
| 79 | ULTIMATE MAX | 1 | 0 | 0 | 229.3176 | 96 | ULTIMATE MIN | 1 | -197.3794 | -88.9111 | 0
| 79 | ULTIMATE MIN | 0 | -167.7464 | -131.4507 | 0 | 97 | ULTIMATE MAX | 0 | 0 | 0 | 102.9673
| 79 | ULTIMATE MIN | 0.5 | -170.9348 | -90.993 | 0 | 97 | ULTIMATE MAX | 1 | 0 | 0 | 119.9227
| 79 | ULTIMATE MIN | 1 | -174.1231 | -50.5354 | 0 | 97 | ULTIMATE MIN | 0 | -162.1103 | -79.2413 | 0
| 80 | ULTIMATE MAX | 0 | 0 | 0 | 229.3176 | 97 | ULTIMATE MIN | 1 | -165.7131 | -81.4107 | 0
| 80 | ULTIMATE MAX | 0.5 | 0 | 9.7884 | 237.1482 | 98 | ULTIMATE MAX | 0 | 0 | 0 | 119.9031
| 80 | ULTIMATE MAX | 1 | 0 | 50.246 | 233.671 | 98 | ULTIMATE MAX | 1 | 0 | 0 | 146.3645
| 80 | ULTIMATE MIN | 0 | -169.926 | -48.2524 | 0 | 98 | ULTIMATE MIN | 0 | -163.7359 | -82.1368 | 0
| 80 | ULTIMATE MIN | 0.5 | -173.1143 | -7.7948 | 0 | 98 | ULTIMATE MIN | 1 | -169.1487 | -84.6625 | 0
| 80 | ULTIMATE MIN | 1 | -176.3027 | 0 | 0 | 99 | ULTIMATE MAX | 0 | 0 | 0 | 146.3838
| 81 | ULTIMATE MAX | 0 | 0 | 56.0059 | 233.6841 | 99 | ULTIMATE MAX | 1 | 0 | 0 | 158.2761
| 81 | ULTIMATE MAX | 0.5 | 0 | 96.5359 | 217.2333 | 99 | ULTIMATE MIN | 0 | -134.9243 | -77.2609 | 0
| 81 | ULTIMATE MAX | 1 | 0 | 137.0659 | 189.4342 | 99 | ULTIMATE MIN | 1 | -137.5368 | -78.1594 | 0
| 81 | ULTIMATE MIN | 0 | -172.1233 | 0 | 0 | 100 | ULTIMATE MAX | 0 | 0 | 0 | 158.2193
| 81 | ULTIMATE MIN | 0.5 | -175.3173 | 0 | 0 | 100 | ULTIMATE MAX | 1 | 0 | 0 | 188.3155
| 81 | ULTIMATE MIN | 1 | -178.5114 | 0 | 0 | 100 | ULTIMATE MIN | 0 | -135.5596 | -79.4971 | 0
| 82 | ULTIMATE MAX | 0 | 0 | 147.0037 | 189.4211 | 100 | ULTIMATE MIN | 1 | -141.9627 | -80.8019 | 0
| 82 | ULTIMATE MAX | 0.5 | 0 | 187.4613 | 147.5037 | 101 | ULTIMATE MAX | 0 | 0 | 32.404 | 79.6484
| 82 | ULTIMATE MAX | 1 | 0 | 227.9189 | 94.2784 | 101 | ULTIMATE MAX | 0.25 | 0 | 34.0435 | 40.1919
| 82 | ULTIMATE MIN | 0 | -174.3499 | 0 | 0 | 101 | ULTIMATE MAX | 0.5 | 0 | 35.6497 | 0
| 82 | ULTIMATE MIN | 0.5 | -177.5382 | 0 | 0 | 101 | ULTIMATE MAX | 0.75 | 0 | 37.2228 | 0
| 82 | ULTIMATE MIN | 1 | -180.7266 | 0 | 0 | 101 | ULTIMATE MAX | 1 | 0 | 38.7628 | 0
| 83 | ULTIMATE MAX | 0 | 0 | 215.7674 | 90.9778 | 101 | ULTIMATE MIN | 0 | -579.008 | 0 | 0
| 83 | ULTIMATE MAX | 1 | 0 | 240.9539 | 54.1797 | 101 | ULTIMATE MIN | 0.25 | -590.6455 | 0 | 0
| 83 | ULTIMATE MIN | 0 | -176.5575 | 0 | 0 | 101 | ULTIMATE MIN | 0.5 | -602.283 | 0 | -3.7518
| 83 | ULTIMATE MIN | 1 | -178.5424 | 0 | 0 | 101 | ULTIMATE MIN | 0.75 | -613.9205 | 0 | -44.463
| 84 | ULTIMATE MAX | 0 | 0 | 279.944 | 55.568 | 101 | ULTIMATE MIN | 1 | -625.558 | 0 | -89.5827
| 84 | ULTIMATE MAX | 1 | 0 | 335.8175 | 0 | 102 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 84 | ULTIMATE MIN | 0 | -178.5796 | 0 | 0 | 102 | ULTIMATE MAX | 0.25 | 0 | 0 | 0
| 84 | ULTIMATE MIN | 1 | -182.9829 | 0 | -113.4644 | 102 | ULTIMATE MAX | 0.5 | 0 | 0 | 3.5344
| 85 | ULTIMATE MAX | 0 | 0 | 324.3096 | 0 | 102 | ULTIMATE MAX | 0.75 | 0 | 0 | 44.982
| 85 | ULTIMATE MAX | 1 | 0 | 365.4186 | 0 | 102 | ULTIMATE MAX | 1 | 0 | 0 | 90.8892
| 85 | ULTIMATE MIN | 0 | -178.828 | 0 | -114.2574 | 102 | ULTIMATE MIN | 0 | -590.0572 | -33.0672 | -81.4919
| 85 | ULTIMATE MIN | 1 | -182.0677 | 0 | -212.1988 | 102 | ULTIMATE MIN | 0.25 | -601.6947 | -34.7066 | -41.2479
| 86 | ULTIMATE MAX | 0 | 0 | 404.3391 | 0 | 102 | ULTIMATE MIN | 0.5 | -613.3322 | -36.3129 | 0
| 86 | ULTIMATE MAX | 1 | 0 | 444.1454 | 0 | 102 | ULTIMATE MIN | 0.75 | -624.9697 | -37.886 | 0
| 86 | ULTIMATE MIN | 0 | -182.1049 | 0 | -212.2572 | 102 | ULTIMATE MIN | 1 | -636.6072 | -39.4259 | 0
| 86 | ULTIMATE MIN | 1 | -185.2419 | 0 | -328.9238
| 87 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 87 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 87 | ULTIMATE MIN | 0 | -368.138 | -164.8595 | -329.668
| 87 | ULTIMATE MIN | 1 | -371.8411 | -164.0337 | -270.7213
| 88 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 88 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 88 | ULTIMATE MIN | 0 | -370.0615 | -161.1256 | -270.8338
| 88 | ULTIMATE MIN | 1 | -371.5724 | -166.5196 | -245.767
| 89 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 89 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 89 | ULTIMATE MIN | 0 | -336.3316 | -138.1006 | -245.7055

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 322.978 | 282.905 | 347.609 | 205.742 | 1000 | 866.667
|  | 제 1경간 중앙부 | 270.668 | - | 347.608 | 175.635 | 1000 | 750
|  | 제 1경간 지점부 | 380.428 | 345.84 | 350.195 | 244.399 | 1000 | 866.667
|  | 제 2경간 중앙부 | 184.67 | - | 350.195 | 119.907 | 1000 | 750
|  | 제 2경간 지점부 | 380.389 | 345.831 | 350.196 | 244.368 | 1000 | 866.667
|  | 제 3경간 중앙부 | 270.678 | - | 347.611 | 175.643 | 1000 | 750
|  | 단지점부(우측) | 322.989 | 282.914 | 347.612 | 205.75 | 1000 | 866.667
| 하부슬래브 | 단지점부(좌측) | 306.664 | 306.874 | 396.124 | 190.598 | 1000 | 750
|  | 제 1경간 중앙부 | 277.76 | - | 396.124 | 179.778 | 1000 | 750
|  | 제 1경간 지점부 | 419.743 | 377.247 | 396.124 | 271.696 | 1000 | 750
|  | 제 2경간 중앙부 | 174.601 | - | 393.94 | 110.809 | 1000 | 750
|  | 제 2경간 지점부 | 419.758 | 377.213 | 396.12 | 271.707 | 1000 | 750
|  | 제 3경간 중앙부 | 277.794 | - | 396.12 | 179.799 | 1000 | 750
|  | 단지점부(우측) | 306.657 | 306.893 | 396.12 | 190.592 | 1000 | 750
| 좌측벽체 | 상부 | 322.978 | 240.705 | 494.821 | 205.742 | 1000 | 666.667
|  | 중앙부 | 133.52 | - | 533.225 | 80.441 | 1000 | 550
|  | 중앙부(부모멘트) | -79.059 | - | 533.225 | -52.411 | 1000 | 550 | 부모멘트
|  | 하부 | 306.664 | 239.056 | 571.628 | 190.598 | 1000 | 550
| 우측벽체 | 상부 | 322.989 | 240.709 | 494.83 | 205.75 | 1000 | 666.667
|  | 중앙부 | 133.519 | - | 533.234 | 80.441 | 1000 | 550
|  | 중앙부(부모멘트) | -79.066 | - | 533.234 | -52.416 | 1000 | 550 | 부모멘트
|  | 하부 | 306.657 | 239.053 | 571.637 | 190.592 | 1000 | 550

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 328.924 | 240.954 | 185.242 | 1000 | 866.667
|  | 제 1경간 중앙부 | 237.148 | - | 173.114 | 1000 | 750
|  | 제 1경간 지점부 | 120.059 | 162.305 | 188.199 | 1000 | 866.667
|  | 제 2경간 중앙부 | 226.825 | - | 176.665 | 1000 | 750
|  | 제 2경간 지점부 | 106.04 | 156.585 | 186.39 | 1000 | 866.667
|  | 제 3경간 중앙부 | 220.401 | - | 150.809 | 1000 | 750
|  | 단지점부(우측) | 311.998 | 219.804 | 164.396 | 1000 | 866.667
| 하부슬래브 | 단지점부(좌측) | 0 | 20.281 | 69.52 | 1000 | 750
|  | 제 1경간 중앙부 | 206.06 | - | 64.289 | 1000 | 750
|  | 제 1경간 지점부 | 429.067 | 273.933 | 89.757 | 1000 | 750
|  | 제 2경간 중앙부 | - | - | - | 1000 | 750
|  | 제 2경간 지점부 | 420.892 | 271.485 | 82.484 | 1000 | 750
|  | 제 3경간 중앙부 | 206.109 | - | 55.913 | 1000 | 750
|  | 단지점부(우측) | 0 | 21.55 | 55.87 | 1000 | 750
| 좌측벽체 | 상부 | 329.668 | 144.349 | 368.138 | 1000 | 666.667
|  | 중앙부 | 146.364 | - | 169.149 | 1000 | 550
|  | 중앙부(부모멘트) | -245.705 | - | 169.149 | 1000 | 550 | 부모멘트
|  | 하부 | 0 | 81.411 | 141.963 | 1000 | 550
| 우측벽체 | 상부 | 313.554 | 143.156 | 321.709 | 1000 | 666.667
|  | 중앙부 | 147.357 | - | 189.103 | 1000 | 550
|  | 중앙부(부모멘트) | -236.335 | - | 189.103 | 1000 | 550 | 부모멘트
|  | 하부 | 0 | 81.146 | 171.228 | 1000 | 550

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 786.667 | 328.924 | 506.442 |  | 1249.224 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.54
상부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 660 | 270.668 | 422.875 |  | 1228.609 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.562
상부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 786.667 | 380.428 | 506.442 |  | 1448.486 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.331
상부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 660 | 226.825 | 348.112 |  | 1026.457 | H16 - 8.0EA |  |  | 1588.8 | 1.535
상부슬래브 : 제 3경간 지점부 |  |  |  | 1000 |  | 786.667 | 380.389 | 506.442 |  | 1448.333 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.331
상부슬래브 : 제 3경간 중앙부 |  |  |  | 1000 |  | 660 | 270.678 | 422.875 |  | 1228.652 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.562
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 786.667 | 322.989 | 506.442 |  | 1226.328 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.568
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 670 | 306.664 | 429.473 |  | 1373.815 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.4
하부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 660 | 277.76 | 422.875 |  | 1261.426 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.522
하부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 670 | 429.067 | 589.585 |  | 1938.512 | H22 - 4.0EA + H19 - 4.0EA |  |  | 2694.4 | 1.374
하부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 660 | 174.601 | 348.112 |  | 787.286 | H16 - 8.0EA |  |  | 1588.8 | 1.994
하부슬래브 : 제 3경간 지점부 |  |  |  | 1000 |  | 670 | 420.892 | 589.585 |  | 1900.487 | H22 - 4.0EA + H19 - 4.0EA |  |  | 2694.4 | 1.401
하부슬래브 : 제 3경간 중앙부 |  |  |  | 1000 |  | 660 | 277.794 | 422.875 |  | 1261.584 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.522
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 670 | 306.657 | 429.473 |  | 1373.785 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.4
좌측벽체 : 상부 |  |  |  | 1000 |  | 586.667 | 329.668 | 585.623 |  | - | H19 - 4.0EA + H16 - 4.0EA |  |  | - | 1.776
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 460 | 146.364 | 561.719 |  | - | H19 - 4.0EA |  |  | - | 3.838
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 470 | 245.705 | 326.279 |  | - | H19 - 4.0EA |  |  | - | 1.328
좌측벽체 : 하부 |  |  |  | 1000 |  | 470 | 306.664 | 458.362 |  | - | H19 - 4.0EA + H16 - 4.0EA |  |  | - | 1.495
우측벽체 : 상부 |  |  |  | 1000 |  | 586.667 | 322.989 | 592.939 |  | - | H19 - 4.0EA + H16 - 4.0EA |  |  | - | 1.836
우측벽체 : 중앙부 |  |  |  | 1000 |  | 460 | 147.357 | 557.438 |  | - | H19 - 4.0EA |  |  | - | 3.783
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 470 | 236.335 | 331.859 |  | - | H19 - 4.0EA |  |  | - | 1.404
우측벽체 : 하부 |  |  |  | 1000 |  | 470 | 306.657 | 458.369 |  | - | H19 - 4.0EA + H16 - 4.0EA |  |  | - | 1.495
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 410.29 |  | 282.905 | 410.29 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 1경간 중앙부 |  |  |  | 404.166 |  | - | 404.166 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 지점부 |  |  |  | 410.29 |  | 345.84 | 410.29 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 중앙부 |  |  |  | 404.166 |  | - | 404.166 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 3경간 지점부 |  |  |  | 410.29 |  | 345.831 | 410.29 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 3경간 중앙부 |  |  |  | 404.166 |  | - | 404.166 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 410.29 |  | 282.914 | 410.29 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 410.29 |  | 306.874 | 410.29 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 1경간 중앙부 |  |  |  | 404.166 |  | - | 404.166 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 지점부 |  |  |  | 410.29 |  | 377.247 | 410.29 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 중앙부 |  |  |  | 404.166 |  | - | 404.166 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 3경간 지점부 |  |  |  | 410.29 |  | 377.213 | 410.29 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 3경간 중앙부 |  |  |  | 404.166 |  | - | 404.166 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 410.29 |  | 306.893 | 410.29 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 306.311 |  | 240.705 | 306.311 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 301.198 |  | - | 301.198 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 309.182 |  | 239.056 | 309.182 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 306.311 |  | 240.709 | 306.311 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 301.199 |  | - | 301.199 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 309.182 |  | 239.053 | 309.182 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 866.667 |  | 786.667 |  | 80 |  | 328.924 |  | 282.905
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (786.67 - 44.761) / 44.761 = 0.0497
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1249.224 mm²
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00247
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (786.67 - a/2) = 506.442 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 328.924 kN.m) ∴ O.K [안전률 1.540]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 282.905 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 660 |  | 90 |  | 270.668 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (660.00 - 44.761) / 44.761 = 0.0412
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1228.609 mm²
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00294
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (660.00 - a/2) = 422.875 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 270.668 kN.m) ∴ O.K [안전률 1.562]
＊ 전단에 대한 검토 (d = 660.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 660.00 = 404.166 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 866.667 |  | 786.667 |  | 80 |  | 380.428 |  | 345.84
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (786.67 - 44.761) / 44.761 = 0.0497
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1448.486 mm²
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00247
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (786.67 - a/2) = 506.442 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 380.428 kN.m) ∴ O.K [안전률 1.331]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 345.840 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 660 |  | 90 |  | 226.825 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (660.00 - 36.651) / 36.651 = 0.0510
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1026.457 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00241
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (660.00 - a/2) = 348.112 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 226.825 kN.m) ∴ O.K [안전률 1.535]
＊ 전단에 대한 검토 (d = 660.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 660.00 = 404.166 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 3경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 866.667 |  | 786.667 |  | 80 |  | 380.389 |  | 345.831
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (786.67 - 44.761) / 44.761 = 0.0497
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1448.333 mm²
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00247
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (786.67 - a/2) = 506.442 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 380.389 kN.m) ∴ O.K [안전률 1.331]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 345.831 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 3경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 660 |  | 90 |  | 270.678 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (660.00 - 44.761) / 44.761 = 0.0412
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1228.652 mm²
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00294
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (660.00 - a/2) = 422.875 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 270.678 kN.m) ∴ O.K [안전률 1.562]
＊ 전단에 대한 검토 (d = 660.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 660.00 = 404.166 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 866.667 |  | 786.667 |  | 80 |  | 322.989 |  | 282.914
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (786.67 - 44.761) / 44.761 = 0.0497
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1226.328 mm²
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00247
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (786.67 - a/2) = 506.442 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 322.989 kN.m) ∴ O.K [안전률 1.568]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 282.914 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 670 |  | 80 |  | 306.664 |  | 306.874
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (670.00 - 44.761) / 44.761 = 0.0419
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1373.815 mm²
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00290
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (670.00 - a/2) = 429.473 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 306.664 kN.m) ∴ O.K [안전률 1.400]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 306.874 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 660 |  | 90 |  | 277.76 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (660.00 - 44.761) / 44.761 = 0.0412
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1261.426 mm²
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00294
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (660.00 - a/2) = 422.875 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 277.760 kN.m) ∴ O.K [안전률 1.522]
＊ 전단에 대한 검토 (d = 660.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 660.00 = 404.166 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 670 |  | 80 |  | 429.067 |  | 377.247
＊ 강도감소계수(Φ) 산정
T = As x fy = 2694.400 x 400.00 = 1077760.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 52.831 mm, c = 52.831 / β1 = 52.831 / 0.85 = 62.155 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (670.00 - 62.155) / 62.155 = 0.0293
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1938.512 mm²
Use As = 2694.400 mm² (철근도심 : 80.000 mm)
1단 : H22 - 4.0 EA + H19 - 4.0 EA (= 2694.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00402
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 2694.400 x 400 x (670.00 - a/2) = 589.585 kN.m
; a = As x fy / (0.85 x fck x b) = 52.831 mm
≥ Mu (= 429.067 kN.m) ∴ O.K [안전률 1.374]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 377.247 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 660 |  | 90 |  | 174.601 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (660.00 - 36.651) / 36.651 = 0.0510
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 787.286 mm²
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00241
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (660.00 - a/2) = 348.112 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 174.601 kN.m) ∴ O.K [안전률 1.994]
＊ 전단에 대한 검토 (d = 660.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 660.00 = 404.166 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 3경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 670 |  | 80 |  | 420.892 |  | 377.213
＊ 강도감소계수(Φ) 산정
T = As x fy = 2694.400 x 400.00 = 1077760.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 52.831 mm, c = 52.831 / β1 = 52.831 / 0.85 = 62.155 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (670.00 - 62.155) / 62.155 = 0.0293
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1900.487 mm²
Use As = 2694.400 mm² (철근도심 : 80.000 mm)
1단 : H22 - 4.0 EA + H19 - 4.0 EA (= 2694.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00402
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 2694.400 x 400 x (670.00 - a/2) = 589.585 kN.m
; a = As x fy / (0.85 x fck x b) = 52.831 mm
≥ Mu (= 420.892 kN.m) ∴ O.K [안전률 1.401]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 377.213 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 3경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 660 |  | 90 |  | 277.794 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (660.00 - 44.761) / 44.761 = 0.0412
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1261.584 mm²
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00294
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (660.00 - a/2) = 422.875 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 277.794 kN.m) ∴ O.K [안전률 1.522]
＊ 전단에 대한 검토 (d = 660.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 660.00 = 404.166 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 750 |  | 670 |  | 80 |  | 306.657 |  | 306.893
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (670.00 - 44.761) / 44.761 = 0.0419
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1373.785 mm²
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00290
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (670.00 - a/2) = 429.473 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 306.657 kN.m) ∴ O.K [안전률 1.400]
＊ 전단에 대한 검토 (d = 670.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 670.00 = 410.290 kN
≥ Vu (= 306.893 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 666.667 |  | 586.667 |  | 494.821 |  | 329.668 |  | 240.705 |  | 666.237
＊ 철근비 검토
As = 1940.400 mm² (인장중심 = 80.00 mm) , 1단 : H19- 4.0EA + H16- 4.0EA , d1 = 80.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0046) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 666.7 x 1000.0 = 13600000.0 N
Cs = As x fy = 776160.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (13600000.0 x 333.33 + 776160.0 x 80.000 + 458400.0 x 576.667) / 14834560.0
= 327.598 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 352.000 mm, ab = k1 x cb = 299.200 mm
fs' = 600 x (352.000 - 90.000) / 352.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 299.200 x 1000.000 = 6103.680 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 776.160 kN
Pb = 6103.680 + 435.022 - 776.160 = 5762.542 kN
Mb = 6103.680 x (586.667 - 299.200/2) + 435.022 x (586.667 - 90.00)
- 5762.542 x (327.598 - 80.000)
= 1456.983 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 252.837 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 105.119 mm, a = k1 x c = 89.351 mm 를 사용.
fs = 600 x (586.667 - 105.119) / 105.119 (≤fy) = 400.000 MPa
fs' = 600 x (105.119 - 90.000) / 105.119 (≤fy) = 86.298 MPa
Cc = 0.85 x 24.0 x 89.351 x 1000.000 = 1822.769 kN
Cs = As' x (fs' - 0.85 x fck) = 75.519 kN
Ts = As x fs = 776.160 kN
Pn = 1822.769 + 75.519 - 776.160 = 1122.129 kN
Mn' = 1822.769 x (586.667 - 89.351/2) + 75.519 x (586.667 - 90.00)
= 1025.432 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0072 ＜ 0.0100 (e' = e + Xp - dc = 913.835 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 80.00 = 470.000 mm
c = 600.00 / (600.00+400.00) x 470.000 = 282.000 mm, a = k1 x c = 239.700 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (470.00-282.00) / 282.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 11817.278 kN ≥ Pn = 1122.129 kN
ΦPn = 0.78 x 1122.129 = 879.001 kN ≥ Pu = 494.821 kN ∴ O.K
ΦMn = ΦPn x 0.666 = 585.623 kN.m ≥ Mu = 329.668 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 470.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 470.00 = 306.311 kN
≥ Vu (= 240.705 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 460 |  | 533.225 |  | 146.364 |  | 0 |  | 274.489
＊ 철근비 검토
As = 1146.000 mm² (인장중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Asf = 1146.000 mm² (압축중심 = 80.00 mm) , 1단 : H19- 4.0EA , d1 = 80.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0042) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 458400.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (11220000.0 x 275.00 + 458400.0 x 90.000 + 458400.0 x 470.000) / 12136800.0
= 275.378 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 276.000 mm, ab = k1 x cb = 234.600 mm
fs' = 600 x (276.000 - 80.000) / 276.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 234.600 x 1000.000 = 4785.840 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 458.400 kN
Pb = 4785.840 + 435.022 - 458.400 = 4762.462 kN
Mb = 4785.840 x (460.000 - 234.600/2) + 435.022 x (460.000 - 80.00)
- 4762.462 x (275.378 - 90.000)
= 922.561 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 193.715 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 158.771 mm, a = k1 x c = 134.955 mm 를 사용.
fs = 600 x (460.000 - 158.771) / 158.771 (≤fy) = 400.000 MPa
fs' = 600 x (158.771 - 80.000) / 158.771 (≤fy) = 297.677 MPa
Cc = 0.85 x 24.0 x 134.955 x 1000.000 = 2753.085 kN
Cs = As' x (fs' - 0.85 x fck) = 317.760 kN
Ts = As x fs = 458.400 kN
Pn = 2753.085 + 317.760 - 458.400 = 2612.445 kN
Mn' = 2753.085 x (460.000 - 134.955/2) + 317.760 x (460.000 - 80.00)
= 1201.396 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0073 ＜ 0.0100 (e' = e + Xp - dc = 459.867 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 90.00 = 460.000 mm
c = 600.00 / (600.00+400.00) x 460.000 = 276.000 mm, a = k1 x c = 234.600 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (460.00-276.00) / 276.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9672.035 kN ≥ Pn = 2612.445 kN
ΦPn = 0.78 x 2612.445 = 2046.415 kN ≥ Pu = 533.225 kN ∴ O.K
ΦMn = ΦPn x 0.274 = 561.719 kN.m ≥ Mu = 146.364 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 460.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 460.00 = 301.198 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 470 |  | 533.225 |  | 245.705 |  | 0 |  | 460.792
＊ 철근비 검토
As = 1146.000 mm² (인장중심 = 80.00 mm) , 1단 : H19- 4.0EA , d1 = 80.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0042) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 458400.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (11220000.0 x 275.00 + 458400.0 x 80.000 + 458400.0 x 460.000) / 12136800.0
= 274.622 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 282.000 mm, ab = k1 x cb = 239.700 mm
fs' = 600 x (282.000 - 90.000) / 282.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 239.700 x 1000.000 = 4889.880 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 458.400 kN
Pb = 4889.880 + 435.022 - 458.400 = 4866.502 kN
Mb = 4889.880 x (470.000 - 239.700/2) + 435.022 x (470.000 - 90.00)
- 4866.502 x (274.622 - 80.000)
= 930.370 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 191.178 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 78.393 mm, a = k1 x c = 66.634 mm 를 사용.
fs = 600 x (470.000 - 78.393) / 78.393 (≤fy) = 400.000 MPa
fs' = 600 x ( 78.393 - 90.000) / 78.393 (≤fy) = 17.784 MPa
Cc = 0.85 x 24.0 x 66.634 x 1000.000 = 1359.336 kN
Cs = As' x (fs' - 0.85 x fck) = -2.999 kN
Ts = As x fs = 458.400 kN
Pn = 1359.336 + -2.999 - 458.400 = 903.935 kN
Mn' = 1359.336 x (470.000 - 66.634/2) + -2.999 x (470.000 - 90.00)
= 592.460 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0087 ＜ 0.0100 (e' = e + Xp - dc = 655.414 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 80.00 = 470.000 mm
c = 600.00 / (600.00+400.00) x 470.000 = 282.000 mm, a = k1 x c = 239.700 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (470.00-282.00) / 282.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9672.035 kN ≥ Pn = 903.935 kN
ΦPn = 0.78 x 903.935 = 708.082 kN ≥ Pu = 533.225 kN ∴ O.K
ΦMn = ΦPn x 0.461 = 326.279 kN.m ≥ Mu = 245.705 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 470.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 470.00 = 307.746 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 470 |  | 571.628 |  | 306.664 |  | 239.056 |  | 536.474
＊ 철근비 검토
As = 1940.400 mm² (인장중심 = 80.00 mm) , 1단 : H19- 4.0EA + H16- 4.0EA , d1 = 80.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0056) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 776160.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (11220000.0 x 275.00 + 776160.0 x 80.000 + 458400.0 x 460.000) / 12454560.0
= 269.657 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 282.000 mm, ab = k1 x cb = 239.700 mm
fs' = 600 x (282.000 - 90.000) / 282.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 239.700 x 1000.000 = 4889.880 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 776.160 kN
Pb = 4889.880 + 435.022 - 776.160 = 4548.742 kN
Mb = 4889.880 x (470.000 - 239.700/2) + 435.022 x (470.000 - 90.00)
- 4548.742 x (269.657 - 80.000)
= 1014.800 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 223.095 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 103.755 mm, a = k1 x c = 88.191 mm 를 사용.
fs = 600 x (470.000 - 103.755) / 103.755 (≤fy) = 400.000 MPa
fs' = 600 x (103.755 - 90.000) / 103.755 (≤fy) = 79.541 MPa
Cc = 0.85 x 24.0 x 88.191 x 1000.000 = 1799.103 kN
Cs = As' x (fs' - 0.85 x fck) = 67.775 kN
Ts = As x fs = 776.160 kN
Pn = 1799.103 + 67.775 - 776.160 = 1090.719 kN
Mn' = 1799.103 x (470.000 - 88.191/2) + 67.775 x (470.000 - 90.00)
= 792.001 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0037 ＜ 0.0100 (e' = e + Xp - dc = 726.131 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 80.00 = 470.000 mm
c = 600.00 / (600.00+400.00) x 470.000 = 282.000 mm, a = k1 x c = 239.700 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (470.00-282.00) / 282.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9913.278 kN ≥ Pn = 1090.719 kN
ΦPn = 0.78 x 1090.719 = 854.396 kN ≥ Pu = 571.628 kN ∴ O.K
ΦMn = ΦPn x 0.536 = 458.362 kN.m ≥ Mu = 306.664 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 470.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 470.00 = 309.182 kN
≥ Vu (= 239.056 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 666.667 |  | 586.667 |  | 494.83 |  | 322.989 |  | 240.709 |  | 652.727
＊ 철근비 검토
As = 1940.400 mm² (인장중심 = 80.00 mm) , 1단 : H19- 4.0EA + H16- 4.0EA , d1 = 80.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0046) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 666.7 x 1000.0 = 13600000.0 N
Cs = As x fy = 776160.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (13600000.0 x 333.33 + 776160.0 x 80.000 + 458400.0 x 576.667) / 14834560.0
= 327.598 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 352.000 mm, ab = k1 x cb = 299.200 mm
fs' = 600 x (352.000 - 90.000) / 352.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 299.200 x 1000.000 = 6103.680 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 776.160 kN
Pb = 6103.680 + 435.022 - 776.160 = 5762.542 kN
Mb = 6103.680 x (586.667 - 299.200/2) + 435.022 x (586.667 - 90.00)
- 5762.542 x (327.598 - 80.000)
= 1456.983 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 252.837 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 106.762 mm, a = k1 x c = 90.747 mm 를 사용.
fs = 600 x (586.667 - 106.762) / 106.762 (≤fy) = 400.000 MPa
fs' = 600 x (106.762 - 90.000) / 106.762 (≤fy) = 94.201 MPa
Cc = 0.85 x 24.0 x 90.747 x 1000.000 = 1851.247 kN
Cs = As' x (fs' - 0.85 x fck) = 84.575 kN
Ts = As x fs = 776.160 kN
Pn = 1851.247 + 84.575 - 776.160 = 1159.663 kN
Mn' = 1851.247 x (586.667 - 90.747/2) + 84.575 x (586.667 - 90.00)
= 1044.073 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0006 ＜ 0.0100 (e' = e + Xp - dc = 900.325 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 80.00 = 470.000 mm
c = 600.00 / (600.00+400.00) x 470.000 = 282.000 mm, a = k1 x c = 239.700 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (470.00-282.00) / 282.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 11817.278 kN ≥ Pn = 1159.663 kN
ΦPn = 0.78 x 1159.663 = 908.403 kN ≥ Pu = 494.830 kN ∴ O.K
ΦMn = ΦPn x 0.653 = 592.939 kN.m ≥ Mu = 322.989 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 470.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 470.00 = 306.311 kN
≥ Vu (= 240.709 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 460 |  | 533.234 |  | 147.357 |  | 0 |  | 276.345
＊ 철근비 검토
As = 1146.000 mm² (인장중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Asf = 1146.000 mm² (압축중심 = 80.00 mm) , 1단 : H19- 4.0EA , d1 = 80.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0042) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 458400.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (11220000.0 x 275.00 + 458400.0 x 90.000 + 458400.0 x 470.000) / 12136800.0
= 275.378 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 276.000 mm, ab = k1 x cb = 234.600 mm
fs' = 600 x (276.000 - 80.000) / 276.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 234.600 x 1000.000 = 4785.840 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 458.400 kN
Pb = 4785.840 + 435.022 - 458.400 = 4762.462 kN
Mb = 4785.840 x (460.000 - 234.600/2) + 435.022 x (460.000 - 80.00)
- 4762.462 x (275.378 - 90.000)
= 922.561 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 193.715 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 156.862 mm, a = k1 x c = 133.332 mm 를 사용.
fs = 600 x (460.000 - 156.862) / 156.862 (≤fy) = 400.000 MPa
fs' = 600 x (156.862 - 80.000) / 156.862 (≤fy) = 293.998 MPa
Cc = 0.85 x 24.0 x 133.332 x 1000.000 = 2719.980 kN
Cs = As' x (fs' - 0.85 x fck) = 313.543 kN
Ts = As x fs = 458.400 kN
Pn = 2719.980 + 313.543 - 458.400 = 2575.123 kN
Mn' = 2719.980 x (460.000 - 133.332/2) + 313.543 x (460.000 - 80.00)
= 1189.006 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0052 ＜ 0.0100 (e' = e + Xp - dc = 461.723 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 90.00 = 460.000 mm
c = 600.00 / (600.00+400.00) x 460.000 = 276.000 mm, a = k1 x c = 234.600 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (460.00-276.00) / 276.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9672.035 kN ≥ Pn = 2575.123 kN
ΦPn = 0.78 x 2575.123 = 2017.179 kN ≥ Pu = 533.234 kN ∴ O.K
ΦMn = ΦPn x 0.276 = 557.438 kN.m ≥ Mu = 147.357 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 460.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 460.00 = 301.199 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 470 |  | 533.234 |  | 236.335 |  | 0 |  | 443.211
＊ 철근비 검토
As = 1146.000 mm² (인장중심 = 80.00 mm) , 1단 : H19- 4.0EA , d1 = 80.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0042) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 458400.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (11220000.0 x 275.00 + 458400.0 x 80.000 + 458400.0 x 460.000) / 12136800.0
= 274.622 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 282.000 mm, ab = k1 x cb = 239.700 mm
fs' = 600 x (282.000 - 90.000) / 282.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 239.700 x 1000.000 = 4889.880 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 458.400 kN
Pb = 4889.880 + 435.022 - 458.400 = 4866.502 kN
Mb = 4889.880 x (470.000 - 239.700/2) + 435.022 x (470.000 - 90.00)
- 4866.502 x (274.622 - 80.000)
= 930.370 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 191.178 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 81.118 mm, a = k1 x c = 68.951 mm 를 사용.
fs = 600 x (470.000 - 81.118) / 81.118 (≤fy) = 400.000 MPa
fs' = 600 x ( 81.118 - 90.000) / 81.118 (≤fy) = 13.703 MPa
Cc = 0.85 x 24.0 x 68.951 x 1000.000 = 1406.592 kN
Cs = As' x (fs' - 0.85 x fck) = -7.674 kN
Ts = As x fs = 458.400 kN
Pn = 1406.592 + -7.674 - 458.400 = 955.866 kN
Mn' = 1406.592 x (470.000 - 68.951/2) + -7.674 x (470.000 - 90.00)
= 609.689 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0065 ＜ 0.0100 (e' = e + Xp - dc = 637.833 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 80.00 = 470.000 mm
c = 600.00 / (600.00+400.00) x 470.000 = 282.000 mm, a = k1 x c = 239.700 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (470.00-282.00) / 282.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9672.035 kN ≥ Pn = 955.866 kN
ΦPn = 0.78 x 955.866 = 748.762 kN ≥ Pu = 533.234 kN ∴ O.K
ΦMn = ΦPn x 0.443 = 331.859 kN.m ≥ Mu = 236.335 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 470.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 470.00 = 307.747 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 470 |  | 571.637 |  | 306.657 |  | 239.053 |  | 536.454
＊ 철근비 검토
As = 1940.400 mm² (인장중심 = 80.00 mm) , 1단 : H19- 4.0EA + H16- 4.0EA , d1 = 80.00 mm
Asf = 1146.000 mm² (압축중심 = 90.00 mm) , 1단 : H19- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0015) ≤ Puse (= 0.0056) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 776160.0 N, Cs' = Asf x fy = 458400.0 N
Xp = (11220000.0 x 275.00 + 776160.0 x 80.000 + 458400.0 x 460.000) / 12454560.0
= 269.657 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 282.000 mm, ab = k1 x cb = 239.700 mm
fs' = 600 x (282.000 - 90.000) / 282.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 239.700 x 1000.000 = 4889.880 kN
Cs = As' x (fs' - 0.85 x fck) = 435.022 kN
Ts = As x fs = 776.160 kN
Pb = 4889.880 + 435.022 - 776.160 = 4548.742 kN
Mb = 4889.880 x (470.000 - 239.700/2) + 435.022 x (470.000 - 90.00)
- 4548.742 x (269.657 - 80.000)
= 1014.800 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 223.095 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 103.757 mm, a = k1 x c = 88.193 mm 를 사용.
fs = 600 x (470.000 - 103.757) / 103.757 (≤fy) = 400.000 MPa
fs' = 600 x (103.757 - 90.000) / 103.757 (≤fy) = 79.553 MPa
Cc = 0.85 x 24.0 x 88.193 x 1000.000 = 1799.147 kN
Cs = As' x (fs' - 0.85 x fck) = 67.790 kN
Ts = As x fs = 776.160 kN
Pn = 1799.147 + 67.790 - 776.160 = 1090.777 kN
Mn' = 1799.147 x (470.000 - 88.193/2) + 67.790 x (470.000 - 90.00)
= 792.023 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0021 ＜ 0.0100 (e' = e + Xp - dc = 726.111 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 80.00 = 470.000 mm
c = 600.00 / (600.00+400.00) x 470.000 = 282.000 mm, a = k1 x c = 239.700 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (470.00-282.00) / 282.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9913.278 kN ≥ Pn = 1090.777 kN
ΦPn = 0.78 x 1090.777 = 854.442 kN ≥ Pu = 571.637 kN ∴ O.K
ΦMn = ΦPn x 0.536 = 458.369 kN.m ≥ Mu = 306.657 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 470.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 470.00 = 309.182 kN
≥ Vu (= 239.053 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
2) 상부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
3) 상부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
4) 상부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
5) 상부슬래브 : 제 3경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
6) 상부슬래브 : 제 3경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
7) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
8) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
9) 하부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
10) 하부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 2694.4 |  | × | 0.2 |  | = | 538.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 538.880 ----------> O.K !!!
11) 하부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
12) 하부슬래브 : 제 3경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 2694.4 |  | × | 0.2 |  | = | 538.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 538.880 ----------> O.K !!!
13) 하부슬래브 : 제 3경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
14) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 750 |  | × | 0.002 |  | = | 1500 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1500.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
15) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
16) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 229.200 ----------> O.K !!!
17) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 229.200 ----------> O.K !!!
18) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
19) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
20) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 229.200 ----------> O.K !!!
21) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1146 |  | × | 0.2 |  | = | 229.2 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 229.200 ----------> O.K !!!
22) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!

## 거더,기둥검토,내측벽체
21. 거더,기둥,내측벽체 검토
(1) 내측벽체 검토
(단위 : kN,m)
|  | 기둥부재 |  | 폭 | 두께 | 높이 |  | 길이 | 축력 |  | 모멘트 |  | 축력×길이 | 모멘트×길이 | Load Case
|  | P1 |  | 1 | 0.4 | 3.65 |  | 1 | 1090.16 |  | 8.45 |  | 1090.16 | 8.45 | 3
[9 empty] | 625.56 |  | 89.58 |  | 625.56 | 89.58 | 2
|  | P2 |  | 1 | 0.4 | 3.65 |  | 1 | 1090.13 |  | 8.44 |  | 1090.13 | 8.44 | 3
[9 empty] | 636.61 |  | 90.89 |  | 636.61 | 90.89 | 1
* 벽체와 기둥의 판별 (P1)
0.4Agfck = 0.4 × 1000 × 400 × 24
|  |  | = 3840000 N = 3840.00 kN | [6 empty] | ≥ 1090.16 kN
∴ 벽체로 검토한다
* 벽체와 기둥의 판별 (P2)
0.4Agfck = 0.4 × 1000 × 400 × 24
|  |  | = 3840000 N = 3840.00 kN | [6 empty] | ≥ 1090.13 kN
∴ 벽체로 검토한다
1)벽체 1
① 축력 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 310 |  | 1090.157 |  |  | 8.45 |  | 0 |  | 7.751
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 90.000 + 202720.0 x 310.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 186.000 mm, ab = k1 x cb = 158.100 mm
fs' = 600 x (186.000 - 90.000) / 186.000 (≤fy) = 309.677 MPa
Cc = 0.85 x 24.0 x 158.100 x 1000.000 = 3225.240 kN
Cs = As' x (fs' - 0.85 x fck) = 146.606 kN
Ts = As x fs = 202.720 kN
Pb = 3225.240 + 146.606 - 202.720 = 3169.126 kN
Mb = 3225.240 x (310.000 - 158.100/2) + 146.606 x (310.000 - 90.00)
- 3169.126 x (200.000 - 90.000)
= 428.519 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 135.217 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 454.805 mm, a = k1 x c = 386.585 mm 를 사용.
fs = 600 x (310.000 - 454.805) / 454.805 (≤fy) = 191.034 MPa
fs' = 600 x (454.805 - 90.000) / 454.805 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 386.585 x 1000.000 = 7886.325 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 96.816 kN
Pn = 7886.325 + 192.381 - 96.816 = 8175.522 kN
Mn' = 7886.325 x (310.000 - 386.585/2) + 192.381 x (310.000 - 90.00)
= 962.719 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0053 ＜ 0.0100 (e' = e + Xp - dc = 117.751 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 90.00 = 310.000 mm
c = 600.00 / (600.00+400.00) x 310.000 = 186.000 mm, a = k1 x c = 158.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (310.00-186.00) / 186.00 = 0.0020
εt ≤ εy 이므로 압축지배단면이며, Φ = 0.65 를 적용한다.
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ＜ Pn = 8175.522 kN
ΦPn = 0.65 x 6835.810 = 4443.277 kN ≥ Pu = 1090.157 kN ∴ O.K
ΦMn = ΦPn x 0.008 = 34.440 kN.m ≥ Mu = 8.450 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 310.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 310.00 = 226.791 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
② 모멘트 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 310 |  | 625.558 |  |  | 89.583 |  | 0 |  | 143.205
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 90.000 + 202720.0 x 310.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 186.000 mm, ab = k1 x cb = 158.100 mm
fs' = 600 x (186.000 - 90.000) / 186.000 (≤fy) = 309.677 MPa
Cc = 0.85 x 24.0 x 158.100 x 1000.000 = 3225.240 kN
Cs = As' x (fs' - 0.85 x fck) = 146.606 kN
Ts = As x fs = 202.720 kN
Pb = 3225.240 + 146.606 - 202.720 = 3169.126 kN
Mb = 3225.240 x (310.000 - 158.100/2) + 146.606 x (310.000 - 90.00)
- 3169.126 x (200.000 - 90.000)
= 428.519 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 135.217 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 170.894 mm, a = k1 x c = 145.260 mm 를 사용.
fs = 600 x (310.000 - 170.894) / 170.894 (≤fy) = 400.000 MPa
fs' = 600 x (170.894 - 90.000) / 170.894 (≤fy) = 284.014 MPa
Cc = 0.85 x 24.0 x 145.260 x 1000.000 = 2963.294 kN
Cs = As' x (fs' - 0.85 x fck) = 133.599 kN
Ts = As x fs = 202.720 kN
Pn = 2963.294 + 133.599 - 202.720 = 2894.174 kN
Mn' = 2963.294 x (310.000 - 145.260/2) + 133.599 x (310.000 - 90.00)
= 732.790 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0097 ＜ 0.0100 (e' = e + Xp - dc = 253.205 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 90.00 = 310.000 mm
c = 600.00 / (600.00+400.00) x 310.000 = 186.000 mm, a = k1 x c = 158.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (310.00-186.00) / 186.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ≥ Pn = 2894.174 kN
ΦPn = 0.78 x 2894.174 = 2267.103 kN ≥ Pu = 625.558 kN ∴ O.K
ΦMn = ΦPn x 0.143 = 324.659 kN.m ≥ Mu = 89.583 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 310.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 310.00 = 211.041 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
2)벽체 2
① 축력 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 310 |  | 1090.13 |  |  | 8.443 |  | 0 |  | 7.745
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 90.000 + 202720.0 x 310.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 186.000 mm, ab = k1 x cb = 158.100 mm
fs' = 600 x (186.000 - 90.000) / 186.000 (≤fy) = 309.677 MPa
Cc = 0.85 x 24.0 x 158.100 x 1000.000 = 3225.240 kN
Cs = As' x (fs' - 0.85 x fck) = 146.606 kN
Ts = As x fs = 202.720 kN
Pb = 3225.240 + 146.606 - 202.720 = 3169.126 kN
Mb = 3225.240 x (310.000 - 158.100/2) + 146.606 x (310.000 - 90.00)
- 3169.126 x (200.000 - 90.000)
= 428.519 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 135.217 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 454.849 mm, a = k1 x c = 386.622 mm 를 사용.
fs = 600 x (310.000 - 454.849) / 454.849 (≤fy) = 191.073 MPa
fs' = 600 x (454.849 - 90.000) / 454.849 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 386.622 x 1000.000 = 7887.081 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 96.836 kN
Pn = 7887.081 + 192.381 - 96.836 = 8176.298 kN
Mn' = 7887.081 x (310.000 - 386.622/2) + 192.381 x (310.000 - 90.00)
= 962.661 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0066 ＜ 0.0100 (e' = e + Xp - dc = 117.745 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 90.00 = 310.000 mm
c = 600.00 / (600.00+400.00) x 310.000 = 186.000 mm, a = k1 x c = 158.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (310.00-186.00) / 186.00 = 0.0020
εt ≤ εy 이므로 압축지배단면이며, Φ = 0.65 를 적용한다.
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ＜ Pn = 8176.298 kN
ΦPn = 0.65 x 6835.810 = 4443.277 kN ≥ Pu = 1090.130 kN ∴ O.K
ΦMn = ΦPn x 0.008 = 34.412 kN.m ≥ Mu = 8.443 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 310.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 310.00 = 226.790 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
② 모멘트 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 310 |  | 636.607 |  |  | 90.889 |  | 0 |  | 142.771
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Asf = 506.800 mm² (압축중심 = 90.00 mm) , 1단 : H13- 4.0EA , d1 = 90.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 90.000 + 202720.0 x 310.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 186.000 mm, ab = k1 x cb = 158.100 mm
fs' = 600 x (186.000 - 90.000) / 186.000 (≤fy) = 309.677 MPa
Cc = 0.85 x 24.0 x 158.100 x 1000.000 = 3225.240 kN
Cs = As' x (fs' - 0.85 x fck) = 146.606 kN
Ts = As x fs = 202.720 kN
Pb = 3225.240 + 146.606 - 202.720 = 3169.126 kN
Mb = 3225.240 x (310.000 - 158.100/2) + 146.606 x (310.000 - 90.00)
- 3169.126 x (200.000 - 90.000)
= 428.519 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 135.217 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 171.688 mm, a = k1 x c = 145.935 mm 를 사용.
fs = 600 x (310.000 - 171.688) / 171.688 (≤fy) = 400.000 MPa
fs' = 600 x (171.688 - 90.000) / 171.688 (≤fy) = 285.476 MPa
Cc = 0.85 x 24.0 x 145.935 x 1000.000 = 2977.074 kN
Cs = As' x (fs' - 0.85 x fck) = 134.341 kN
Ts = As x fs = 202.720 kN
Pn = 2977.074 + 134.341 - 202.720 = 2908.695 kN
Mn' = 2977.074 x (310.000 - 145.935/2) + 134.341 x (310.000 - 90.00)
= 735.218 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0055 ＜ 0.0100 (e' = e + Xp - dc = 252.771 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 90.00 = 310.000 mm
c = 600.00 / (600.00+400.00) x 310.000 = 186.000 mm, a = k1 x c = 158.100 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (310.00-186.00) / 186.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ≥ Pn = 2908.695 kN
ΦPn = 0.78 x 2908.695 = 2278.477 kN ≥ Pu = 636.607 kN ∴ O.K
ΦMn = ΦPn x 0.143 = 325.301 kN.m ≥ Mu = 90.889 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 310.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 310.00 = 211.416 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.

## 절점부 검토
22. 절점부 검토
1) 절점 60
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 205.742 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 205.742 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 1166.726 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 205.74 × 10^6 |  |  | = | 0.756 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 1166.726²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 205.74 × 10^6 |  |  | = | 1959.344 mm²
|  |  |  | R × fsa |  |  | 1166.726 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1959.344 mm² - 794.400 mm²
[5 empty] | = | 1164.944 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H22 @250 - 4EA
∴ Total As = 1548.400 mm² > Req'd As (= 1164.944 mm²) -------------> O.K !!!
2) 절점 1
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 190.598 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 190.598 kN.m
R = √(T1² + T2²) = 930.054 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 190.60 × 10^6 |  |  | = | 1.102 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 930.054²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 190.60 × 10^6 |  |  | = | 2277.020 mm²
|  |  |  | R × fsa |  |  | 930.054 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 2277.020 mm² - 794.400 mm²
[5 empty] | = | 1482.620 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H25 @250 - 4EA
∴ Total As = 2026.800 mm² > Req'd As (= 1482.620 mm²) -------------> O.K !!!
3) 절점 42
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 205.750 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 205.750 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 1166.726 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 205.75 × 10^6 |  |  | = | 0.756 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 1166.726²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 205.75 × 10^6 |  |  | = | 1959.421 mm²
|  |  |  | R × fsa |  |  | 1166.726 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1959.421 mm² - 794.400 mm²
[5 empty] | = | 1165.021 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H22 @250 - 4EA
∴ Total As = 1548.400 mm² > Req'd As (= 1165.021 mm²) -------------> O.K !!!
4) 절점 37
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 190.592 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 190.592 kN.m
R = √(T1² + T2²) = 930.054 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 190.59 × 10^6 |  |  | = | 1.102 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 930.054²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 190.59 × 10^6 |  |  | = | 2276.958 mm²
|  |  |  | R × fsa |  |  | 930.054 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 2276.958 mm² - 794.400 mm²
[5 empty] | = | 1482.558 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H25 @250 - 4EA
∴ Total As = 2026.800 mm² > Req'd As (= 1482.558 mm²) -------------> O.K !!!

## 사용성 검토
23. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 786.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 375.031 | O.K |  | 3
2 | 상부슬래브 : 제 1경간 중앙부 |  | 660 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 337.872 | O.K |  | 2.703
3 | 상부슬래브 : 제 2경간 지점부 |  | 786.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 287.834 | O.K |  | 2.303
4 | 상부슬래브 : 제 2경간 중앙부 |  | 660 |  | H16 - 8.0EA |  |  | 125 | 445.229 | O.K |  | 3.562
5 | 상부슬래브 : 제 3경간 지점부 |  | 786.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 287.893 | O.K |  | 2.303
6 | 상부슬래브 : 제 3경간 중앙부 |  | 660 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 337.85 | O.K |  | 2.703
7 | 상부슬래브 : 단지점부(우측) |  | 786.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 375.01 | O.K |  | 3
8 | 하부슬래브 : 단지점부(좌측) |  | 670 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 328.298 | O.K |  | 2.626
9 | 하부슬래브 : 제 1경간 중앙부 |  | 660 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 325.448 | O.K |  | 2.604
10 | 하부슬래브 : 제 2경간 지점부 |  | 670 |  | H22 - 4.0EA + H19 - 4.0EA |  |  | 125 | 313.98 | O.K |  | 2.512
11 | 하부슬래브 : 제 2경간 중앙부 |  | 660 |  | H16 - 8.0EA |  |  | 125 | 498.618 | O.K |  | 3.989
12 | 하부슬래브 : 제 3경간 지점부 |  | 670 |  | H22 - 4.0EA + H19 - 4.0EA |  |  | 125 | 313.958 | O.K |  | 2.512
13 | 하부슬래브 : 제 3경간 중앙부 |  | 660 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 325.387 | O.K |  | 2.603
14 | 하부슬래브 : 단지점부(우측) |  | 670 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 328.312 | O.K |  | 2.626
15 | 좌측벽체 : 상부 |  | 586.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 231.402 | O.K |  | 1.851
16 | 좌측벽체 : 중앙부 |  | 460 |  | H19 - 4.0EA |  |  | 250 | 285.558 | O.K |  | 1.142
17 | 좌측벽체 : 중앙부(부모멘트) |  | 470 |  | H19 - 4.0EA |  |  | 250 | 587.604 | O.K |  | 2.35
18 | 좌측벽체 : 하부 |  | 470 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 173.776 | O.K |  | 1.39
19 | 우측벽체 : 상부 |  | 586.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 231.386 | O.K |  | 1.851
20 | 우측벽체 : 중앙부 |  | 460 |  | H19 - 4.0EA |  |  | 250 | 285.564 | O.K |  | 1.142
21 | 우측벽체 : 중앙부(부모멘트) |  | 470 |  | H19 - 4.0EA |  |  | 250 | 587.53 | O.K |  | 2.35
22 | 우측벽체 : 하부 |  | 470 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 173.785 | O.K |  | 1.39
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 205.742 x 1000000 / [1940.400 x (786.667 - 133.233/3)]
= 142.849 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x786.7/(7x1940.400)]
= 133.233 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 142.85) - 2.5 x 70.50 = 375.03 mm
300 x (210 / fs) = 300 x (210 / 142.85) = 441.03 mm
Sa는 작은 값인 375.03 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 375.03 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 175.635 x 1000000 / [1940.400 x (660.000 - 121.005/3)]
= 146.071 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x660.0/(7x1940.400)]
= 121.005 mm
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 146.07) - 2.5 x 80.50 = 337.87 mm
300 x (210 / fs) = 300 x (210 / 146.07) = 431.30 mm
Sa는 작은 값인 337.87 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 337.87 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 244.399 x 1000000 / [1940.400 x (786.667 - 133.233/3)]
= 169.689 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x786.7/(7x1940.400)]
= 133.233 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 169.69) - 2.5 x 70.50 = 287.83 mm
300 x (210 / fs) = 300 x (210 / 169.69) = 371.27 mm
Sa는 작은 값인 287.83 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 287.83 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 119.907 x 1000000 / [1588.800 x (660.000 - 110.551/3)]
= 121.111 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x660.0/(7x1588.800)]
= 110.551 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 121.11) - 2.5 x 82.00 = 445.23 mm
300 x (210 / fs) = 300 x (210 / 121.11) = 520.18 mm
Sa는 작은 값인 445.23 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 445.23 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 3경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 244.368 x 1000000 / [1940.400 x (786.667 - 133.233/3)]
= 169.668 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x786.7/(7x1940.400)]
= 133.233 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 169.67) - 2.5 x 70.50 = 287.89 mm
300 x (210 / fs) = 300 x (210 / 169.67) = 371.31 mm
Sa는 작은 값인 287.89 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 287.89 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 3경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 175.643 x 1000000 / [1940.400 x (660.000 - 121.005/3)]
= 146.077 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x660.0/(7x1940.400)]
= 121.005 mm
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 146.08) - 2.5 x 80.50 = 337.85 mm
300 x (210 / fs) = 300 x (210 / 146.08) = 431.28 mm
Sa는 작은 값인 337.85 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 337.85 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 205.750 x 1000000 / [1940.400 x (786.667 - 133.233/3)]
= 142.855 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x786.7/(7x1940.400)]
= 133.233 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 142.85) - 2.5 x 70.50 = 375.01 mm
300 x (210 / fs) = 300 x (210 / 142.85) = 441.01 mm
Sa는 작은 값인 375.01 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 375.01 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 190.598 x 1000000 / [1940.400 x (670.000 - 122.010/3)]
= 156.080 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x670.0/(7x1940.400)]
= 122.010 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 156.08) - 2.5 x 70.50 = 328.30 mm
300 x (210 / fs) = 300 x (210 / 156.08) = 403.64 mm
Sa는 작은 값인 328.30 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 328.30 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 179.778 x 1000000 / [1940.400 x (660.000 - 121.005/3)]
= 149.516 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x660.0/(7x1940.400)]
= 121.005 mm
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 149.52) - 2.5 x 80.50 = 325.45 mm
300 x (210 / fs) = 300 x (210 / 149.52) = 421.36 mm
Sa는 작은 값인 325.45 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 325.45 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 271.696 x 1000000 / [2694.400 x (670.000 - 141.230/3)]
= 161.877 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x2694.400/1000.0 + 7x2694.400/1000.0 x √[(1 + 2x1000.0x670.0/(7x2694.400)]
= 141.230 mm
Use As = 2694.400 mm² (철근도심 : 80.000 mm)
1단 : H22 - 4.0 EA + H19 - 4.0 EA (= 2694.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 22/2 = 69.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 161.88) - 2.5 x 69.00 = 313.98 mm
300 x (210 / fs) = 300 x (210 / 161.88) = 389.18 mm
Sa는 작은 값인 313.98 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 313.98 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 110.809 x 1000000 / [1588.800 x (660.000 - 110.551/3)]
= 111.922 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x660.0/(7x1588.800)]
= 110.551 mm
Use As = 1588.800 mm² (철근도심 : 90.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 16/2 = 82.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 111.92) - 2.5 x 82.00 = 498.62 mm
300 x (210 / fs) = 300 x (210 / 111.92) = 562.89 mm
Sa는 작은 값인 498.62 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 498.62 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 3경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 271.707 x 1000000 / [2694.400 x (670.000 - 141.230/3)]
= 161.884 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x2694.400/1000.0 + 7x2694.400/1000.0 x √[(1 + 2x1000.0x670.0/(7x2694.400)]
= 141.230 mm
Use As = 2694.400 mm² (철근도심 : 80.000 mm)
1단 : H22 - 4.0 EA + H19 - 4.0 EA (= 2694.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 22/2 = 69.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 161.88) - 2.5 x 69.00 = 313.96 mm
300 x (210 / fs) = 300 x (210 / 161.88) = 389.17 mm
Sa는 작은 값인 313.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 313.96 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 3경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 179.799 x 1000000 / [1940.400 x (660.000 - 121.005/3)]
= 149.534 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x660.0/(7x1940.400)]
= 121.005 mm
Use As = 1940.400 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 149.53) - 2.5 x 80.50 = 325.39 mm
300 x (210 / fs) = 300 x (210 / 149.53) = 421.31 mm
Sa는 작은 값인 325.39 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 325.39 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 190.592 x 1000000 / [1940.400 x (670.000 - 122.010/3)]
= 156.076 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x670.0/(7x1940.400)]
= 122.010 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 156.08) - 2.5 x 70.50 = 328.31 mm
300 x (210 / fs) = 300 x (210 / 156.08) = 403.65 mm
Sa는 작은 값인 328.31 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 328.31 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 205.742 x 1000000 / [1940.400 x (586.667 - 113.388/3)]
= 193.179 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x586.7/(7x1940.400)]
= 113.388 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 193.18) - 2.5 x 70.50 = 231.40 mm
300 x (210 / fs) = 300 x (210 / 193.18) = 326.12 mm
Sa는 작은 값인 231.40 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 231.40 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 80.441 x 1000000 / [1146.000 x (460.000 - 78.260/3)]
= 161.768 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1146.000/1000.0 + 7x1146.000/1000.0 x √[(1 + 2x1000.0x460.0/(7x1146.000)]
= 78.260 mm
Use As = 1146.000 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA (= 1146.000 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 161.77) - 2.5 x 80.50 = 285.56 mm
300 x (210 / fs) = 300 x (210 / 161.77) = 389.45 mm
Sa는 작은 값인 285.56 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 285.56 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 52.411 x 1000000 / [1146.000 x (470.000 - 79.185/3)]
= 103.096 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1146.000/1000.0 + 7x1146.000/1000.0 x √[(1 + 2x1000.0x470.0/(7x1146.000)]
= 79.185 mm
Use As = 1146.000 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA (= 1146.000 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 103.10) - 2.5 x 70.50 = 587.60 mm
300 x (210 / fs) = 300 x (210 / 103.10) = 611.08 mm
Sa는 작은 값인 587.60 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 587.60 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 190.598 x 1000000 / [1940.400 x (470.000 - 100.225/3)]
= 224.984 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x470.0/(7x1940.400)]
= 100.225 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 224.98) - 2.5 x 70.50 = 173.78 mm
300 x (210 / fs) = 300 x (210 / 224.98) = 280.02 mm
Sa는 작은 값인 173.78 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 173.78 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 205.750 x 1000000 / [1940.400 x (586.667 - 113.388/3)]
= 193.187 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x586.7/(7x1940.400)]
= 113.388 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 193.19) - 2.5 x 70.50 = 231.39 mm
300 x (210 / fs) = 300 x (210 / 193.19) = 326.11 mm
Sa는 작은 값인 231.39 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 231.39 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 80.441 x 1000000 / [1146.000 x (460.000 - 78.260/3)]
= 161.766 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1146.000/1000.0 + 7x1146.000/1000.0 x √[(1 + 2x1000.0x460.0/(7x1146.000)]
= 78.260 mm
Use As = 1146.000 mm² (철근도심 : 90.000 mm)
1단 : H19 - 4.0 EA (= 1146.000 mm²) , d1 = 90.00 mm
* 철근의 최대 중심간격
Cc = 90.00 - 19/2 = 80.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 161.77) - 2.5 x 80.50 = 285.56 mm
300 x (210 / fs) = 300 x (210 / 161.77) = 389.45 mm
Sa는 작은 값인 285.56 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 285.56 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 52.416 x 1000000 / [1146.000 x (470.000 - 79.185/3)]
= 103.106 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1146.000/1000.0 + 7x1146.000/1000.0 x √[(1 + 2x1000.0x470.0/(7x1146.000)]
= 79.185 mm
Use As = 1146.000 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA (= 1146.000 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 103.11) - 2.5 x 70.50 = 587.53 mm
300 x (210 / fs) = 300 x (210 / 103.11) = 611.02 mm
Sa는 작은 값인 587.53 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 587.53 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 190.592 x 1000000 / [1940.400 x (470.000 - 100.225/3)]
= 224.977 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x470.0/(7x1940.400)]
= 100.225 mm
Use As = 1940.400 mm² (철근도심 : 80.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 19/2 = 70.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 224.98) - 2.5 x 70.50 = 173.79 mm
300 x (210 / fs) = 300 x (210 / 224.98) = 280.03 mm
Sa는 작은 값인 173.79 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 173.79 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 4.475 m
- fy = 400 MPa
- 부재두께(T) = 0.75 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 4.475 / 28
T = 0.160 m < 0.750 m -----------> O.K

## 기초 지지력 검토
24. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  | = | 706.029 |  | / | 13.9 |  | = | 50.793 |  | kN/m²
|  |  | - 상부연직하중 |  |  | = | 133 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  | 10 |  | kN/m²
3) 내부 수압
|  |  | - 암거내부수압 |  |  | = | 32 |  | kN/m²
4) 최대 지반 반력
|  |  | Qmax | = | 50.793 |  | + | 133 |  | + | 10 |  | + | 32
|  |  |  | = | 225.793 |  | kN/m²

## 주철근 조립도
25. 주철근 조립도