## 표지
P2-13B 구조계산서
| ▣ 구조형식 |  | : | 지중 2 련 암거
( 내공 : 2@(3.5M ⅹ 3.5M) )
| ▣ 토 피(FH) |  | = | 4.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 거더,기둥,내측벽체 검토
[5 empty] | 22. | 절점부 검토
[5 empty] | 23. | 사용성 검토
[5 empty] | 24. | 기초 지지력 검토
[5 empty] | 25. | 주철근 조립도

## 설계요약표
1. 설계 요약표
P2-13B (토피=4.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 4.0m
안정(지지력)검토 | Qmax = 171.293 kN/m²
단면 위치 | 내구성검토 |  |  | 단 면 검 토 | [13 empty] | 절 점 부 보 강
| 균열검토 |  |  | 휨 검 토 | [6 empty] | 전 단 검 토
| 철근간격 mm | 최대간격 mm |  | 사용철근 | Mu kN.m |  | ΦMn kN.m |  | S.F |  | 사용철근 |  | Vu kN |  | ΦVn kN |  | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 438.195 |  | H16 - 4.0EA + H13 - 4.0EA | 153.394 |  | 250.953 |  | 1.64 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.607 | 0.637 | H19 @250 - 4EA
상부슬래브 : 제 1경간 중앙부 | 125 | 479.639 |  | H16 - 4.0EA + H13 - 4.0EA | 124.013 |  | 215.56 |  | 1.74 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 지점부 | 125 | 445.583 |  | H19 - 4.0EA + H16 - 4.0EA | 208.151 |  | 370.096 |  | 1.78 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 중앙부 | 125 | 479.639 |  | H16 - 4.0EA + H13 - 4.0EA | 124.013 |  | 215.56 |  | 1.74 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 단지점부(우측) | 125 | 438.193 |  | H16 - 4.0EA + H13 - 4.0EA | 153.395 |  | 250.953 |  | 1.64 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.607 | 0.637 | H19 @250 - 4EA
하부슬래브 : 단지점부(좌측) | 125 | 444.587 |  | H16 - 8.0EA | 145.169 |  | 250.878 |  | 1.73 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 1.013 | 0.637 | H22 @250 - 4EA
하부슬래브 : 제 1경간 중앙부 | 125 | 443.298 |  | H16 - 4.0EA + H13 - 4.0EA | 128.785 |  | 215.56 |  | 1.67 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 지점부 | 125 | 444.14 |  | H19 - 8.0EA | 206.465 |  | 356.544 |  | 1.73 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 중앙부 | 125 | 443.298 |  | H16 - 4.0EA + H13 - 4.0EA | 128.785 |  | 215.56 |  | 1.67 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 단지점부(우측) | 125 | 444.587 |  | H16 - 8.0EA | 145.169 |  | 250.878 |  | 1.73 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 1.013 | 0.637 | H22 @250 - 4EA
좌측벽체 : 상부 | 125 | 281.138 |  | H16 - 4.0EA + H13 - 4.0EA | 153.394 |  | 276.034 |  | 1.8 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부 | 250 | 403.43 |  | H16 - 4.0EA | 67.788 |  | 257.123 |  | 3.79 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부(부모멘트) | 250 | 459.529 |  | H16 - 4.0EA | 62.854 |  | 276.173 |  | 4.39 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 하부 | 125 | 252.111 |  | H16 - 8.0EA | 145.169 |  | 242.052 |  | 1.67 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 상부 | 125 | 281.136 |  | H16 - 4.0EA + H13 - 4.0EA | 153.395 |  | 276.03 |  | 1.8 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부 | 250 | 403.43 |  | H16 - 4.0EA | 67.788 |  | 257.122 |  | 3.79 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부(부모멘트) | 250 | 459.524 |  | H16 - 4.0EA | 62.863 |  | 276.084 |  | 4.39 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 하부 | 125 | 252.111 |  | H16 - 8.0EA | 145.169 |  | 242.052 |  | 1.67 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
기둥단면검토
기둥 위치 | 기둥 형태 |  | 사용 철근 |  |  | e |  | eb |  | Pu |  | ΦPn |  | Mu |  | ΦMn |  | 비 고
[6 empty] | (mm) |  | (mm) |  | (kN) |  | (kN) |  | (kN.m) |  | (kN.m)
P1 | 벽 체 |  | H13 |  |  | 0 |  | 101.845 |  | 662.807 |  | 4076.318 |  | 0 |  | 0.001 |  | 축력 최대시
[6 empty] | 16.525 |  | 101.845 |  | 385.359 |  | 4076.318 |  | 6.368 |  | 67.359 |  | 모멘트 최대시

## 설계조건
2. 설계조건
1) 구조형식
- 지중 2 련 암거 ( 내공 : 2@(3.5M ⅹ 3.5M), 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 10 |  | kN/m² |  | (∵ 토피 : | 4 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 1~14,20~31
| 2 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 15~19,32~36
| 3 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 37
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.2 | 0.275 | 23 |  | 5.95 |  | 4.325
| 2 |  | 0.4 | 0.275 | 24 |  | 4.68 |  | 4.325
| 3 |  | 0.88 | 0.275 | 25 |  | 4.2 |  | 4.325
| 4 |  | 1.483 | 0.275 | 26 |  | 4.05 |  | 4.325
| 5 |  | 2.767 | 0.275 | 27 |  | 3.9 |  | 4.325
| 6 |  | 3.42 | 0.275 | 28 |  | 3.42 |  | 4.325
| 7 |  | 3.9 | 0.275 | 29 |  | 2.15 |  | 4.325
| 8 |  | 4.05 | 0.275 | 30 |  | 0.88 |  | 4.325
| 9 |  | 4.2 | 0.275 | 31 |  | 0.4 |  | 4.325
| 10 |  | 4.68 | 0.275 | 32 |  | 0.2 |  | 4.325
| 11 |  | 5.333 | 0.275 | 33 |  | 0.2 |  | 4.05
| 12 |  | 6.617 | 0.275 | 34 |  | 0.2 |  | 3.72
| 13 |  | 7.22 | 0.275 | 35 |  | 0.2 |  | 0.88
| 14 |  | 7.7 | 0.275 | 36 |  | 0.2 |  | 0.55
| 15 |  | 7.9 | 0.275 | 37 |  | 0.2 |  | -0.225
| 16 |  | 7.9 | 0.55 | 38 |  | 1.483 |  | -0.225
| 17 |  | 7.9 | 0.88 | 39 |  | 2.767 |  | -0.225
| 18 |  | 7.9 | 3.72 | 40 |  | 4.05 |  | -0.225
| 19 |  | 7.9 | 4.05 | 41 |  | 5.333 |  | -0.225
| 20 |  | 7.9 | 4.325 | 42 |  | 6.617 |  | -0.225
| 21 |  | 7.7 | 4.325 | 43 |  | 7.9 |  | -0.225
| 22 |  | 7.22 | 4.325

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 1~14,23~36
| 2 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 15~22,37~44
| 3 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 45
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.2 | 0.275 | 35 |  | 0.88 |  | 4.325
| 2 |  | 0.4 | 0.275 | 36 |  | 0.4 |  | 4.325
| 3 |  | 0.88 | 0.275 | 37 |  | 0.2 |  | 4.325
| 4 |  | 1.483 | 0.275 | 38 |  | 0.2 |  | 4.05
| 5 |  | 2.767 | 0.275 | 39 |  | 0.2 |  | 3.72
| 6 |  | 3.42 | 0.275 | 40 |  | 0.2 |  | 3.313
| 7 |  | 3.9 | 0.275 | 41 |  | 0.2 |  | 2.3
| 8 |  | 4.05 | 0.275 | 42 |  | 0.2 |  | 1.288
| 9 |  | 4.2 | 0.275 | 43 |  | 0.2 |  | 0.88
| 10 |  | 4.68 | 0.275 | 44 |  | 0.2 |  | 0.55
| 11 |  | 5.333 | 0.275 | 45 |  | 0.2 |  | -0.225
| 12 |  | 6.617 | 0.275 | 46 |  | 1.483 |  | -0.225
| 13 |  | 7.22 | 0.275 | 47 |  | 2.767 |  | -0.225
| 14 |  | 7.7 | 0.275 | 48 |  | 4.05 |  | -0.225
| 15 |  | 7.9 | 0.275 | 49 |  | 5.333 |  | -0.225
| 16 |  | 7.9 | 0.55 | 50 |  | 6.617 |  | -0.225
| 17 |  | 7.9 | 0.88 | 51 |  | 7.9 |  | -0.225
| 18 |  | 7.9 | 1.288 | 52 |  | 8.4 |  | 0.275
| 19 |  | 7.9 | 2.3 | 53 |  | 8.4 |  | 1.288
| 20 |  | 7.9 | 3.312 | 54 |  | 8.4 |  | 2.3
| 21 |  | 7.9 | 3.72 | 55 |  | 8.4 |  | 3.312
| 22 |  | 7.9 | 4.05 | 56 |  | 8.4 |  | 4.325
| 23 |  | 7.9 | 4.325 | 57 |  | 7.9 |  | 4.825
| 24 |  | 7.7 | 4.325 | 58 |  | 6.617 |  | 4.825
| 25 |  | 7.22 | 4.325 | 59 |  | 5.333 |  | 4.825
| 26 |  | 6.617 | 4.325 | 60 |  | 4.05 |  | 4.825
| 27 |  | 5.333 | 4.325 | 61 |  | 2.767 |  | 4.825
| 28 |  | 4.68 | 4.325 | 62 |  | 1.483 |  | 4.825
| 29 |  | 4.2 | 4.325 | 63 |  | 0.2 |  | 4.825
| 30 |  | 4.05 | 4.325 | 64 |  | -0.3 |  | 4.325
| 31 |  | 3.9 | 4.325 | 65 |  | -0.3 |  | 3.313
| 32 |  | 3.42 | 4.325 | 66 |  | -0.3 |  | 2.3
| 33 |  | 2.767 | 4.325 | 67 |  | -0.3 |  | 1.288
| 34 |  | 1.483 | 4.325 | 68 |  | -0.3 |  | 0.275

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 8.100 × 8.100 ) |  |  | = | 8.1 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 8.100 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 11819.666 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.400/2 + 1.283/2) = 9946 kN/m |  |  |  |  | 1,15
| Kv2 |  |  | Kvⅹ(1.283/2 + 1.283/2) = 15165 kN/m |  |  |  |  | 4~5,8,11,12
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 4.050m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 8.100 × 8.100 ) |  |  |  |  | = | 8.1 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 8.100 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 29735.13 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 29735.130 |  |  |  |  | = | 9911.71 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 8.100 × 8.100 ) |  |  |  |  | = | 8.1 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 8.100 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 29735.13 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 29735.130 |  |  |  |  | = | 9911.71 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 4.600 × 4.600 ) |  |  |  |  | = | 4.6 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 4.600 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 45453.28 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 45453.280 |  |  |  |  | = | 15151.09 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(1.283/2 + 0.400/2) = 25022 kN/m | [8 empty] | 23,37
|  | Ksb1 |  |  | Ksbⅹ(1.283/2 + 0.400/2) = 8341 kN/m
|  | Kv2 |  |  | Kvⅹ(1.283/2 + 1.283/2) = 38150 kN/m | [8 empty] | 26~27,30,33,34
|  | Ksb2 |  |  | Ksbⅹ(1.283/2 + 1.283/2) = 12717 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(1.012/2 + 0.550/2) = 35499 kN/m | [8 empty] | 1,15,23,37
|  | Kss1 |  |  | Kssⅹ(1.012/2 + 0.550/2) = 11833 kN/m
|  | Kh2 |  |  | Khⅹ(1.012/2 + 1.012/2) = 45999 kN/m | [8 empty] | 18~20,40~42
|  | Kss2 |  |  | Kssⅹ(1.012/2 + 1.012/2) = 15333 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.400/2 + 1.283/2) = 25022 kN/m | [8 empty] | 1,15
|  | Ksb1 |  |  | Ksbⅹ(0.400/2 + 1.283/2) = 8341 kN/m
|  | Kv2 |  |  | Kvⅹ(1.283/2 + 1.283/2) = 38150 kN/m | [8 empty] | 4~5,8,11,12
|  | Ksb2 |  |  | Ksbⅹ(1.283/2 + 1.283/2) = 12717 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 4.00 × 19.00 |  |  |  |  | = | 76 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 76 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 상부 슬래브에 작용하는 하중 (Wl1) - 토피 4m 이상
|  |  | - Wl1 |  | = | 10.000 kN/m²
② 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (4.275 × 19.000) × 0.500 | [9 empty] | = | 40.613 | kN/m²
|  | - Wh2 |  | = | 40.613 + 0.275 × 19.000 × 0.500 | [9 empty] | = | 43.225 | kN/m²
|  | - Wh3 |  | = | 43.225 + 0.330 × 19.000 × 0.500 | [9 empty] | = | 46.361 | kN/m²
|  | - Wh4 |  | = | 46.361 + 2.840 × 19.000 × 0.500 | [9 empty] | = | 73.34 | kN/m²
|  | - Wh5 |  | = | 73.340 + 0.330 × 19.000 × 0.500 | [9 empty] | = | 76.475 | kN/m²
|  | - Wh6 |  | = | 76.475 + 0.275 × 19.000 × 0.500 | [9 empty] | = | 79.088 | kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 8.05 |  | 197.3 |  |  |  | 19 |  |  | 0.163
|  | 계 | [11 empty] | 0.163
Tg = 1.25 Tg' = 1.25 × 0.163 = 0.204 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.204 / 2π × 2.617 = 0.085 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 4.275 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 8.325 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.085 × 0.204 × cos(π× 4.275 / (2 × 30.000)) = 0.003426
U(Zb) = 2 / π²× 0.085 × 0.204 × cos(π× 8.325 / (2 × 30.000)) = 0.003185
Po = Ksb,top × (U(Zu) - U(Zb))
= 9911.710 × (0.003426 - 0.003185) = 2.389 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 4.275 |  | 45453.28 |  |  |  | 0.003426 |  |  |  |  | 0.000241 |  | 10.954
|  | 4.55 |  | 45453.28 |  |  |  | 0.003415 |  |  |  |  | 0.00023 |  | 10.454
|  | 4.88 |  | 45453.28 |  |  |  | 0.0034 |  |  |  |  | 0.000215 |  | 9.772
|  | 5.288 |  | 45453.28 |  |  |  | 0.00338 |  |  |  |  | 0.000195 |  | 8.863
|  | 6.3 |  | 45453.28 |  |  |  | 0.003324 |  |  |  |  | 0.000139 |  | 6.318
|  | 7.313 |  | 45453.28 |  |  |  | 0.003259 |  |  |  |  | 7.4e-05 |  | 3.363
|  | 7.72 |  | 45453.28 |  |  |  | 0.003231 |  |  |  |  | 4.6e-05 |  | 2.091
|  | 8.05 |  | 45453.28 |  |  |  | 0.003206 |  |  |  |  | 2.1e-05 |  | 0.954
|  | 8.325 |  | 45453.28 |  |  |  | 0.003185 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000041 = 0.770 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000078 = 1.470 kN/m²
Vs = (Vu - Vb) / 2 = (0.770 + 1.470) / 2 = 1.120 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 4.275) = 2.018 kN/m²
② 하부슬래브
fb = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.325) = 1.887 kN/m²
③ 중간벽체
fu1 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 4.275) = 1.101 kN/m²
fb1 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 8.325) = 1.029 kN/m²
④ 측벽
f1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 4.275) = 1.467 kN/m²
f2 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 4.550) = 1.461 kN/m²
f3 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 4.880) = 1.453 kN/m²
f4 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 5.288) = 1.444 kN/m²
f5 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 6.300) = 1.420 kN/m²
f6 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 7.313) = 1.396 kN/m²
f7 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 7.720) = 1.386 kN/m²
f8 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 8.050) = 1.379 kN/m²
f9 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 8.325) = 1.372 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 0.950, h = 4.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.52 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.52 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.52 | 1.6 | 0.8 | 0.8
2) 극한하중 기둥최대편심 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.52 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.52 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.52 | 1.6 | 0.8 | 0.8
3) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.95 | 1 | 1 | 1
| 2 |  | 1 | 0.95 |  | 1 | 1
| 3 |  | 1 | 0.95 | 1 | 0.5 | 0.5
4) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.95 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 9 J= 9, 10 SEC=1 NSEG=1 ANG=180
10 J= 10, 11 SEC=1 NSEG=2 ANG=180
| JOINT | 11 J= 11, 12 SEC=1 NSEG=4 ANG=180
| 1 X= 0.200 Y= 0.000 Z= 0.275 | 12 J= 12, 13 SEC=1 NSEG=2 ANG=180
| 2 X= 0.400 Y= 0.000 Z= 0.275 | 13 J= 13, 14 SEC=1 NSEG=1 ANG=180
| 3 X= 0.880 Y= 0.000 Z= 0.275 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=180
| 4 X= 1.483 Y= 0.000 Z= 0.275 | 15 J= 15, 16 SEC=2 NSEG=1 ANG=0
| 5 X= 2.767 Y= 0.000 Z= 0.275 | 16 J= 16, 17 SEC=2 NSEG=1 ANG=0
| 6 X= 3.420 Y= 0.000 Z= 0.275 | 17 J= 17, 18 SEC=2 NSEG=4 ANG=0
| 7 X= 3.900 Y= 0.000 Z= 0.275 | 18 J= 18, 19 SEC=2 NSEG=1 ANG=0
| 8 X= 4.050 Y= 0.000 Z= 0.275 | 19 J= 19, 20 SEC=2 NSEG=1 ANG=0
| 9 X= 4.200 Y= 0.000 Z= 0.275 | 20 J= 20, 21 SEC=1 NSEG=1 ANG=0
| 10 X= 4.680 Y= 0.000 Z= 0.275 | 21 J= 21, 22 SEC=1 NSEG=1 ANG=0
| 11 X= 5.333 Y= 0.000 Z= 0.275 | 22 J= 22, 23 SEC=1 NSEG=4 ANG=0
| 12 X= 6.617 Y= 0.000 Z= 0.275 | 23 J= 23, 24 SEC=1 NSEG=4 ANG=0
| 13 X= 7.220 Y= 0.000 Z= 0.275 | 24 J= 24, 25 SEC=1 NSEG=1 ANG=0
| 14 X= 7.700 Y= 0.000 Z= 0.275 | 25 J= 25, 26 SEC=1 NSEG=1 ANG=0
| 15 X= 7.900 Y= 0.000 Z= 0.275 | 26 J= 26, 27 SEC=1 NSEG=1 ANG=0
| 16 X= 7.900 Y= 0.000 Z= 0.550 | 27 J= 27, 28 SEC=1 NSEG=1 ANG=0
| 17 X= 7.900 Y= 0.000 Z= 0.880 | 28 J= 28, 29 SEC=1 NSEG=4 ANG=0
| 18 X= 7.900 Y= 0.000 Z= 3.720 | 29 J= 29, 30 SEC=1 NSEG=4 ANG=0
| 19 X= 7.900 Y= 0.000 Z= 4.050 | 30 J= 30, 31 SEC=1 NSEG=1 ANG=0
| 20 X= 7.900 Y= 0.000 Z= 4.325 | 31 J= 31, 32 SEC=1 NSEG=1 ANG=0
| 21 X= 7.700 Y= 0.000 Z= 4.325 | 32 J= 32, 33 SEC=2 NSEG=1 ANG=180
| 22 X= 7.220 Y= 0.000 Z= 4.325 | 33 J= 33, 34 SEC=2 NSEG=1 ANG=180
| 23 X= 5.950 Y= 0.000 Z= 4.325 | 34 J= 34, 35 SEC=2 NSEG=4 ANG=180
| 24 X= 4.680 Y= 0.000 Z= 4.325 | 35 J= 35, 36 SEC=2 NSEG=1 ANG=180
| 25 X= 4.200 Y= 0.000 Z= 4.325 | 36 J= 36, 1 SEC=2 NSEG=1 ANG=180
| 26 X= 4.050 Y= 0.000 Z= 4.325 | 37 J= 26, 8 SEC=3 NSEG=4 ANG=0
27 X= 3.900 Y= 0.000 Z= 4.325
| 28 X= 3.420 Y= 0.000 Z= 4.325 | NLLINK
| 29 X= 2.150 Y= 0.000 Z= 4.325 | 1 J=1,37 NLP=SP1 ANG=0
| 30 X= 0.880 Y= 0.000 Z= 4.325 | 2 J=4,38 NLP=SP2 ANG=0
| 31 X= 0.400 Y= 0.000 Z= 4.325 | 3 J=5,39 NLP=SP2 ANG=0
| 32 X= 0.200 Y= 0.000 Z= 4.325 | 4 J=8,40 NLP=SP2 ANG=0
| 33 X= 0.200 Y= 0.000 Z= 4.050 | 5 J=11,41 NLP=SP2 ANG=0
| 34 X= 0.200 Y= 0.000 Z= 3.720 | 6 J=12,42 NLP=SP2 ANG=0
| 35 X= 0.200 Y= 0.000 Z= 0.880 | 7 J=15,43 NLP=SP1 ANG=0
36 X= 0.200 Y= 0.000 Z= 0.550
| 37 X= 0.200 Y= 0.000 Z= -0.225 | LOAD
| 38 X= 1.483 Y= 0.000 Z= -0.225 | NAME=SELFWGT SW=1
| 39 X= 2.767 Y= 0.000 Z= -0.225 | NAME=NWDEAD
| 40 X= 4.050 Y= 0.000 Z= -0.225 | TYPE=Distributed Span
| 41 X= 5.333 Y= 0.000 Z= -0.225 | ADD=20 RD=0,1 UZ=-76,-76
| 42 X= 6.617 Y= 0.000 Z= -0.225 | ADD=21 RD=0,1 UZ=-76,-76
| 43 X= 7.900 Y= 0.000 Z= -0.225 | ADD=22 RD=0,1 UZ=-76,-76
ADD=23 RD=0,1 UZ=-76,-76
| RESTRAINT | ADD=24 RD=0,1 UZ=-76,-76
| ADD=37 DOF=U1, U2, U3, R1, R2, R3 | ADD=25 RD=0,1 UZ=-76,-76
| ADD=38 DOF=U1, U2, U3, R1, R2, R3 | ADD=26 RD=0,1 UZ=-76,-76
| ADD=39 DOF=U1, U2, U3, R1, R2, R3 | ADD=27 RD=0,1 UZ=-76,-76
| ADD=40 DOF=U1, U2, U3, R1, R2, R3 | ADD=28 RD=0,1 UZ=-76,-76
| ADD=41 DOF=U1, U2, U3, R1, R2, R3 | ADD=29 RD=0,1 UZ=-76,-76
| ADD=42 DOF=U1, U2, U3, R1, R2, R3 | ADD=30 RD=0,1 UZ=-76,-76
| ADD=43 DOF=U1, U2, U3, R1, R2, R3 | ADD=31 RD=0,1 UZ=-76,-76
NAME=LIVEFULL
| SPRING | TYPE=Distributed Span
| ADD=1 U1=1e+010 | ADD=20 RD=0,1 UZ=-10,-10
ADD=21 RD=0,1 UZ=-10,-10
| MATERIAL | ADD=22 RD=0,1 UZ=-10,-10
| NAME=CONC IDES=C M=0.0001 W=24.5 | ADD=23 RD=0,1 UZ=-10,-10
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | ADD=24 RD=0,1 UZ=-10,-10
ADD=25 RD=0,1 UZ=-10,-10
| NLPROP | ADD=26 RD=0,1 UZ=-10,-10
| NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=27 RD=0,1 UZ=-10,-10
| DOF=U1 KE=9946.25 CE=0.99999 K=9946.25 OPEN=0 | ADD=28 RD=0,1 UZ=-10,-10
| NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=29 RD=0,1 UZ=-10,-10
| DOF=U1 KE=15164.6 CE=0.99999 K=15164.6 OPEN=0 | ADD=30 RD=0,1 UZ=-10,-10
ADD=31 RD=0,1 UZ=-10,-10
| FRAME SECTION | NAME=HORLIVE
| NAME=1 MAT=CONC SH=R T=0.55, 1 | TYPE=Distributed Span
| NAME=2 MAT=CONC SH=R T=0.4, 1 | ADD=15 RD=0,1 UX=-5,-5
| NAME=3 MAT=CONC SH=R T=0.3, 1 | ADD=16 RD=0,1 UX=-5,-5
ADD=17 RD=0,1 UX=-5,-5
| FRAME | ADD=18 RD=0,1 UX=-5,-5
| 1 J= 1, 2 SEC=1 NSEG=1 ANG=180 | ADD=19 RD=0,1 UX=-5,-5
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | ADD=32 RD=0,1 UX=5,5
| 3 J= 3, 4 SEC=1 NSEG=2 ANG=180 | ADD=33 RD=0,1 UX=5,5
| 4 J= 4, 5 SEC=1 NSEG=4 ANG=180 | ADD=34 RD=0,1 UX=5,5
| 5 J= 5, 6 SEC=1 NSEG=2 ANG=180 | ADD=35 RD=0,1 UX=5,5
| 6 J= 6, 7 SEC=1 NSEG=1 ANG=180 | ADD=36 RD=0,1 UX=5,5
| 7 J= 7, 8 SEC=1 NSEG=1 ANG=180 | NAME=NWSOFULL
TYPE=Distributed Span
| ADD=15 RD=0,1 UX=-79.088,-76.475 | OUTPUT
| ADD=16 RD=0,1 UX=-76.475,-73.34 | ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
| ADD=17 RD=0,1 UX=-73.34,-46.361 | ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*
ADD=18 RD=0,1 UX=-46.361,-43.225
ADD=19 RD=0,1 UX=-43.225,-40.613
ADD=32 RD=0,1 UX=40.613,43.225
ADD=33 RD=0,1 UX=43.225,46.361
ADD=34 RD=0,1 UX=46.361,73.34
ADD=35 RD=0,1 UX=73.34,76.475
ADD=36 RD=0,1 UX=76.475,79.088
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=HORLIVE
LOAD=NWSOFULL
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.52 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.52 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.52 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.52 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.52 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.52 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST7 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.95 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
NAME=HIST8 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.95 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
NAME=HIST9 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.95 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=0.5 AT=1
LOAD=NWSOFULL SF=0.5 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
HIST=HIST3 SF=1
HIST=HIST4 SF=1
HIST=HIST5 SF=1
HIST=HIST6 SF=1
NAME=SERVICE TYPE=ENVE
HIST=HIST7 SF=1
HIST=HIST8 SF=1
HIST=HIST9 SF=1

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | ADD=54 DOF=U1, U2, U3, R1, R2, R3
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | ADD=55 DOF=U1, U2, U3, R1, R2, R3
ADD=56 DOF=U1, U2, U3, R1, R2, R3
| JOINT | ADD=57 DOF=U1, U2, U3, R1, R2, R3
| 1 X= 0.200 Y= 0.000 Z= 0.275 | ADD=58 DOF=U1, U2, U3, R1, R2, R3
| 2 X= 0.400 Y= 0.000 Z= 0.275 | ADD=59 DOF=U1, U2, U3, R1, R2, R3
| 3 X= 0.880 Y= 0.000 Z= 0.275 | ADD=60 DOF=U1, U2, U3, R1, R2, R3
| 4 X= 1.483 Y= 0.000 Z= 0.275 | ADD=61 DOF=U1, U2, U3, R1, R2, R3
| 5 X= 2.767 Y= 0.000 Z= 0.275 | ADD=62 DOF=U1, U2, U3, R1, R2, R3
| 6 X= 3.420 Y= 0.000 Z= 0.275 | ADD=63 DOF=U1, U2, U3, R1, R2, R3
| 7 X= 3.900 Y= 0.000 Z= 0.275 | ADD=64 DOF=U1, U2, U3, R1, R2, R3
| 8 X= 4.050 Y= 0.000 Z= 0.275 | ADD=65 DOF=U1, U2, U3, R1, R2, R3
| 9 X= 4.200 Y= 0.000 Z= 0.275 | ADD=66 DOF=U1, U2, U3, R1, R2, R3
| 10 X= 4.680 Y= 0.000 Z= 0.275 | ADD=67 DOF=U1, U2, U3, R1, R2, R3
| 11 X= 5.333 Y= 0.000 Z= 0.275 | ADD=68 DOF=U1, U2, U3, R1, R2, R3
12 X= 6.617 Y= 0.000 Z= 0.275
| 13 X= 7.220 Y= 0.000 Z= 0.275 | SPRING
| 14 X= 7.700 Y= 0.000 Z= 0.275 | ADD=1 U1=8340.7 U3=11833
| 15 X= 7.900 Y= 0.000 Z= 0.275 | ADD=4 U1=12716.7
| 16 X= 7.900 Y= 0.000 Z= 0.550 | ADD=5 U1=12716.7
| 17 X= 7.900 Y= 0.000 Z= 0.880 | ADD=8 U1=12716.7
| 18 X= 7.900 Y= 0.000 Z= 1.288 | ADD=11 U1=12716.7
| 19 X= 7.900 Y= 0.000 Z= 2.300 | ADD=12 U1=12716.7
| 20 X= 7.900 Y= 0.000 Z= 3.312 | ADD=15 U1=8340.7 U3=11833
| 21 X= 7.900 Y= 0.000 Z= 3.720 | ADD=18 U3=15332.9
| 22 X= 7.900 Y= 0.000 Z= 4.050 | ADD=19 U3=15332.9
| 23 X= 7.900 Y= 0.000 Z= 4.325 | ADD=20 U3=15332.9
| 24 X= 7.700 Y= 0.000 Z= 4.325 | ADD=23 U1=8340.7 U3=11833
| 25 X= 7.220 Y= 0.000 Z= 4.325 | ADD=26 U1=12716.7
| 26 X= 6.617 Y= 0.000 Z= 4.325 | ADD=27 U1=12716.7
| 27 X= 5.333 Y= 0.000 Z= 4.325 | ADD=30 U1=12716.7
| 28 X= 4.680 Y= 0.000 Z= 4.325 | ADD=33 U1=12716.7
| 29 X= 4.200 Y= 0.000 Z= 4.325 | ADD=34 U1=12716.7
| 30 X= 4.050 Y= 0.000 Z= 4.325 | ADD=37 U1=8340.7 U3=11833
| 31 X= 3.900 Y= 0.000 Z= 4.325 | ADD=40 U3=15332.9
| 32 X= 3.420 Y= 0.000 Z= 4.325 | ADD=41 U3=15332.9
| 33 X= 2.767 Y= 0.000 Z= 4.325 | ADD=42 U3=15332.9
34 X= 1.483 Y= 0.000 Z= 4.325
| 35 X= 0.880 Y= 0.000 Z= 4.325 | MATERIAL
| 36 X= 0.400 Y= 0.000 Z= 4.325 | NAME=CONC IDES=C M=0.0001 W=24.5
| 37 X= 0.200 Y= 0.000 Z= 4.325 | T=0 E=2.7e+007 U=0.17 A=9.99e-006
38 X= 0.200 Y= 0.000 Z= 4.050
| 39 X= 0.200 Y= 0.000 Z= 3.720 | NLPROP
| 40 X= 0.200 Y= 0.000 Z= 3.313 | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 41 X= 0.200 Y= 0.000 Z= 2.300 | DOF=U1 KE=25022.1 CE=0.99999 K=25022.1 OPEN=0
| 42 X= 0.200 Y= 0.000 Z= 1.288 | NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 43 X= 0.200 Y= 0.000 Z= 0.880 | DOF=U1 KE=38150.2 CE=0.99999 K=38150.2 OPEN=0
| 44 X= 0.200 Y= 0.000 Z= 0.550 | NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 45 X= 0.200 Y= 0.000 Z= -0.225 | DOF=U1 KE=35499 CE=0.99999 K=35499 OPEN=0
| 46 X= 1.483 Y= 0.000 Z= -0.225 | NAME=SP4 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 47 X= 2.767 Y= 0.000 Z= -0.225 | DOF=U1 KE=45998.7 CE=0.99999 K=45998.7 OPEN=0
48 X= 4.050 Y= 0.000 Z= -0.225
| 49 X= 5.333 Y= 0.000 Z= -0.225 | FRAME SECTION
| 50 X= 6.617 Y= 0.000 Z= -0.225 | NAME=1 MAT=CONC SH=R T=0.55, 1
| 51 X= 7.900 Y= 0.000 Z= -0.225 | NAME=2 MAT=CONC SH=R T=0.4, 1
| 52 X= 8.400 Y= 0.000 Z= 0.275 | NAME=3 MAT=CONC SH=R T=0.3, 1
53 X= 8.400 Y= 0.000 Z= 1.288
| 54 X= 8.400 Y= 0.000 Z= 2.300 | FRAME
| 55 X= 8.400 Y= 0.000 Z= 3.312 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 56 X= 8.400 Y= 0.000 Z= 4.325 | 2 J= 2, 3 SEC=1 NSEG=1 ANG=180
| 57 X= 7.900 Y= 0.000 Z= 4.825 | 3 J= 3, 4 SEC=1 NSEG=2 ANG=180
| 58 X= 6.617 Y= 0.000 Z= 4.825 | 4 J= 4, 5 SEC=1 NSEG=4 ANG=180
| 59 X= 5.333 Y= 0.000 Z= 4.825 | 5 J= 5, 6 SEC=1 NSEG=2 ANG=180
| 60 X= 4.050 Y= 0.000 Z= 4.825 | 6 J= 6, 7 SEC=1 NSEG=1 ANG=180
| 61 X= 2.767 Y= 0.000 Z= 4.825 | 7 J= 7, 8 SEC=1 NSEG=1 ANG=180
| 62 X= 1.483 Y= 0.000 Z= 4.825 | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| 63 X= 0.200 Y= 0.000 Z= 4.825 | 9 J= 9, 10 SEC=1 NSEG=1 ANG=180
| 64 X= -0.300 Y= 0.000 Z= 4.325 | 10 J= 10, 11 SEC=1 NSEG=2 ANG=180
| 65 X= -0.300 Y= 0.000 Z= 3.313 | 11 J= 11, 12 SEC=1 NSEG=4 ANG=180
| 66 X= -0.300 Y= 0.000 Z= 2.300 | 12 J= 12, 13 SEC=1 NSEG=2 ANG=180
| 67 X= -0.300 Y= 0.000 Z= 1.288 | 13 J= 13, 14 SEC=1 NSEG=1 ANG=180
| 68 X= -0.300 Y= 0.000 Z= 0.275 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=180
15 J= 15, 16 SEC=2 NSEG=1 ANG=0
| RESTRAINT | 16 J= 16, 17 SEC=2 NSEG=1 ANG=0
| ADD=45 DOF=U1, U2, U3, R1, R2, R3 | 17 J= 17, 18 SEC=2 NSEG=1 ANG=0
| ADD=46 DOF=U1, U2, U3, R1, R2, R3 | 18 J= 18, 19 SEC=2 NSEG=4 ANG=0
| ADD=47 DOF=U1, U2, U3, R1, R2, R3 | 19 J= 19, 20 SEC=2 NSEG=4 ANG=0
| ADD=48 DOF=U1, U2, U3, R1, R2, R3 | 20 J= 20, 21 SEC=2 NSEG=1 ANG=0
| ADD=49 DOF=U1, U2, U3, R1, R2, R3 | 21 J= 21, 22 SEC=2 NSEG=1 ANG=0
| ADD=50 DOF=U1, U2, U3, R1, R2, R3 | 22 J= 22, 23 SEC=2 NSEG=1 ANG=0
| ADD=51 DOF=U1, U2, U3, R1, R2, R3 | 23 J= 23, 24 SEC=1 NSEG=1 ANG=0
| ADD=52 DOF=U1, U2, U3, R1, R2, R3 | 24 J= 24, 25 SEC=1 NSEG=1 ANG=0
| ADD=53 DOF=U1, U2, U3, R1, R2, R3 | 25 J= 25, 26 SEC=1 NSEG=2 ANG=0
| 26 J= 26, 27 SEC=1 NSEG=4 ANG=0 | ADD=26 RD=0,1 UX=2.3887,2.3887
| 27 J= 27, 28 SEC=1 NSEG=2 ANG=0 | ADD=27 RD=0,1 UX=2.3887,2.3887
| 28 J= 28, 29 SEC=1 NSEG=1 ANG=0 | ADD=28 RD=0,1 UX=2.3887,2.3887
| 29 J= 29, 30 SEC=1 NSEG=1 ANG=0 | ADD=29 RD=0,1 UX=2.3887,2.3887
| 30 J= 30, 31 SEC=1 NSEG=1 ANG=0 | ADD=30 RD=0,1 UX=2.3887,2.3887
| 31 J= 31, 32 SEC=1 NSEG=1 ANG=0 | ADD=31 RD=0,1 UX=2.3887,2.3887
| 32 J= 32, 33 SEC=1 NSEG=2 ANG=0 | ADD=32 RD=0,1 UX=2.3887,2.3887
| 33 J= 33, 34 SEC=1 NSEG=4 ANG=0 | ADD=33 RD=0,1 UX=2.3887,2.3887
| 34 J= 34, 35 SEC=1 NSEG=2 ANG=0 | ADD=34 RD=0,1 UX=2.3887,2.3887
| 35 J= 35, 36 SEC=1 NSEG=1 ANG=0 | ADD=35 RD=0,1 UX=2.3887,2.3887
| 36 J= 36, 37 SEC=1 NSEG=1 ANG=0 | ADD=36 RD=0,1 UX=2.3887,2.3887
| 37 J= 37, 38 SEC=2 NSEG=1 ANG=180 | NAME=SEWALL
| 38 J= 38, 39 SEC=2 NSEG=1 ANG=180 | TYPE=Distributed Span
| 39 J= 39, 40 SEC=2 NSEG=1 ANG=180 | ADD=15 RD=0,1 UX=0,0.9545
| 40 J= 40, 41 SEC=2 NSEG=4 ANG=180 | ADD=16 RD=0,1 UX=0.9545,2.0909
| 41 J= 41, 42 SEC=2 NSEG=4 ANG=180 | ADD=17 RD=0,1 UX=2.0909,3.3635
| 42 J= 42, 43 SEC=2 NSEG=1 ANG=180 | ADD=18 RD=0,1 UX=3.3635,6.318
| 43 J= 43, 44 SEC=2 NSEG=1 ANG=180 | ADD=19 RD=0,1 UX=6.318,8.8634
| 44 J= 44, 1 SEC=2 NSEG=1 ANG=180 | ADD=20 RD=0,1 UX=8.8634,9.7725
| 45 J= 30, 8 SEC=3 NSEG=4 ANG=0 | ADD=21 RD=0,1 UX=9.7725,10.4543
ADD=22 RD=0,1 UX=10.4543,10.9542
| NLLINK | ADD=37 RD=0,1 UX=10.9542,10.4543
| 1 J=1,45 NLP=SP1 ANG=0 | ADD=38 RD=0,1 UX=10.4543,9.7725
| 2 J=4,46 NLP=SP2 ANG=0 | ADD=39 RD=0,1 UX=9.7725,8.8634
| 3 J=5,47 NLP=SP2 ANG=0 | ADD=40 RD=0,1 UX=8.8634,6.318
| 4 J=8,48 NLP=SP2 ANG=0 | ADD=41 RD=0,1 UX=6.318,3.3635
| 5 J=11,49 NLP=SP2 ANG=0 | ADD=42 RD=0,1 UX=3.3635,2.0909
| 6 J=12,50 NLP=SP2 ANG=0 | ADD=43 RD=0,1 UX=2.0909,0.9545
| 7 J=15,51 NLP=SP1 ANG=0 | ADD=44 RD=0,1 UX=0.9545,0
| 8 J=15,52 NLP=SP3 ANG=180 | NAME=SEPRINSH
| 9 J=18,53 NLP=SP4 ANG=180 | TYPE=Distributed Span
| 10 J=19,54 NLP=SP4 ANG=180 | ADD=1 RD=0,1 UX=-1.47,-1.47
| 11 J=20,55 NLP=SP4 ANG=180 | ADD=2 RD=0,1 UX=-1.47,-1.47
| 12 J=23,56 NLP=SP3 ANG=180 | ADD=3 RD=0,1 UX=-1.47,-1.47
| 13 J=23,57 NLP=SP1 ANG=0 | ADD=4 RD=0,1 UX=-1.47,-1.47
| 14 J=26,58 NLP=SP2 ANG=0 | ADD=5 RD=0,1 UX=-1.47,-1.47
| 15 J=27,59 NLP=SP2 ANG=0 | ADD=6 RD=0,1 UX=-1.47,-1.47
| 16 J=30,60 NLP=SP2 ANG=0 | ADD=7 RD=0,1 UX=-1.47,-1.47
| 17 J=33,61 NLP=SP2 ANG=0 | ADD=8 RD=0,1 UX=-1.47,-1.47
| 18 J=34,62 NLP=SP2 ANG=0 | ADD=9 RD=0,1 UX=-1.47,-1.47
| 19 J=37,63 NLP=SP1 ANG=0 | ADD=10 RD=0,1 UX=-1.47,-1.47
| 20 J=37,64 NLP=SP3 ANG=180 | ADD=11 RD=0,1 UX=-1.47,-1.47
| 21 J=40,65 NLP=SP4 ANG=180 | ADD=12 RD=0,1 UX=-1.47,-1.47
| 22 J=41,66 NLP=SP4 ANG=180 | ADD=13 RD=0,1 UX=-1.47,-1.47
| 23 J=42,67 NLP=SP4 ANG=180 | ADD=14 RD=0,1 UX=-1.47,-1.47
| 24 J=1,68 NLP=SP3 ANG=180 | ADD=15 RD=0,1 UZ=1.12,1.12
ADD=16 RD=0,1 UZ=1.12,1.12
| LOAD | ADD=17 RD=0,1 UZ=1.12,1.12
| NAME=SELFWGT SW=1 | ADD=18 RD=0,1 UZ=1.12,1.12
| NAME=NWDEAD | ADD=19 RD=0,1 UZ=1.12,1.12
| TYPE=Distributed Span | ADD=20 RD=0,1 UZ=1.12,1.12
| ADD=23 RD=0,1 UZ=-76,-76 | ADD=21 RD=0,1 UZ=1.12,1.12
| ADD=24 RD=0,1 UZ=-76,-76 | ADD=22 RD=0,1 UZ=1.12,1.12
| ADD=25 RD=0,1 UZ=-76,-76 | ADD=23 RD=0,1 UX=0.77,0.77
| ADD=26 RD=0,1 UZ=-76,-76 | ADD=24 RD=0,1 UX=0.77,0.77
| ADD=27 RD=0,1 UZ=-76,-76 | ADD=25 RD=0,1 UX=0.77,0.77
| ADD=28 RD=0,1 UZ=-76,-76 | ADD=26 RD=0,1 UX=0.77,0.77
| ADD=29 RD=0,1 UZ=-76,-76 | ADD=27 RD=0,1 UX=0.77,0.77
| ADD=30 RD=0,1 UZ=-76,-76 | ADD=28 RD=0,1 UX=0.77,0.77
| ADD=31 RD=0,1 UZ=-76,-76 | ADD=29 RD=0,1 UX=0.77,0.77
| ADD=32 RD=0,1 UZ=-76,-76 | ADD=30 RD=0,1 UX=0.77,0.77
| ADD=33 RD=0,1 UZ=-76,-76 | ADD=31 RD=0,1 UX=0.77,0.77
| ADD=34 RD=0,1 UZ=-76,-76 | ADD=32 RD=0,1 UX=0.77,0.77
| ADD=35 RD=0,1 UZ=-76,-76 | ADD=33 RD=0,1 UX=0.77,0.77
| ADD=36 RD=0,1 UZ=-76,-76 | ADD=34 RD=0,1 UX=0.77,0.77
| NAME=LIVEFULL | ADD=35 RD=0,1 UX=0.77,0.77
| TYPE=Distributed Span | ADD=36 RD=0,1 UX=0.77,0.77
| ADD=23 RD=0,1 UZ=-10,-10 | ADD=37 RD=0,1 UZ=-1.12,-1.12
| ADD=24 RD=0,1 UZ=-10,-10 | ADD=38 RD=0,1 UZ=-1.12,-1.12
| ADD=25 RD=0,1 UZ=-10,-10 | ADD=39 RD=0,1 UZ=-1.12,-1.12
| ADD=26 RD=0,1 UZ=-10,-10 | ADD=40 RD=0,1 UZ=-1.12,-1.12
| ADD=27 RD=0,1 UZ=-10,-10 | ADD=41 RD=0,1 UZ=-1.12,-1.12
| ADD=28 RD=0,1 UZ=-10,-10 | ADD=42 RD=0,1 UZ=-1.12,-1.12
| ADD=29 RD=0,1 UZ=-10,-10 | ADD=43 RD=0,1 UZ=-1.12,-1.12
| ADD=30 RD=0,1 UZ=-10,-10 | ADD=44 RD=0,1 UZ=-1.12,-1.12
| ADD=31 RD=0,1 UZ=-10,-10 | NAME=SEINER
| ADD=32 RD=0,1 UZ=-10,-10 | TYPE=Distributed Span
| ADD=33 RD=0,1 UZ=-10,-10 | ADD=1 RD=0,1 UX=1.88677,1.88677
| ADD=34 RD=0,1 UZ=-10,-10 | ADD=2 RD=0,1 UX=1.88677,1.88677
| ADD=35 RD=0,1 UZ=-10,-10 | ADD=3 RD=0,1 UX=1.88677,1.88677
| ADD=36 RD=0,1 UZ=-10,-10 | ADD=4 RD=0,1 UX=1.88677,1.88677
| NAME=SEUPSLAB | ADD=5 RD=0,1 UX=1.88677,1.88677
| TYPE=Distributed Span | ADD=6 RD=0,1 UX=1.88677,1.88677
| ADD=23 RD=0,1 UX=2.3887,2.3887 | ADD=7 RD=0,1 UX=1.88677,1.88677
| ADD=24 RD=0,1 UX=2.3887,2.3887 | ADD=8 RD=0,1 UX=1.88677,1.88677
| ADD=25 RD=0,1 UX=2.3887,2.3887 | ADD=9 RD=0,1 UX=1.88677,1.88677
ADD=10 RD=0,1 UX=1.88677,1.88677
ADD=11 RD=0,1 UX=1.88677,1.88677
ADD=12 RD=0,1 UX=1.88677,1.88677
ADD=13 RD=0,1 UX=1.88677,1.88677
ADD=14 RD=0,1 UX=1.88677,1.88677
ADD=15 RD=0,1 UX=1.3722,1.37866
ADD=16 RD=0,1 UX=1.37866,1.38643
ADD=17 RD=0,1 UX=1.38643,1.396
ADD=18 RD=0,1 UX=1.396,1.41982
ADD=19 RD=0,1 UX=1.41982,1.44363
ADD=20 RD=0,1 UX=1.44363,1.45322
ADD=21 RD=0,1 UX=1.45322,1.46098
ADD=22 RD=0,1 UX=1.46098,1.46745
ADD=23 RD=0,1 UX=2.01775,2.01775
ADD=24 RD=0,1 UX=2.01775,2.01775
ADD=25 RD=0,1 UX=2.01775,2.01775
ADD=26 RD=0,1 UX=2.01775,2.01775
ADD=27 RD=0,1 UX=2.01775,2.01775
ADD=28 RD=0,1 UX=2.01775,2.01775
ADD=29 RD=0,1 UX=2.01775,2.01775
ADD=30 RD=0,1 UX=2.01775,2.01775
ADD=31 RD=0,1 UX=2.01775,2.01775
ADD=32 RD=0,1 UX=2.01775,2.01775
ADD=33 RD=0,1 UX=2.01775,2.01775
ADD=34 RD=0,1 UX=2.01775,2.01775
ADD=35 RD=0,1 UX=2.01775,2.01775
ADD=36 RD=0,1 UX=2.01775,2.01775
ADD=37 RD=0,1 UX=1.46745,1.46098
ADD=38 RD=0,1 UX=1.46098,1.45322
ADD=39 RD=0,1 UX=1.45322,1.44363
ADD=40 RD=0,1 UX=1.44363,1.41982
ADD=41 RD=0,1 UX=1.41982,1.396
ADD=42 RD=0,1 UX=1.396,1.38643
ADD=43 RD=0,1 UX=1.38643,1.37866
ADD=44 RD=0,1 UX=1.37866,1.3722
ADD=45 RD=0,1 UX=1.10059,1.02915
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=SEUPSLAB
LOAD=SEWALL
LOAD=SEPRINSH
LOAD=SEINER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.95 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=1 AT=1
LOAD=SEWALL SF=1 AT=1
LOAD=SEPRINSH SF=1 AT=1
LOAD=SEINER SF=1 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.95 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=-1 AT=1
LOAD=SEWALL SF=-1 AT=1
LOAD=SEPRINSH SF=-1 AT=1
LOAD=SEINER SF=-1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 15 | ULTIMATE MIN | 0 | -325.0139 | -228.8608 | -145.1692
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 15 | ULTIMATE MIN | 1 | -321.7799 | -192.4369 | -87.2671
| 1 | ULTIMATE MIN | 0 | -228.8608 | -178.8294 | -145.1692 | 16 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 1 | ULTIMATE MIN | 1 | -228.8608 | -182.0634 | -109.0799 | 16 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 16 | ULTIMATE MIN | 0 | -321.7799 | -192.4369 | -87.2671
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 25.2291 | 16 | ULTIMATE MIN | 1 | -317.8991 | -150.2458 | -30.77
| 2 | ULTIMATE MIN | 0 | -228.8608 | -182.0634 | -109.0799 | 17 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 2 | ULTIMATE MIN | 1 | -228.8608 | -189.825 | -29.2564 | 17 | ULTIMATE MAX | 0.25 | 0 | 0 | 49.6905
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 25.2291 | 17 | ULTIMATE MAX | 0.5 | 0 | 12.6229 | 67.7878
| 3 | ULTIMATE MAX | 0.5 | 0 | 0 | 76.2721 | 17 | ULTIMATE MAX | 0.75 | 0 | 82.462 | 33.5794
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 128.7851 | 17 | ULTIMATE MAX | 1 | 0 | 144.6391 | 0
| 3 | ULTIMATE MIN | 0 | -228.8608 | -189.825 | -29.2564 | 17 | ULTIMATE MIN | 0 | -317.8991 | -150.2458 | -30.77
| 3 | ULTIMATE MIN | 0.5 | -228.8608 | -194.7002 | 0 | 17 | ULTIMATE MIN | 0.25 | -309.5495 | -65.0826 | 0
| 3 | ULTIMATE MIN | 1 | -228.8608 | -199.5755 | 0 | 17 | ULTIMATE MIN | 0.5 | -301.1999 | 0 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 41.771 | 128.7851 | 17 | ULTIMATE MIN | 0.75 | -292.8503 | 0 | -1.9194
| 4 | ULTIMATE MAX | 0.25 | 0 | 36.5804 | 116.2097 | 17 | ULTIMATE MIN | 1 | -284.5007 | 0 | -51.5336
| 4 | ULTIMATE MAX | 0.5 | 0 | 31.3898 | 105.3005 | 18 | ULTIMATE MAX | 0 | 0 | 144.6363 | 0
| 4 | ULTIMATE MAX | 0.75 | 0 | 26.1992 | 96.0574 | 18 | ULTIMATE MAX | 1 | 0 | 170.927 | 0
| 4 | ULTIMATE MAX | 1 | 0 | 21.0087 | 88.4805 | 18 | ULTIMATE MIN | 0 | -284.5007 | 0 | -51.5336
| 4 | ULTIMATE MIN | 0 | -228.8608 | 0 | 0 | 18 | ULTIMATE MIN | 1 | -280.6199 | 0 | -103.5806
| 4 | ULTIMATE MIN | 0.25 | -228.8608 | 0 | 0 | 19 | ULTIMATE MAX | 0 | 0 | 170.927 | 0
| 4 | ULTIMATE MIN | 0.5 | -228.8608 | 0 | 0 | 19 | ULTIMATE MAX | 1 | 0 | 191.5714 | 0
| 4 | ULTIMATE MIN | 0.75 | -228.8608 | -1.7791 | 0 | 19 | ULTIMATE MIN | 0 | -280.6199 | 0 | -103.5806
| 4 | ULTIMATE MIN | 1 | -228.8608 | -5.672 | 0 | 19 | ULTIMATE MIN | 1 | -277.3859 | 0 | -153.3949
| 5 | ULTIMATE MAX | 0 | 0 | 240.2608 | 88.4805 | 20 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 0.5 | 0 | 234.9813 | 15.5559 | 20 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 1 | 0 | 229.7018 | 0 | 20 | ULTIMATE MIN | 0 | -191.5714 | -277.3859 | -153.3949
| 5 | ULTIMATE MIN | 0 | -228.8608 | 0 | 0 | 20 | ULTIMATE MIN | 1 | -191.5714 | -247.8479 | -102.7019
| 5 | ULTIMATE MIN | 0.5 | -228.8608 | 0 | 0 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MIN | 1 | -228.8608 | 0 | -64.9622 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 43.7199
| 6 | ULTIMATE MAX | 0 | 0 | 229.7018 | 0 | 21 | ULTIMATE MIN | 0 | -191.5714 | -247.8479 | -102.7019
| 6 | ULTIMATE MAX | 1 | 0 | 221.9402 | 0 | 21 | ULTIMATE MIN | 1 | -191.5714 | -176.9567 | -11.2704
| 6 | ULTIMATE MIN | 0 | -228.8608 | 0 | -64.9622 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 43.7199
| 6 | ULTIMATE MIN | 1 | -228.8608 | 0 | -173.3563 | 22 | ULTIMATE MAX | 0.25 | 0 | 0 | 85.3722
| 7 | ULTIMATE MAX | 0 | 0 | 221.9402 | 0 | 22 | ULTIMATE MAX | 0.5 | 0 | 0 | 112.1365
| 7 | ULTIMATE MAX | 1 | 0 | 219.5147 | 0 | 22 | ULTIMATE MAX | 0.75 | 0 | 0 | 124.0127
| 7 | ULTIMATE MIN | 0 | -228.8608 | 0 | -173.3563 | 22 | ULTIMATE MAX | 1 | 0 | 32.9329 | 121.0008
| 7 | ULTIMATE MIN | 1 | -228.8608 | 0 | -206.4654 | 22 | ULTIMATE MIN | 0 | -191.5714 | -176.9567 | -11.2704
| 8 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 22 | ULTIMATE MIN | 0.25 | -191.5714 | -130.0652 | 0
| 8 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 22 | ULTIMATE MIN | 0.5 | -191.5714 | -83.1736 | 0
| 8 | ULTIMATE MIN | 0 | -228.8608 | -219.5147 | -206.4654 | 22 | ULTIMATE MIN | 0.75 | -191.5714 | -38.2743 | 0
| 8 | ULTIMATE MIN | 1 | -228.8608 | -221.9402 | -173.3563 | 22 | ULTIMATE MIN | 1 | -191.5714 | 0 | 0
| 9 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 0 | 0 | 32.9321 | 121.0008
| 9 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 0.25 | 0 | 79.8236 | 103.1008
| 9 | ULTIMATE MIN | 0 | -228.8608 | -221.9402 | -173.3563 | 23 | ULTIMATE MAX | 0.5 | 0 | 126.7152 | 70.3128
| 9 | ULTIMATE MIN | 1 | -228.8608 | -229.7018 | -64.9622 | 23 | ULTIMATE MAX | 0.75 | 0 | 173.6068 | 29.6167
| 10 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 220.4984 | 0
| 10 | ULTIMATE MAX | 0.5 | 0 | 0 | 15.5559 | 23 | ULTIMATE MIN | 0 | -191.5714 | 0 | 0
| 10 | ULTIMATE MAX | 1 | 0 | 0 | 88.4805 | 23 | ULTIMATE MIN | 0.25 | -191.5714 | 0 | 0
| 10 | ULTIMATE MIN | 0 | -228.8608 | -229.7018 | -64.9622 | 23 | ULTIMATE MIN | 0.5 | -191.5714 | 0 | 0
| 10 | ULTIMATE MIN | 0.5 | -228.8608 | -234.9813 | 0 | 23 | ULTIMATE MIN | 0.75 | -191.5714 | 0 | 0
| 10 | ULTIMATE MIN | 1 | -228.8608 | -240.2608 | 0 | 23 | ULTIMATE MIN | 1 | -191.5714 | 0 | -39.9275
| 11 | ULTIMATE MAX | 0 | 0 | 5.6717 | 88.4805 | 24 | ULTIMATE MAX | 0 | 0 | 220.4984 | 0
| 11 | ULTIMATE MAX | 0.25 | 0 | 1.7787 | 96.0574 | 24 | ULTIMATE MAX | 1 | 0 | 291.3896 | 0
| 11 | ULTIMATE MAX | 0.5 | 0 | 0 | 105.3005 | 24 | ULTIMATE MIN | 0 | -191.5714 | 0 | -39.9275
| 11 | ULTIMATE MAX | 0.75 | 0 | 0 | 116.2097 | 24 | ULTIMATE MIN | 1 | -191.5714 | 0 | -162.7806
| 11 | ULTIMATE MAX | 1 | 0 | 0 | 128.7851 | 25 | ULTIMATE MAX | 0 | 0 | 291.3896 | 0
| 11 | ULTIMATE MIN | 0 | -228.8608 | -21.0087 | 0 | 25 | ULTIMATE MAX | 1 | 0 | 313.5431 | 0
| 11 | ULTIMATE MIN | 0.25 | -228.8608 | -26.1992 | 0 | 25 | ULTIMATE MIN | 0 | -191.5714 | 0 | -162.7806
| 11 | ULTIMATE MIN | 0.5 | -228.8608 | -31.3898 | 0 | 25 | ULTIMATE MIN | 1 | -191.5714 | 0 | -208.1506
| 11 | ULTIMATE MIN | 0.75 | -228.8608 | -36.5804 | 0 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MIN | 1 | -228.8608 | -41.771 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 12 | ULTIMATE MAX | 0 | 0 | 199.5755 | 128.7851 | 26 | ULTIMATE MIN | 0 | -191.5714 | -313.5431 | -208.1506
| 12 | ULTIMATE MAX | 0.5 | 0 | 194.7002 | 76.2721 | 26 | ULTIMATE MIN | 1 | -191.5714 | -291.3896 | -162.7806
| 12 | ULTIMATE MAX | 1 | 0 | 189.825 | 25.2291 | 27 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 12 | ULTIMATE MIN | 0 | -228.8608 | 0 | 0 | 27 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 12 | ULTIMATE MIN | 0.5 | -228.8608 | 0 | 0 | 27 | ULTIMATE MIN | 0 | -191.5714 | -291.3896 | -162.7806
| 12 | ULTIMATE MIN | 1 | -228.8608 | 0 | -29.2557 | 27 | ULTIMATE MIN | 1 | -191.5714 | -220.4984 | -39.9275
| 13 | ULTIMATE MAX | 0 | 0 | 189.825 | 25.2291 | 28 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 13 | ULTIMATE MAX | 1 | 0 | 182.0634 | 0 | 28 | ULTIMATE MAX | 0.25 | 0 | 0 | 29.6167
| 13 | ULTIMATE MIN | 0 | -228.8608 | 0 | -29.2557 | 28 | ULTIMATE MAX | 0.5 | 0 | 0 | 70.3128
| 13 | ULTIMATE MIN | 1 | -228.8608 | 0 | -109.0799 | 28 | ULTIMATE MAX | 0.75 | 0 | 0 | 103.1008
| 14 | ULTIMATE MAX | 0 | 0 | 182.0634 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 0 | 121.0008
| 14 | ULTIMATE MAX | 1 | 0 | 178.8294 | 0 | 28 | ULTIMATE MIN | 0 | -191.5714 | -220.4984 | -39.9275
| 14 | ULTIMATE MIN | 0 | -228.8608 | 0 | -109.0799 | 28 | ULTIMATE MIN | 0.25 | -191.5714 | -173.6068 | 0
| 14 | ULTIMATE MIN | 1 | -228.8608 | 0 | -145.1692 | 28 | ULTIMATE MIN | 0.5 | -191.5714 | -126.7152 | 0
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 0.75 | -191.5714 | -79.8236 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 1 | -191.5714 | -32.9321 | 0
| FRAME | LOAD | DIST | P | V2 | M3
| 29 | ULTIMATE MAX | 0 | 0 | 0 | 121.0008
| 29 | ULTIMATE MAX | 0.25 | 0 | 38.2743 | 124.0127
| 29 | ULTIMATE MAX | 0.5 | 0 | 83.1736 | 112.1365
| 29 | ULTIMATE MAX | 0.75 | 0 | 130.0652 | 85.3722
| 29 | ULTIMATE MAX | 1 | 0 | 176.9567 | 43.7199
| 29 | ULTIMATE MIN | 0 | -191.5714 | -32.933 | 0
| 29 | ULTIMATE MIN | 0.25 | -191.5714 | 0 | 0
| 29 | ULTIMATE MIN | 0.5 | -191.5714 | 0 | 0
| 29 | ULTIMATE MIN | 0.75 | -191.5714 | 0 | 0
| 29 | ULTIMATE MIN | 1 | -191.5714 | 0 | -11.27
| 30 | ULTIMATE MAX | 0 | 0 | 176.9567 | 43.7199
| 30 | ULTIMATE MAX | 1 | 0 | 247.8479 | 0
| 30 | ULTIMATE MIN | 0 | -191.5714 | 0 | -11.27
| 30 | ULTIMATE MIN | 1 | -191.5714 | 0 | -102.7014
| 31 | ULTIMATE MAX | 0 | 0 | 247.8479 | 0
| 31 | ULTIMATE MAX | 1 | 0 | 277.3859 | 0
| 31 | ULTIMATE MIN | 0 | -191.5714 | 0 | -102.7014
| 31 | ULTIMATE MIN | 1 | -191.5714 | 0 | -153.3944
| 32 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 32 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 32 | ULTIMATE MIN | 0 | -277.3859 | -191.5714 | -153.3944
| 32 | ULTIMATE MIN | 1 | -280.6199 | -170.927 | -103.58
| 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 33 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 33 | ULTIMATE MIN | 0 | -280.6199 | -170.927 | -103.58
| 33 | ULTIMATE MIN | 1 | -284.5007 | -144.6363 | -51.5331
| 34 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 34 | ULTIMATE MAX | 0.25 | 0 | 0 | 33.5796
| 34 | ULTIMATE MAX | 0.5 | 0 | 0 | 67.7879
| 34 | ULTIMATE MAX | 0.75 | 0 | 65.0826 | 49.6903
| 34 | ULTIMATE MAX | 1 | 0 | 150.2458 | 0
| 34 | ULTIMATE MIN | 0 | -284.5007 | -144.6388 | -51.5331
| 34 | ULTIMATE MIN | 0.25 | -292.8503 | -82.4617 | -1.9194
| 34 | ULTIMATE MIN | 0.5 | -301.1999 | -12.6226 | 0
| 34 | ULTIMATE MIN | 0.75 | -309.5495 | 0 | 0
| 34 | ULTIMATE MIN | 1 | -317.8991 | 0 | -30.77
| 35 | ULTIMATE MAX | 0 | 0 | 150.2458 | 0
| 35 | ULTIMATE MAX | 1 | 0 | 192.4369 | 0
| 35 | ULTIMATE MIN | 0 | -317.8991 | 0 | -30.77
| 35 | ULTIMATE MIN | 1 | -321.7799 | 0 | -87.2671
| 36 | ULTIMATE MAX | 0 | 0 | 192.4369 | 0
| 36 | ULTIMATE MAX | 1 | 0 | 228.8608 | 0
| 36 | ULTIMATE MIN | 0 | -321.7799 | 0 | -87.2671
| 36 | ULTIMATE MIN | 1 | -325.0139 | 0 | -145.1692
| 37 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0.25 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0.5 | 0 | 0 | 5e-06
| 37 | ULTIMATE MAX | 0.75 | 0 | 0 | 0.000135
| 37 | ULTIMATE MAX | 1 | 0 | 0 | 0.000265
| 37 | ULTIMATE MIN | 0 | -627.0861 | -0.000129 | -0.000256
| 37 | ULTIMATE MIN | 0.25 | -636.0164 | -0.000129 | -0.000125
| 37 | ULTIMATE MIN | 0.5 | -644.9466 | -0.000129 | 0
| 37 | ULTIMATE MIN | 0.75 | -653.8769 | -0.000129 | 0
| 37 | ULTIMATE MIN | 1 | -662.8071 | -0.000129 | 0
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 16 | SERVICE MAX | 1 | 0 | 0 | 0
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 16 | SERVICE MIN | 0 | -214.2783 | -121.9086 | -57.2426
| 1 | SERVICE MIN | 0 | -144.6735 | -117.0894 | -93.7082 | 16 | SERVICE MIN | 1 | -211.0443 | -95.5391 | -21.5997
| 1 | SERVICE MIN | 1 | -144.6735 | -119.7844 | -70.9285 | 17 | SERVICE MAX | 0 | 0 | 0 | 0
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 17 | SERVICE MAX | 0.25 | 0 | 0 | 28.1631
| 2 | SERVICE MAX | 1 | 0 | 0 | 17.188 | 17 | SERVICE MAX | 0.5 | 0 | 6.7575 | 40.7242
| 2 | SERVICE MIN | 0 | -144.6735 | -119.7844 | -70.9285 | 17 | SERVICE MAX | 0.75 | 0 | 50.4069 | 20.5942
| 2 | SERVICE MIN | 1 | -144.6735 | -126.2524 | -15.8011 | 17 | SERVICE MAX | 1 | 0 | 89.2676 | 0
| 3 | SERVICE MAX | 0 | 0 | 0 | 17.188 | 17 | SERVICE MIN | 0 | -211.0443 | -95.5391 | -21.5997
| 3 | SERVICE MAX | 0.5 | 0 | 0 | 51.538 | 17 | SERVICE MIN | 0.25 | -204.0863 | -42.3121 | 0
| 3 | SERVICE MAX | 1 | 0 | 0 | 87.1128 | 17 | SERVICE MIN | 0.5 | -197.1283 | 0 | 0
| 3 | SERVICE MIN | 0 | -144.6735 | -126.2524 | -15.8011 | 17 | SERVICE MIN | 0.75 | -190.1703 | 0 | -1.4242
| 3 | SERVICE MIN | 0.5 | -144.6735 | -130.3152 | 0 | 17 | SERVICE MIN | 1 | -183.2123 | 0 | -31.7186
| 3 | SERVICE MIN | 1 | -144.6735 | -134.3779 | 0 | 18 | SERVICE MAX | 0 | 0 | 89.2654 | 0
| 4 | SERVICE MAX | 0 | 0 | 28.9654 | 87.1128 | 18 | SERVICE MAX | 1 | 0 | 105.6971 | 0
| 4 | SERVICE MAX | 0.25 | 0 | 24.64 | 78.5092 | 18 | SERVICE MIN | 0 | -183.2123 | 0 | -31.7186
| 4 | SERVICE MAX | 0.5 | 0 | 20.3145 | 71.294 | 18 | SERVICE MIN | 1 | -179.9783 | 0 | -63.9158
| 4 | SERVICE MAX | 0.75 | 0 | 15.989 | 65.4673 | 19 | SERVICE MAX | 0 | 0 | 105.697 | 0
| 4 | SERVICE MAX | 1 | 0 | 11.6635 | 61.029 | 19 | SERVICE MAX | 1 | 0 | 118.5998 | 0
| 4 | SERVICE MIN | 0 | -144.6735 | 0 | 0 | 19 | SERVICE MIN | 0 | -179.9783 | 0 | -63.9158
| 4 | SERVICE MIN | 0.25 | -144.6735 | 0 | 0 | 19 | SERVICE MIN | 1 | -177.2833 | 0 | -94.7731
| 4 | SERVICE MIN | 0.5 | -144.6735 | 0 | 0 | 20 | SERVICE MAX | 0 | 0 | 0 | 0
| 4 | SERVICE MIN | 0.75 | -144.6735 | -1.7868 | 0 | 20 | SERVICE MAX | 1 | 0 | 0 | 0
| 4 | SERVICE MIN | 1 | -144.6735 | -6.1123 | 0 | 20 | SERVICE MIN | 0 | -118.5997 | -177.2833 | -94.7731
| 5 | SERVICE MAX | 0 | 0 | 161.0362 | 61.029 | 20 | SERVICE MIN | 1 | -118.5997 | -158.1483 | -61.2324
| 5 | SERVICE MAX | 0.5 | 0 | 156.6366 | 12.4669 | 21 | SERVICE MAX | 0 | 0 | 0 | 0
| 5 | SERVICE MAX | 1 | 0 | 152.237 | 0 | 21 | SERVICE MAX | 1 | 0 | 0 | 30.3088
| 5 | SERVICE MIN | 0 | -144.6735 | 0 | 0 | 21 | SERVICE MIN | 0 | -118.5997 | -158.1483 | -61.2324
| 5 | SERVICE MIN | 0.5 | -144.6735 | 0 | 0 | 21 | SERVICE MIN | 1 | -118.5997 | -112.2243 | -1.8237
| 5 | SERVICE MIN | 1 | -144.6735 | 0 | -41.2546 | 22 | SERVICE MAX | 0 | 0 | 0 | 30.3088
| 6 | SERVICE MAX | 0 | 0 | 152.237 | 0 | 22 | SERVICE MAX | 0.25 | 0 | 0 | 56.688
| 6 | SERVICE MAX | 1 | 0 | 145.769 | 0 | 22 | SERVICE MAX | 0.5 | 0 | 0 | 73.4227
| 6 | SERVICE MIN | 0 | -144.6735 | 0 | -41.2546 | 22 | SERVICE MAX | 0.75 | 0 | 0 | 80.5127
| 6 | SERVICE MIN | 1 | -144.6735 | 0 | -112.7761 | 22 | SERVICE MAX | 1 | 0 | 23.2349 | 77.958
| 7 | SERVICE MAX | 0 | 0 | 145.769 | 0 | 22 | SERVICE MIN | 0 | -118.5997 | -112.2243 | -1.8237
| 7 | SERVICE MAX | 1 | 0 | 143.7477 | 0 | 22 | SERVICE MIN | 0.25 | -118.5997 | -81.8475 | 0
| 7 | SERVICE MIN | 0 | -144.6735 | 0 | -112.7761 | 22 | SERVICE MIN | 0.5 | -118.5997 | -51.4707 | 0
| 7 | SERVICE MIN | 1 | -144.6735 | 0 | -134.4898 | 22 | SERVICE MIN | 0.75 | -118.5997 | -21.1522 | 0
| 8 | SERVICE MAX | 0 | 0 | 0 | 0 | 22 | SERVICE MIN | 1 | -118.5997 | 0 | 0
| 8 | SERVICE MAX | 1 | 0 | 0 | 0 | 23 | SERVICE MAX | 0 | 0 | 23.2345 | 77.958
| 8 | SERVICE MIN | 0 | -144.6735 | -143.7477 | -134.4898 | 23 | SERVICE MAX | 0.25 | 0 | 53.6113 | 65.7587
| 8 | SERVICE MIN | 1 | -144.6735 | -145.769 | -112.7761 | 23 | SERVICE MAX | 0.5 | 0 | 83.9881 | 43.9148
| 9 | SERVICE MAX | 0 | 0 | 0 | 0 | 23 | SERVICE MAX | 0.75 | 0 | 114.365 | 16.7893
| 9 | SERVICE MAX | 1 | 0 | 0 | 0 | 23 | SERVICE MAX | 1 | 0 | 144.7418 | 0
| 9 | SERVICE MIN | 0 | -144.6735 | -145.769 | -112.7761 | 23 | SERVICE MIN | 0 | -118.5997 | 0 | 0
| 9 | SERVICE MIN | 1 | -144.6735 | -152.237 | -41.2546 | 23 | SERVICE MIN | 0.25 | -118.5997 | 0 | 0
| 10 | SERVICE MAX | 0 | 0 | 0 | 0 | 23 | SERVICE MIN | 0.5 | -118.5997 | 0 | 0
| 10 | SERVICE MAX | 0.5 | 0 | 0 | 12.4669 | 23 | SERVICE MIN | 0.75 | -118.5997 | 0 | 0
| 10 | SERVICE MAX | 1 | 0 | 0 | 61.029 | 23 | SERVICE MIN | 1 | -118.5997 | 0 | -28.7069
| 10 | SERVICE MIN | 0 | -144.6735 | -152.237 | -41.2546 | 24 | SERVICE MAX | 0 | 0 | 144.7418 | 0
| 10 | SERVICE MIN | 0.5 | -144.6735 | -156.6366 | 0 | 24 | SERVICE MAX | 1 | 0 | 190.6658 | 0
| 10 | SERVICE MIN | 1 | -144.6735 | -161.0362 | 0 | 24 | SERVICE MIN | 0 | -118.5997 | 0 | -28.7069
| 11 | SERVICE MAX | 0 | 0 | 6.1121 | 61.029 | 24 | SERVICE MIN | 1 | -118.5997 | 0 | -109.2047
| 11 | SERVICE MAX | 0.25 | 0 | 1.7866 | 65.4673 | 25 | SERVICE MAX | 0 | 0 | 190.6658 | 0
| 11 | SERVICE MAX | 0.5 | 0 | 0 | 71.294 | 25 | SERVICE MAX | 1 | 0 | 205.017 | 0
| 11 | SERVICE MAX | 0.75 | 0 | 0 | 78.5092 | 25 | SERVICE MIN | 0 | -118.5997 | 0 | -109.2047
| 11 | SERVICE MAX | 1 | 0 | 0 | 87.1128 | 25 | SERVICE MIN | 1 | -118.5997 | 0 | -138.8809
| 11 | SERVICE MIN | 0 | -144.6735 | -11.6635 | 0 | 26 | SERVICE MAX | 0 | 0 | 0 | 0
| 11 | SERVICE MIN | 0.25 | -144.6735 | -15.989 | 0 | 26 | SERVICE MAX | 1 | 0 | 0 | 0
| 11 | SERVICE MIN | 0.5 | -144.6735 | -20.3145 | 0 | 26 | SERVICE MIN | 0 | -118.5997 | -205.017 | -138.8809
| 11 | SERVICE MIN | 0.75 | -144.6735 | -24.64 | 0 | 26 | SERVICE MIN | 1 | -118.5997 | -190.6658 | -109.2047
| 11 | SERVICE MIN | 1 | -144.6735 | -28.9654 | 0 | 27 | SERVICE MAX | 0 | 0 | 0 | 0
| 12 | SERVICE MAX | 0 | 0 | 134.3779 | 87.1128 | 27 | SERVICE MAX | 1 | 0 | 0 | 0
| 12 | SERVICE MAX | 0.5 | 0 | 130.3152 | 51.538 | 27 | SERVICE MIN | 0 | -118.5997 | -190.6658 | -109.2047
| 12 | SERVICE MAX | 1 | 0 | 126.2524 | 17.188 | 27 | SERVICE MIN | 1 | -118.5997 | -144.7418 | -28.7069
| 12 | SERVICE MIN | 0 | -144.6735 | 0 | 0 | 28 | SERVICE MAX | 0 | 0 | 0 | 0
| 12 | SERVICE MIN | 0.5 | -144.6735 | 0 | 0 | 28 | SERVICE MAX | 0.25 | 0 | 0 | 16.7893
| 12 | SERVICE MIN | 1 | -144.6735 | 0 | -15.8007 | 28 | SERVICE MAX | 0.5 | 0 | 0 | 43.9148
| 13 | SERVICE MAX | 0 | 0 | 126.2524 | 17.188 | 28 | SERVICE MAX | 0.75 | 0 | 0 | 65.7587
| 13 | SERVICE MAX | 1 | 0 | 119.7844 | 0 | 28 | SERVICE MAX | 1 | 0 | 0 | 77.958
| 13 | SERVICE MIN | 0 | -144.6735 | 0 | -15.8007 | 28 | SERVICE MIN | 0 | -118.5997 | -144.7418 | -28.7069
| 13 | SERVICE MIN | 1 | -144.6735 | 0 | -70.9285 | 28 | SERVICE MIN | 0.25 | -118.5997 | -114.365 | 0
| 14 | SERVICE MAX | 0 | 0 | 119.7844 | 0 | 28 | SERVICE MIN | 0.5 | -118.5997 | -83.9881 | 0
| 14 | SERVICE MAX | 1 | 0 | 117.0894 | 0 | 28 | SERVICE MIN | 0.75 | -118.5997 | -53.6113 | 0
| 14 | SERVICE MIN | 0 | -144.6735 | 0 | -70.9285 | 28 | SERVICE MIN | 1 | -118.5997 | -23.2345 | 0
| 14 | SERVICE MIN | 1 | -144.6735 | 0 | -93.7082 | 29 | SERVICE MAX | 0 | 0 | 0 | 77.958
| 15 | SERVICE MAX | 0 | 0 | 0 | 0 | 29 | SERVICE MAX | 0.25 | 0 | 21.1522 | 80.5127
| 15 | SERVICE MAX | 1 | 0 | 0 | 0 | 29 | SERVICE MAX | 0.5 | 0 | 51.4707 | 73.4227
| 15 | SERVICE MIN | 0 | -216.9733 | -144.6735 | -93.7082 | 29 | SERVICE MAX | 0.75 | 0 | 81.8475 | 56.688
| 15 | SERVICE MIN | 1 | -214.2783 | -121.9086 | -57.2426 | 29 | SERVICE MAX | 1 | 0 | 112.2243 | 30.3088
| 16 | SERVICE MAX | 0 | 0 | 0 | 0 | 29 | SERVICE MIN | 0 | -118.5997 | -23.235 | 0
| FRAME | LOAD | DIST | P | V2 | M3
| 29 | SERVICE MIN | 0.25 | -118.5997 | 0 | 0
| 29 | SERVICE MIN | 0.5 | -118.5997 | 0 | 0
| 29 | SERVICE MIN | 0.75 | -118.5997 | 0 | 0
| 29 | SERVICE MIN | 1 | -118.5997 | 0 | -1.8234
| 30 | SERVICE MAX | 0 | 0 | 112.2243 | 30.3088
| 30 | SERVICE MAX | 1 | 0 | 158.1483 | 0
| 30 | SERVICE MIN | 0 | -118.5997 | 0 | -1.8234
| 30 | SERVICE MIN | 1 | -118.5997 | 0 | -61.232
| 31 | SERVICE MAX | 0 | 0 | 158.1483 | 0
| 31 | SERVICE MAX | 1 | 0 | 177.2833 | 0
| 31 | SERVICE MIN | 0 | -118.5997 | 0 | -61.232
| 31 | SERVICE MIN | 1 | -118.5997 | 0 | -94.7727
| 32 | SERVICE MAX | 0 | 0 | 0 | 0
| 32 | SERVICE MAX | 1 | 0 | 0 | 0
| 32 | SERVICE MIN | 0 | -177.2833 | -118.5997 | -94.7727
| 32 | SERVICE MIN | 1 | -179.9783 | -105.697 | -63.9155
| 33 | SERVICE MAX | 0 | 0 | 0 | 0
| 33 | SERVICE MAX | 1 | 0 | 0 | 0
| 33 | SERVICE MIN | 0 | -179.9783 | -105.697 | -63.9155
| 33 | SERVICE MIN | 1 | -183.2123 | -89.2653 | -31.7183
| 34 | SERVICE MAX | 0 | 0 | 0 | 0
| 34 | SERVICE MAX | 0.25 | 0 | 0 | 20.5944
| 34 | SERVICE MAX | 0.5 | 0 | 0 | 40.7243
| 34 | SERVICE MAX | 0.75 | 0 | 42.3121 | 28.163
| 34 | SERVICE MAX | 1 | 0 | 95.5391 | 0
| 34 | SERVICE MIN | 0 | -183.2123 | -89.2675 | -31.7183
| 34 | SERVICE MIN | 0.25 | -190.1703 | -50.4068 | -1.4242
| 34 | SERVICE MIN | 0.5 | -197.1283 | -6.7573 | 0
| 34 | SERVICE MIN | 0.75 | -204.0863 | 0 | 0
| 34 | SERVICE MIN | 1 | -211.0443 | 0 | -21.5997
| 35 | SERVICE MAX | 0 | 0 | 95.5391 | 0
| 35 | SERVICE MAX | 1 | 0 | 121.9086 | 0
| 35 | SERVICE MIN | 0 | -211.0443 | 0 | -21.5997
| 35 | SERVICE MIN | 1 | -214.2783 | 0 | -57.2426
| 36 | SERVICE MAX | 0 | 0 | 121.9086 | 0
| 36 | SERVICE MAX | 1 | 0 | 144.6735 | 0
| 36 | SERVICE MIN | 0 | -214.2783 | 0 | -57.2426
| 36 | SERVICE MIN | 1 | -216.9733 | 0 | -93.7082
| 37 | SERVICE MAX | 0 | 0 | 0 | 0
| 37 | SERVICE MAX | 0.25 | 0 | 0 | 0
| 37 | SERVICE MAX | 0.5 | 0 | 0 | 3e-06
| 37 | SERVICE MAX | 0.75 | 0 | 0 | 8.5e-05
| 37 | SERVICE MAX | 1 | 0 | 0 | 0.000167
| 37 | SERVICE MIN | 0 | -410.034 | -8.1e-05 | -0.000161
| 37 | SERVICE MIN | 0.25 | -417.4759 | -8.1e-05 | -7.9e-05
| 37 | SERVICE MIN | 0.5 | -424.9178 | -8.1e-05 | 0
| 37 | SERVICE MIN | 0.75 | -432.3597 | -8.1e-05 | 0
| 37 | SERVICE MIN | 1 | -439.8015 | -8.1e-05 | 0

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 15.4552 | 0 | 39.0075 | 15 | ULTIMATE MIN | 0 | -100.9113 | 0 | 0
| 1 | ULTIMATE MAX | 1 | 15.5386 | 0 | 41.8186 | 15 | ULTIMATE MIN | 1 | -97.9083 | 0 | 0
| 1 | ULTIMATE MIN | 0 | 0 | -18.1045 | 0 | 16 | ULTIMATE MAX | 0 | 0 | 20.881 | 33.1869
| 1 | ULTIMATE MIN | 1 | 0 | -20.7995 | 0 | 16 | ULTIMATE MAX | 1 | 0 | 19.9223 | 26.444
| 2 | ULTIMATE MAX | 0 | 15.5386 | 0 | 41.8186 | 16 | ULTIMATE MIN | 0 | -97.9083 | 0 | 0
| 2 | ULTIMATE MAX | 1 | 15.7386 | 0 | 50.7643 | 16 | ULTIMATE MIN | 1 | -94.3047 | 0 | 0
| 2 | ULTIMATE MIN | 0 | 0 | -20.7992 | 0 | 17 | ULTIMATE MAX | 0 | 0 | 19.9223 | 26.444
| 2 | ULTIMATE MIN | 1 | 0 | -27.2672 | 0 | 17 | ULTIMATE MAX | 1 | 0 | 18.242 | 18.6407
| 3 | ULTIMATE MAX | 0 | 15.7386 | 0 | 50.7643 | 17 | ULTIMATE MIN | 0 | -94.3047 | 0 | 0
| 3 | ULTIMATE MAX | 0.5 | 15.8643 | 0 | 57.9709 | 17 | ULTIMATE MIN | 1 | -89.8493 | 0 | 0
| 3 | ULTIMATE MAX | 1 | 15.99 | 0 | 66.4024 | 18 | ULTIMATE MAX | 0 | 0 | 27.508 | 18.6407
| 3 | ULTIMATE MIN | 0 | 0 | -27.2672 | 0 | 18 | ULTIMATE MAX | 0.25 | 0 | 26.2096 | 11.8414
| 3 | ULTIMATE MIN | 0.5 | 0 | -31.3299 | 0 | 18 | ULTIMATE MAX | 0.5 | 0 | 24.7229 | 5.3945
| 3 | ULTIMATE MIN | 1 | 0 | -35.3927 | 0 | 18 | ULTIMATE MAX | 0.75 | 0 | 23.0478 | 0
| 4 | ULTIMATE MAX | 0 | 16.0107 | 62.4303 | 66.4024 | 18 | ULTIMATE MAX | 1 | 0 | 23.3151 | 0
| 4 | ULTIMATE MAX | 0.25 | 15.877 | 58.1048 | 47.0565 | 18 | ULTIMATE MIN | 0 | -124.4371 | 0 | 0
| 4 | ULTIMATE MAX | 0.5 | 15.7432 | 53.7794 | 29.099 | 18 | ULTIMATE MIN | 0.25 | -121.6743 | 0 | 0
| 4 | ULTIMATE MAX | 0.75 | 15.6094 | 49.4539 | 12.5301 | 18 | ULTIMATE MIN | 0.5 | -118.9115 | 0 | 0
| 4 | ULTIMATE MAX | 1 | 15.4756 | 45.1284 | 0 | 18 | ULTIMATE MIN | 0.75 | -116.1488 | 0 | -3.9648
| 4 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 18 | ULTIMATE MIN | 1 | -113.386 | 0 | -9.6239
| 4 | ULTIMATE MIN | 0.25 | 0 | 0 | 0 | 19 | ULTIMATE MAX | 0 | 0 | 39.2621 | 0
| 4 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 19 | ULTIMATE MAX | 0.25 | 0 | 37.2232 | 0
| 4 | ULTIMATE MIN | 0.75 | 0 | 0 | 0 | 19 | ULTIMATE MAX | 0.5 | 0 | 35.0218 | 0
| 4 | ULTIMATE MIN | 1 | 0 | 0 | -2.6503 | 19 | ULTIMATE MAX | 0.75 | 0 | 32.6579 | 0
| 5 | ULTIMATE MAX | 0 | 17.1314 | 152.6514 | 0 | 19 | ULTIMATE MAX | 1 | 0 | 32.4455 | 0
| 5 | ULTIMATE MAX | 0.5 | 16.9953 | 148.2518 | 0 | 19 | ULTIMATE MIN | 0 | -148.1446 | 0 | -9.6239
| 5 | ULTIMATE MAX | 1 | 16.8592 | 143.8522 | 0 | 19 | ULTIMATE MIN | 0.25 | -145.8832 | 0 | -15.9306
| 5 | ULTIMATE MIN | 0 | 0 | 0 | -2.6503 | 19 | ULTIMATE MIN | 0.5 | -143.6871 | 0 | -25.0731
| 5 | ULTIMATE MIN | 0.5 | 0 | 0 | -51.7728 | 19 | ULTIMATE MIN | 0.75 | -141.4911 | 0 | -33.638
| 5 | ULTIMATE MIN | 1 | 0 | 0 | -99.4588 | 19 | ULTIMATE MIN | 1 | -139.2951 | 0 | -41.5842
| 6 | ULTIMATE MAX | 0 | 16.8592 | 143.8522 | 0 | 20 | ULTIMATE MAX | 0 | 0 | 54.3181 | 0
| 6 | ULTIMATE MAX | 1 | 16.6592 | 137.3842 | 0 | 20 | ULTIMATE MAX | 1 | 0 | 49.9254 | 0
| 6 | ULTIMATE MIN | 0 | 0 | 0 | -99.4588 | 20 | ULTIMATE MIN | 0 | -174.4358 | 0 | -41.5842
| 6 | ULTIMATE MIN | 1 | 0 | 0 | -166.9555 | 20 | ULTIMATE MIN | 1 | -170.8943 | 0 | -62.8627
| 7 | ULTIMATE MAX | 0 | 16.6592 | 137.3842 | 0 | 21 | ULTIMATE MAX | 0 | 0 | 49.9254 | 0
| 7 | ULTIMATE MAX | 1 | 16.5967 | 135.363 | 0 | 21 | ULTIMATE MAX | 1 | 0 | 46.1071 | 0
| 7 | ULTIMATE MIN | 0 | 0 | 0 | -166.9555 | 21 | ULTIMATE MIN | 0 | -170.8943 | 0 | -62.8627
| 7 | ULTIMATE MIN | 1 | 0 | 0 | -187.4115 | 21 | ULTIMATE MIN | 1 | -168.0299 | 0 | -78.7143
| 8 | ULTIMATE MAX | 0 | 16.5976 | 0 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 46.1071 | 0
| 8 | ULTIMATE MAX | 1 | 16.6601 | 0 | 0 | 22 | ULTIMATE MAX | 1 | 0 | 44.0026 | 0
| 8 | ULTIMATE MIN | 0 | 0 | -135.3627 | -187.4117 | 22 | ULTIMATE MIN | 0 | -168.0299 | 0 | -78.7143
| 8 | ULTIMATE MIN | 1 | 0 | -137.384 | -166.9557 | 22 | ULTIMATE MIN | 1 | -165.6429 | 0 | -90.9368
| 9 | ULTIMATE MAX | 0 | 16.6601 | 0 | 0 | 23 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 9 | ULTIMATE MAX | 1 | 16.8602 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 9 | ULTIMATE MIN | 0 | 0 | -137.384 | -166.9557 | 23 | ULTIMATE MIN | 0 | -57.8099 | -192.9506 | -90.9368
| 9 | ULTIMATE MIN | 1 | 0 | -143.852 | -99.4591 | 23 | ULTIMATE MIN | 1 | -56.7746 | -173.8156 | -54.2602
| 10 | ULTIMATE MAX | 0 | 16.8602 | 0 | 0 | 24 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 10 | ULTIMATE MAX | 0.5 | 16.9963 | 0 | 0 | 24 | ULTIMATE MAX | 1 | 0 | 0 | 29.6722
| 10 | ULTIMATE MAX | 1 | 17.1323 | 0 | 0 | 24 | ULTIMATE MIN | 0 | -56.7746 | -173.8156 | -54.2602
| 10 | ULTIMATE MIN | 0 | 0 | -143.852 | -99.4591 | 24 | ULTIMATE MIN | 1 | -54.2899 | -127.8916 | 0
| 10 | ULTIMATE MIN | 0.5 | 0 | -148.2516 | -51.7732 | 25 | ULTIMATE MAX | 0 | 0 | 0 | 29.6722
| 10 | ULTIMATE MIN | 1 | 0 | -152.6512 | -2.6508 | 25 | ULTIMATE MAX | 0.5 | 0 | 0 | 62.4392
| 11 | ULTIMATE MAX | 0 | 15.4763 | 0 | 0 | 25 | ULTIMATE MAX | 1 | 0 | 0 | 86.5091
| 11 | ULTIMATE MAX | 0.25 | 15.6101 | 0 | 12.5295 | 25 | ULTIMATE MIN | 0 | -54.2899 | -127.8916 | 0
| 11 | ULTIMATE MAX | 0.5 | 15.7439 | 0 | 29.0983 | 25 | ULTIMATE MIN | 0.5 | -52.7292 | -99.0456 | 0
| 11 | ULTIMATE MAX | 0.75 | 15.8776 | 0 | 47.0555 | 25 | ULTIMATE MIN | 1 | -51.1685 | -70.1995 | 0
| 11 | ULTIMATE MAX | 1 | 16.0114 | 0 | 66.4013 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 86.5091
| 11 | ULTIMATE MIN | 0 | 0 | -45.1279 | -2.6508 | 26 | ULTIMATE MAX | 0.25 | 0 | 0 | 102.5765
| 11 | ULTIMATE MIN | 0.25 | 0 | -49.4534 | 0 | 26 | ULTIMATE MAX | 0.5 | 0 | 0 | 108.7854
| 11 | ULTIMATE MIN | 0.5 | 0 | -53.7789 | 0 | 26 | ULTIMATE MAX | 0.75 | 0 | 26.7279 | 105.1358
| 11 | ULTIMATE MIN | 0.75 | 0 | -58.1043 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 57.4396 | 91.6278
| 11 | ULTIMATE MIN | 1 | 0 | -62.4298 | 0 | 26 | ULTIMATE MIN | 0 | -55.5937 | -70.1984 | 0
| 12 | ULTIMATE MAX | 0 | 15.9877 | 35.3923 | 66.4013 | 26 | ULTIMATE MIN | 0.25 | -53.9321 | -39.4867 | 0
| 12 | ULTIMATE MAX | 0.5 | 15.862 | 31.3296 | 57.9695 | 26 | ULTIMATE MIN | 0.5 | -52.2704 | -8.775 | 0
| 12 | ULTIMATE MAX | 1 | 15.7364 | 27.2668 | 50.7627 | 26 | ULTIMATE MIN | 0.75 | -50.6088 | 0 | 0
| 12 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 26 | ULTIMATE MIN | 1 | -49.5736 | 0 | 0
| 12 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 57.4382 | 91.6278
| 12 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 27 | ULTIMATE MAX | 0.5 | 0 | 88.6761 | 67.7746
| 13 | ULTIMATE MAX | 0 | 15.7364 | 27.2668 | 50.7627 | 27 | ULTIMATE MAX | 1 | 0 | 119.914 | 34.3625
| 13 | ULTIMATE MAX | 1 | 15.5363 | 20.7988 | 41.8165 | 27 | ULTIMATE MIN | 0 | -53.4299 | 0 | 0
| 13 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 27 | ULTIMATE MIN | 0.5 | -51.7398 | 0 | 0
| 13 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 27 | ULTIMATE MIN | 1 | -50.0496 | 0 | 0
| 14 | ULTIMATE MAX | 0 | 15.5363 | 20.7991 | 41.8165 | 28 | ULTIMATE MAX | 0 | 0 | 119.914 | 34.3625
| 14 | ULTIMATE MAX | 1 | 15.453 | 18.1041 | 39.0053 | 28 | ULTIMATE MAX | 1 | 0 | 165.838 | 0
| 14 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 0 | -50.0496 | 0 | 0
| 14 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 1 | -50.8483 | 0 | -34.8596
| 15 | ULTIMATE MAX | 0 | 0 | 21.3905 | 39.0053 | 29 | ULTIMATE MAX | 0 | 0 | 165.838 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 20.881 | 33.1869 | 29 | ULTIMATE MAX | 1 | 0 | 180.1893 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 29 | ULTIMATE MIN | 0 | -50.8483 | 0 | -34.8596 | 45 | ULTIMATE MAX | 0.25 | 0 | 1.3995 | 2.7968
| 29 | ULTIMATE MIN | 1 | -51.6247 | 0 | -60.8103 | 45 | ULTIMATE MAX | 0.5 | 0 | 2.4867 | 0.82784
| 30 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 45 | ULTIMATE MAX | 0.75 | 0 | 3.5559 | 2.2333
| 30 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 45 | ULTIMATE MAX | 1 | 0 | 4.6069 | 6.3679
| 30 | ULTIMATE MIN | 0 | -51.6211 | -180.1898 | -60.8103 | 45 | ULTIMATE MIN | 0 | -355.5927 | -0.29482 | -3.657
| 30 | ULTIMATE MIN | 1 | -50.8446 | -165.8386 | -34.8595 | 45 | ULTIMATE MIN | 0.25 | -363.0346 | -1.4001 | -2.7975
| 31 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 45 | ULTIMATE MIN | 0.5 | -370.4765 | -2.4873 | -0.8279
| 31 | ULTIMATE MAX | 1 | 0 | 0 | 34.3621 | 45 | ULTIMATE MIN | 0.75 | -377.9183 | -3.5565 | -2.2328
| 31 | ULTIMATE MIN | 0 | -50.8446 | -165.8386 | -34.8595 | 45 | ULTIMATE MIN | 1 | -385.3602 | -4.6075 | -6.3667
| 31 | ULTIMATE MIN | 1 | -50.0545 | -119.9146 | 0
| 32 | ULTIMATE MAX | 0 | 0 | 0 | 34.3621
| 32 | ULTIMATE MAX | 0.5 | 0 | 0 | 67.7752
| 32 | ULTIMATE MAX | 1 | 0 | 0 | 91.6285
| 32 | ULTIMATE MIN | 0 | -50.0545 | -119.9146 | 0
| 32 | ULTIMATE MIN | 0.5 | -51.7447 | -88.6767 | 0
| 32 | ULTIMATE MIN | 1 | -53.4348 | -57.4388 | 0
| 33 | ULTIMATE MAX | 0 | 0 | 0 | 91.6285
| 33 | ULTIMATE MAX | 0.25 | 0 | 0 | 105.1367
| 33 | ULTIMATE MAX | 0.5 | 0 | 8.7736 | 108.7865
| 33 | ULTIMATE MAX | 0.75 | 0 | 39.4853 | 102.5778
| 33 | ULTIMATE MAX | 1 | 0 | 70.197 | 86.5106
| 33 | ULTIMATE MIN | 0 | -49.5705 | -57.4401 | 0
| 33 | ULTIMATE MIN | 0.25 | -50.6143 | -26.7284 | 0
| 33 | ULTIMATE MIN | 0.5 | -52.276 | 0 | 0
| 33 | ULTIMATE MIN | 0.75 | -53.9376 | 0 | 0
| 33 | ULTIMATE MIN | 1 | -55.5992 | 0 | 0
| 34 | ULTIMATE MAX | 0 | 0 | 70.1981 | 86.5106
| 34 | ULTIMATE MAX | 0.5 | 0 | 99.0442 | 62.4409
| 34 | ULTIMATE MAX | 1 | 0 | 127.8902 | 29.674
| 34 | ULTIMATE MIN | 0 | -51.1747 | 0 | 0
| 34 | ULTIMATE MIN | 0.5 | -52.7354 | 0 | 0
| 34 | ULTIMATE MIN | 1 | -54.2961 | 0 | 0
| 35 | ULTIMATE MAX | 0 | 0 | 127.8902 | 29.674
| 35 | ULTIMATE MAX | 1 | 0 | 173.8142 | 0
| 35 | ULTIMATE MIN | 0 | -54.2961 | 0 | 0
| 35 | ULTIMATE MIN | 1 | -56.7808 | 0 | -54.2564
| 36 | ULTIMATE MAX | 0 | 0 | 173.8142 | 0
| 36 | ULTIMATE MAX | 1 | 0 | 192.9492 | 0
| 36 | ULTIMATE MIN | 0 | -56.7808 | 0 | -54.2564
| 36 | ULTIMATE MIN | 1 | -57.816 | 0 | -90.9328
| 37 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 37 | ULTIMATE MIN | 0 | -165.6417 | -44.0006 | -90.9328
| 37 | ULTIMATE MIN | 1 | -168.0287 | -46.1155 | -78.7079
| 38 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 38 | ULTIMATE MIN | 0 | -168.0287 | -46.1155 | -78.7079
| 38 | ULTIMATE MIN | 1 | -170.8931 | -49.9337 | -62.8536
| 39 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 39 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 39 | ULTIMATE MIN | 0 | -170.8931 | -49.9337 | -62.8536
| 39 | ULTIMATE MIN | 1 | -174.4258 | -54.3156 | -41.6261
| 40 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 0.25 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 0.75 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 40 | ULTIMATE MIN | 0 | -139.285 | -32.4542 | -41.6261
| 40 | ULTIMATE MIN | 0.25 | -141.4832 | -32.6572 | -33.6725
| 40 | ULTIMATE MIN | 0.5 | -143.6815 | -35.0235 | -25.099
| 40 | ULTIMATE MIN | 0.75 | -145.8797 | -37.2271 | -15.9468
| 40 | ULTIMATE MIN | 1 | -148.1442 | -39.268 | -9.6244
| 41 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 41 | ULTIMATE MAX | 0.25 | 0 | 0 | 0
| 41 | ULTIMATE MAX | 0.5 | 0 | 0 | 5.3914
| 41 | ULTIMATE MAX | 0.75 | 0 | 0 | 11.8394
| 41 | ULTIMATE MAX | 1 | 0 | 0 | 18.6397
| 41 | ULTIMATE MIN | 0 | -113.3858 | -23.3148 | -9.6244
| 41 | ULTIMATE MIN | 0.25 | -116.1486 | -23.0522 | -3.9655
| 41 | ULTIMATE MIN | 0.5 | -118.9113 | -24.7273 | 0
| 41 | ULTIMATE MIN | 0.75 | -121.6741 | -26.214 | 0
| 41 | ULTIMATE MIN | 1 | -124.4368 | -27.5124 | 0
| 42 | ULTIMATE MAX | 0 | 0 | 0 | 18.6397
| 42 | ULTIMATE MAX | 1 | 0 | 0 | 26.4443
| 42 | ULTIMATE MIN | 0 | -89.8493 | -18.2451 | 0
| 42 | ULTIMATE MIN | 1 | -94.3047 | -19.9254 | 0
| 43 | ULTIMATE MAX | 0 | 0 | 0 | 26.4443
| 43 | ULTIMATE MAX | 1 | 0 | 0 | 33.1882
| 43 | ULTIMATE MIN | 0 | -94.3047 | -19.9254 | 0
| 43 | ULTIMATE MIN | 1 | -97.9083 | -20.8841 | 0
| 44 | ULTIMATE MAX | 0 | 0 | 0 | 33.1882
| 44 | ULTIMATE MAX | 1 | 0 | 0 | 39.0075
| 44 | ULTIMATE MIN | 0 | -97.9083 | -20.8841 | 0
| 44 | ULTIMATE MIN | 1 | -100.9113 | -21.3936 | 0
| 45 | ULTIMATE MAX | 0 | 0 | 0.2942 | 3.6557

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 153.394 | 176.957 | 191.571 | 94.773 | 1000 | 650
|  | 제 1경간 중앙부 | 124.013 | - | 191.571 | 80.513 | 1000 | 550
|  | 제 1경간 지점부 | 208.151 | 220.498 | 191.571 | 138.881 | 1000 | 650
|  | 제 2경간 중앙부 | 124.013 | - | 191.571 | 80.513 | 1000 | 550
|  | 단지점부(우측) | 153.395 | 176.957 | 191.571 | 94.773 | 1000 | 650
| 하부슬래브 | 단지점부(좌측) | 145.169 | 189.825 | 228.861 | 93.708 | 1000 | 550
|  | 제 1경간 중앙부 | 128.785 | - | 228.861 | 87.113 | 1000 | 550
|  | 제 1경간 지점부 | 206.465 | 229.702 | 228.861 | 134.49 | 1000 | 550
|  | 제 2경간 중앙부 | 128.785 | - | 228.861 | 87.113 | 1000 | 550
|  | 단지점부(우측) | 145.169 | 189.825 | 228.861 | 93.708 | 1000 | 550
| 좌측벽체 | 상부 | 153.394 | 144.639 | 277.386 | 94.773 | 1000 | 500
|  | 중앙부 | 67.788 | - | 301.2 | 40.724 | 1000 | 400
|  | 중앙부(부모멘트) | -51.533 | - | 301.2 | -31.718 | 1000 | 400 | 부모멘트
|  | 하부 | 145.169 | 150.246 | 325.014 | 93.708 | 1000 | 400
| 우측벽체 | 상부 | 153.395 | 144.639 | 277.386 | 94.773 | 1000 | 500
|  | 중앙부 | 67.788 | - | 301.2 | 40.724 | 1000 | 400
|  | 중앙부(부모멘트) | -51.534 | - | 301.2 | -31.719 | 1000 | 400 | 부모멘트
|  | 하부 | 145.169 | 150.246 | 325.014 | 93.708 | 1000 | 400

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 90.933 | 127.89 | 57.816 | 1000 | 650
|  | 제 1경간 중앙부 | 108.786 | - | 52.276 | 1000 | 550
|  | 제 1경간 지점부 | 60.81 | 119.915 | 51.625 | 1000 | 650
|  | 제 2경간 중앙부 | 108.785 | - | 52.27 | 1000 | 550
|  | 단지점부(우측) | 90.937 | 127.892 | 57.81 | 1000 | 650
| 하부슬래브 | 단지점부(좌측) | 0 | 27.267 | 15.455 | 1000 | 550
|  | 제 1경간 중앙부 | 66.402 | - | 15.99 | 1000 | 550
|  | 제 1경간 지점부 | 187.412 | 143.852 | 16.598 | 1000 | 550
|  | 제 2경간 중앙부 | 66.401 | - | 16.011 | 1000 | 550
|  | 단지점부(우측) | 0 | 27.267 | 15.453 | 1000 | 550
| 좌측벽체 | 상부 | 90.933 | 49.934 | 165.642 | 1000 | 500
|  | 중앙부 | 26.444 | - | 94.305 | 1000 | 400
|  | 중앙부(부모멘트) | -62.854 | - | 94.305 | 1000 | 400 | 부모멘트
|  | 하부 | 0 | 19.925 | 100.911 | 1000 | 400
| 우측벽체 | 상부 | 90.937 | 49.925 | 165.643 | 1000 | 500
|  | 중앙부 | 26.444 | - | 94.305 | 1000 | 400
|  | 중앙부(부모멘트) | -62.863 | - | 94.305 | 1000 | 400 | 부모멘트
|  | 하부 | 0 | 19.922 | 100.911 | 1000 | 400

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 580 | 153.394 | 250.953 |  | 788.368 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.636
상부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 500 | 124.013 | 215.56 |  | 740.23 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.738
상부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 580 | 208.151 | 370.096 |  | 1075.067 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.778
상부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 500 | 124.013 | 215.56 |  | 740.23 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.738
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 580 | 153.395 | 250.953 |  | 788.371 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.636
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 480 | 145.169 | 250.878 |  | 906.294 | H16 - 8.0EA |  |  | 1588.8 | 1.728
하부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 500 | 128.785 | 215.56 |  | 769.159 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.674
하부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 480 | 206.465 | 356.544 |  | 1299.604 | H19 - 8.0EA |  |  | 2292 | 1.727
하부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 500 | 128.785 | 215.56 |  | 769.159 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.674
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 480 | 145.169 | 250.878 |  | 906.294 | H16 - 8.0EA |  |  | 1588.8 | 1.728
좌측벽체 : 상부 |  |  |  | 1000 |  | 430 | 153.394 | 276.034 |  | - | H16 - 4.0EA + H13 - 4.0EA |  |  | - | 1.8
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 350 | 67.788 | 257.123 |  | - | H16 - 4.0EA |  |  | - | 3.793
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 330 | 62.854 | 276.173 |  | - | H16 - 4.0EA |  |  | - | 4.394
좌측벽체 : 하부 |  |  |  | 1000 |  | 330 | 145.169 | 242.052 |  | - | H16 - 8.0EA |  |  | - | 1.667
우측벽체 : 상부 |  |  |  | 1000 |  | 430 | 153.395 | 276.03 |  | - | H16 - 4.0EA + H13 - 4.0EA |  |  | - | 1.799
우측벽체 : 중앙부 |  |  |  | 1000 |  | 350 | 67.788 | 257.122 |  | - | H16 - 4.0EA |  |  | - | 3.793
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 330 | 62.863 | 276.084 |  | - | H16 - 4.0EA |  |  | - | 4.392
우측벽체 : 하부 |  |  |  | 1000 |  | 330 | 145.169 | 242.052 |  | - | H16 - 8.0EA |  |  | - | 1.667
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 293.939 |  | 176.957 | 293.939 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 1경간 중앙부 |  |  |  | 306.186 |  | - | 306.186 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 지점부 |  |  |  | 293.939 |  | 220.498 | 293.939 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 중앙부 |  |  |  | 306.186 |  | - | 306.186 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 293.939 |  | 176.957 | 293.939 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 293.939 |  | 189.825 | 293.939 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 1경간 중앙부 |  |  |  | 306.186 |  | - | 306.186 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 지점부 |  |  |  | 293.939 |  | 229.702 | 293.939 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 중앙부 |  |  |  | 306.186 |  | - | 306.186 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 293.939 |  | 189.825 | 293.939 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 212.093 |  | 144.639 | 212.093 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 225.858 |  | - | 225.858 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 213.811 |  | 150.246 | 213.811 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 212.093 |  | 144.639 | 212.093 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 225.858 |  | - | 225.858 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 213.811 |  | 150.246 | 213.811 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 650 |  | 580 |  | 70 |  | 153.394 |  | 176.957
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (580.00 - 30.016) / 30.016 = 0.0550
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 788.368 mm²
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00224
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (580.00 - a/2) = 250.953 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 153.394 kN.m) ∴ O.K [안전률 1.636]
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 480.00 = 293.939 kN
≥ Vu (= 176.957 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 500 |  | 50 |  | 124.013 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (500.00 - 30.016) / 30.016 = 0.0470
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 740.230 mm²
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (500.00 - a/2) = 215.560 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 124.013 kN.m) ∴ O.K [안전률 1.738]
＊ 전단에 대한 검토 (d = 500.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 500.00 = 306.186 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 650 |  | 580 |  | 70 |  | 208.151 |  | 220.498
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (580.00 - 44.761) / 44.761 = 0.0359
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1075.067 mm²
Use As = 1940.400 mm² (철근도심 : 70.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00335
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (580.00 - a/2) = 370.096 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 208.151 kN.m) ∴ O.K [안전률 1.778]
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 480.00 = 293.939 kN
≥ Vu (= 220.498 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 500 |  | 50 |  | 124.013 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (500.00 - 30.016) / 30.016 = 0.0470
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 740.230 mm²
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (500.00 - a/2) = 215.560 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 124.013 kN.m) ∴ O.K [안전률 1.738]
＊ 전단에 대한 검토 (d = 500.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 500.00 = 306.186 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 650 |  | 580 |  | 70 |  | 153.395 |  | 176.957
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (580.00 - 30.016) / 30.016 = 0.0550
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 788.371 mm²
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00224
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (580.00 - a/2) = 250.953 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 153.395 kN.m) ∴ O.K [안전률 1.636]
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 480.00 = 293.939 kN
≥ Vu (= 176.957 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 480 |  | 70 |  | 145.169 |  | 189.825
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (480.00 - 36.651) / 36.651 = 0.0363
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 906.294 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00331
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (480.00 - a/2) = 250.878 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 145.169 kN.m) ∴ O.K [안전률 1.728]
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 480.00 = 293.939 kN
≥ Vu (= 189.825 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 500 |  | 50 |  | 128.785 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (500.00 - 30.016) / 30.016 = 0.0470
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 769.159 mm²
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (500.00 - a/2) = 215.560 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 128.785 kN.m) ∴ O.K [안전률 1.674]
＊ 전단에 대한 검토 (d = 500.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 500.00 = 306.186 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 480 |  | 70 |  | 206.465 |  | 229.702
＊ 강도감소계수(Φ) 산정
T = As x fy = 2292.000 x 400.00 = 916800.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 44.941 mm, c = 44.941 / β1 = 44.941 / 0.85 = 52.872 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (480.00 - 52.872) / 52.872 = 0.0242
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1299.604 mm²
Use As = 2292.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 8.0 EA (= 2292.000 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00478
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 2292.000 x 400 x (480.00 - a/2) = 356.544 kN.m
; a = As x fy / (0.85 x fck x b) = 44.941 mm
≥ Mu (= 206.465 kN.m) ∴ O.K [안전률 1.727]
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 480.00 = 293.939 kN
≥ Vu (= 229.702 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 500 |  | 50 |  | 128.785 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (500.00 - 30.016) / 30.016 = 0.0470
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 769.159 mm²
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (500.00 - a/2) = 215.560 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 128.785 kN.m) ∴ O.K [안전률 1.674]
＊ 전단에 대한 검토 (d = 500.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 500.00 = 306.186 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 550 |  | 480 |  | 70 |  | 145.169 |  | 189.825
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (480.00 - 36.651) / 36.651 = 0.0363
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 906.294 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00331
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (480.00 - a/2) = 250.878 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 145.169 kN.m) ∴ O.K [안전률 1.728]
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 480.00 = 293.939 kN
≥ Vu (= 189.825 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 500 |  | 430 |  | 277.386 |  | 153.394 |  | 144.639 |  | 553
＊ 철근비 검토
As = 1301.200 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA + H13- 4.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0042) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 500.0 x 1000.0 = 10200000.0 N
Cs = As x fy = 520480.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (10200000.0 x 250.00 + 520480.0 x 70.000 + 317760.0 x 450.000) / 11038240.0
= 247.270 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 258.000 mm, ab = k1 x cb = 219.300 mm
fs' = 600 x (258.000 - 50.000) / 258.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 219.300 x 1000.000 = 4473.720 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 520.480 kN
Pb = 4473.720 + 301.554 - 520.480 = 4254.794 kN
Mb = 4473.720 x (430.000 - 219.300/2) + 301.554 x (430.000 - 50.00)
- 4254.794 x (247.270 - 70.000)
= 793.499 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 186.495 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 62.280 mm, a = k1 x c = 52.938 mm 를 사용.
fs = 600 x (430.000 - 62.280) / 62.280 (≤fy) = 400.000 MPa
fs' = 600 x ( 62.280 - 50.000) / 62.280 (≤fy) = 118.302 MPa
Cc = 0.85 x 24.0 x 52.938 x 1000.000 = 1079.929 kN
Cs = As' x (fs' - 0.85 x fck) = 77.773 kN
Ts = As x fs = 520.480 kN
Pn = 1079.929 + 77.773 - 520.480 = 637.223 kN
Mn' = 1079.929 x (430.000 - 52.938/2) + 77.773 x (430.000 - 50.00)
= 465.339 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0085 ＜ 0.0100 (e' = e + Xp - dc = 730.270 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 70.00 = 330.000 mm
c = 600.00 / (600.00+400.00) x 330.000 = 198.000 mm, a = k1 x c = 168.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (330.00-198.00) / 198.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 8796.392 kN ≥ Pn = 637.223 kN
ΦPn = 0.78 x 637.223 = 499.158 kN ≥ Pu = 277.386 kN ∴ O.K
ΦMn = ΦPn x 0.553 = 276.034 kN.m ≥ Mu = 153.394 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 330.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 330.00 = 212.093 kN
≥ Vu (= 144.639 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 400 |  | 350 |  | 301.2 |  | 67.788 |  | 0 |  | 225.06
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0040) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (8160000.0 x 200.00 + 317760.0 x 50.000 + 317760.0 x 330.000) / 8795520.0
= 199.277 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 210.000 mm, ab = k1 x cb = 178.500 mm
fs' = 600 x (210.000 - 70.000) / 210.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 178.500 x 1000.000 = 3641.400 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 3641.400 + 301.554 - 317.760 = 3625.194 kN
Mb = 3641.400 x (350.000 - 178.500/2) + 301.554 x (350.000 - 70.00)
- 3625.194 x (199.277 - 50.000)
= 492.770 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 135.929 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 95.938 mm, a = k1 x c = 81.547 mm 를 사용.
fs = 600 x (350.000 - 95.938) / 95.938 (≤fy) = 400.000 MPa
fs' = 600 x ( 95.938 - 70.000) / 95.938 (≤fy) = 162.218 MPa
Cc = 0.85 x 24.0 x 81.547 x 1000.000 = 1663.567 kN
Cs = As' x (fs' - 0.85 x fck) = 112.660 kN
Ts = As x fs = 317.760 kN
Pn = 1663.567 + 112.660 - 317.760 = 1458.467 kN
Mn' = 1663.567 x (350.000 - 81.547/2) + 112.660 x (350.000 - 70.00)
= 545.963 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0037 ＜ 0.0100 (e' = e + Xp - dc = 374.337 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 50.00 = 350.000 mm
c = 600.00 / (600.00+400.00) x 350.000 = 210.000 mm, a = k1 x c = 178.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (350.00-210.00) / 210.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7010.487 kN ≥ Pn = 1458.467 kN
ΦPn = 0.78 x 1458.467 = 1142.466 kN ≥ Pu = 301.200 kN ∴ O.K
ΦMn = ΦPn x 0.225 = 257.123 kN.m ≥ Mu = 67.788 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 350.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 350.00 = 225.858 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 400 |  | 330 |  | 301.2 |  | 62.854 |  | 0 |  | 208.677
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0040) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (8160000.0 x 200.00 + 317760.0 x 70.000 + 317760.0 x 350.000) / 8795520.0
= 200.723 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 198.000 mm, ab = k1 x cb = 168.300 mm
fs' = 600 x (198.000 - 50.000) / 198.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 168.300 x 1000.000 = 3433.320 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 3433.320 + 301.554 - 317.760 = 3417.114 kN
Mb = 3433.320 x (330.000 - 168.300/2) + 301.554 x (330.000 - 50.00)
- 3417.114 x (200.723 - 70.000)
= 481.823 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 141.003 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 102.601 mm, a = k1 x c = 87.211 mm 를 사용.
fs = 600 x (330.000 - 102.601) / 102.601 (≤fy) = 400.000 MPa
fs' = 600 x (102.601 - 50.000) / 102.601 (≤fy) = 307.606 MPa
Cc = 0.85 x 24.0 x 87.211 x 1000.000 = 1779.107 kN
Cs = As' x (fs' - 0.85 x fck) = 228.157 kN
Ts = As x fs = 317.760 kN
Pn = 1779.107 + 228.157 - 317.760 = 1689.503 kN
Mn' = 1779.107 x (330.000 - 87.211/2) + 228.157 x (330.000 - 50.00)
= 573.410 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0041 ＜ 0.0100 (e' = e + Xp - dc = 339.400 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 70.00 = 330.000 mm
c = 600.00 / (600.00+400.00) x 330.000 = 198.000 mm, a = k1 x c = 168.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (330.00-198.00) / 198.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7010.487 kN ≥ Pn = 1689.503 kN
ΦPn = 0.78 x 1689.503 = 1323.444 kN ≥ Pu = 301.200 kN ∴ O.K
ΦMn = ΦPn x 0.209 = 276.173 kN.m ≥ Mu = 62.854 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 330.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 330.00 = 212.952 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 400 |  | 330 |  | 325.014 |  | 145.169 |  | 150.246 |  | 446.655
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0060) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (8160000.0 x 200.00 + 635520.0 x 70.000 + 317760.0 x 350.000) / 9113280.0
= 196.165 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 198.000 mm, ab = k1 x cb = 168.300 mm
fs' = 600 x (198.000 - 50.000) / 198.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 168.300 x 1000.000 = 3433.320 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 635.520 kN
Pb = 3433.320 + 301.554 - 635.520 = 3099.354 kN
Mb = 3433.320 x (330.000 - 168.300/2) + 301.554 x (330.000 - 50.00)
- 3099.354 x (196.165 - 70.000)
= 537.488 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 173.419 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 69.710 mm, a = k1 x c = 59.254 mm 를 사용.
fs = 600 x (330.000 - 69.710) / 69.710 (≤fy) = 400.000 MPa
fs' = 600 x ( 69.710 - 50.000) / 69.710 (≤fy) = 169.646 MPa
Cc = 0.85 x 24.0 x 59.254 x 1000.000 = 1208.773 kN
Cs = As' x (fs' - 0.85 x fck) = 118.561 kN
Ts = As x fs = 635.520 kN
Pn = 1208.773 + 118.561 - 635.520 = 691.814 kN
Mn' = 1208.773 x (330.000 - 59.254/2) + 118.561 x (330.000 - 50.00)
= 396.280 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0068 ＜ 0.0100 (e' = e + Xp - dc = 572.820 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 70.00 = 330.000 mm
c = 600.00 / (600.00+400.00) x 330.000 = 198.000 mm, a = k1 x c = 168.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (330.00-198.00) / 198.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7251.730 kN ≥ Pn = 691.814 kN
ΦPn = 0.78 x 691.814 = 541.921 kN ≥ Pu = 325.014 kN ∴ O.K
ΦMn = ΦPn x 0.447 = 242.052 kN.m ≥ Mu = 145.169 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 330.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 330.00 = 213.811 kN
≥ Vu (= 150.246 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 500 |  | 430 |  | 277.386 |  | 153.395 |  | 144.639 |  | 553.002
＊ 철근비 검토
As = 1301.200 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA + H13- 4.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0042) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 500.0 x 1000.0 = 10200000.0 N
Cs = As x fy = 520480.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (10200000.0 x 250.00 + 520480.0 x 70.000 + 317760.0 x 450.000) / 11038240.0
= 247.270 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 258.000 mm, ab = k1 x cb = 219.300 mm
fs' = 600 x (258.000 - 50.000) / 258.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 219.300 x 1000.000 = 4473.720 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 520.480 kN
Pb = 4473.720 + 301.554 - 520.480 = 4254.794 kN
Mb = 4473.720 x (430.000 - 219.300/2) + 301.554 x (430.000 - 50.00)
- 4254.794 x (247.270 - 70.000)
= 793.499 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 186.495 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 62.279 mm, a = k1 x c = 52.937 mm 를 사용.
fs = 600 x (430.000 - 62.279) / 62.279 (≤fy) = 400.000 MPa
fs' = 600 x ( 62.279 - 50.000) / 62.279 (≤fy) = 118.298 MPa
Cc = 0.85 x 24.0 x 52.937 x 1000.000 = 1079.921 kN
Cs = As' x (fs' - 0.85 x fck) = 77.770 kN
Ts = As x fs = 520.480 kN
Pn = 1079.921 + 77.770 - 520.480 = 637.211 kN
Mn' = 1079.921 x (430.000 - 52.937/2) + 77.770 x (430.000 - 50.00)
= 465.335 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0045 ＜ 0.0100 (e' = e + Xp - dc = 730.272 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 70.00 = 330.000 mm
c = 600.00 / (600.00+400.00) x 330.000 = 198.000 mm, a = k1 x c = 168.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (330.00-198.00) / 198.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 8796.392 kN ≥ Pn = 637.211 kN
ΦPn = 0.78 x 637.211 = 499.149 kN ≥ Pu = 277.386 kN ∴ O.K
ΦMn = ΦPn x 0.553 = 276.030 kN.m ≥ Mu = 153.395 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 330.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 330.00 = 212.093 kN
≥ Vu (= 144.639 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 400 |  | 350 |  | 301.2 |  | 67.788 |  | 0 |  | 225.059
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0040) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (8160000.0 x 200.00 + 317760.0 x 50.000 + 317760.0 x 330.000) / 8795520.0
= 199.277 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 210.000 mm, ab = k1 x cb = 178.500 mm
fs' = 600 x (210.000 - 70.000) / 210.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 178.500 x 1000.000 = 3641.400 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 3641.400 + 301.554 - 317.760 = 3625.194 kN
Mb = 3641.400 x (350.000 - 178.500/2) + 301.554 x (350.000 - 70.00)
- 3625.194 x (199.277 - 50.000)
= 492.770 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 135.929 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 95.938 mm, a = k1 x c = 81.547 mm 를 사용.
fs = 600 x (350.000 - 95.938) / 95.938 (≤fy) = 400.000 MPa
fs' = 600 x ( 95.938 - 70.000) / 95.938 (≤fy) = 162.218 MPa
Cc = 0.85 x 24.0 x 81.547 x 1000.000 = 1663.567 kN
Cs = As' x (fs' - 0.85 x fck) = 112.660 kN
Ts = As x fs = 317.760 kN
Pn = 1663.567 + 112.660 - 317.760 = 1458.467 kN
Mn' = 1663.567 x (350.000 - 81.547/2) + 112.660 x (350.000 - 70.00)
= 545.963 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0039 ＜ 0.0100 (e' = e + Xp - dc = 374.337 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 50.00 = 350.000 mm
c = 600.00 / (600.00+400.00) x 350.000 = 210.000 mm, a = k1 x c = 178.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (350.00-210.00) / 210.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7010.487 kN ≥ Pn = 1458.467 kN
ΦPn = 0.78 x 1458.467 = 1142.466 kN ≥ Pu = 301.200 kN ∴ O.K
ΦMn = ΦPn x 0.225 = 257.122 kN.m ≥ Mu = 67.788 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 350.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 350.00 = 225.858 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 400 |  | 330 |  | 301.2 |  | 62.863 |  | 0 |  | 208.707
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0040) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (8160000.0 x 200.00 + 317760.0 x 70.000 + 317760.0 x 350.000) / 8795520.0
= 200.723 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 198.000 mm, ab = k1 x cb = 168.300 mm
fs' = 600 x (198.000 - 50.000) / 198.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 168.300 x 1000.000 = 3433.320 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 317.760 kN
Pb = 3433.320 + 301.554 - 317.760 = 3417.114 kN
Mb = 3433.320 x (330.000 - 168.300/2) + 301.554 x (330.000 - 50.00)
- 3417.114 x (200.723 - 70.000)
= 481.823 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 141.003 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 102.561 mm, a = k1 x c = 87.177 mm 를 사용.
fs = 600 x (330.000 - 102.561) / 102.561 (≤fy) = 400.000 MPa
fs' = 600 x (102.561 - 50.000) / 102.561 (≤fy) = 307.491 MPa
Cc = 0.85 x 24.0 x 87.177 x 1000.000 = 1778.408 kN
Cs = As' x (fs' - 0.85 x fck) = 228.065 kN
Ts = As x fs = 317.760 kN
Pn = 1778.408 + 228.065 - 317.760 = 1688.714 kN
Mn' = 1778.408 x (330.000 - 87.177/2) + 228.065 x (330.000 - 50.00)
= 573.215 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0089 ＜ 0.0100 (e' = e + Xp - dc = 339.430 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 70.00 = 330.000 mm
c = 600.00 / (600.00+400.00) x 330.000 = 198.000 mm, a = k1 x c = 168.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (330.00-198.00) / 198.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7010.487 kN ≥ Pn = 1688.714 kN
ΦPn = 0.78 x 1688.714 = 1322.826 kN ≥ Pu = 301.200 kN ∴ O.K
ΦMn = ΦPn x 0.209 = 276.084 kN.m ≥ Mu = 62.863 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 330.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 330.00 = 212.952 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 400 |  | 330 |  | 325.014 |  | 145.169 |  | 150.246 |  | 446.655
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 794.400 mm² (압축중심 = 50.00 mm) , 1단 : H16- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0060) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (8160000.0 x 200.00 + 635520.0 x 70.000 + 317760.0 x 350.000) / 9113280.0
= 196.165 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 198.000 mm, ab = k1 x cb = 168.300 mm
fs' = 600 x (198.000 - 50.000) / 198.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 168.300 x 1000.000 = 3433.320 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 635.520 kN
Pb = 3433.320 + 301.554 - 635.520 = 3099.354 kN
Mb = 3433.320 x (330.000 - 168.300/2) + 301.554 x (330.000 - 50.00)
- 3099.354 x (196.165 - 70.000)
= 537.488 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 173.419 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 69.710 mm, a = k1 x c = 59.254 mm 를 사용.
fs = 600 x (330.000 - 69.710) / 69.710 (≤fy) = 400.000 MPa
fs' = 600 x ( 69.710 - 50.000) / 69.710 (≤fy) = 169.646 MPa
Cc = 0.85 x 24.0 x 59.254 x 1000.000 = 1208.773 kN
Cs = As' x (fs' - 0.85 x fck) = 118.561 kN
Ts = As x fs = 635.520 kN
Pn = 1208.773 + 118.561 - 635.520 = 691.814 kN
Mn' = 1208.773 x (330.000 - 59.254/2) + 118.561 x (330.000 - 50.00)
= 396.280 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0068 ＜ 0.0100 (e' = e + Xp - dc = 572.820 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 70.00 = 330.000 mm
c = 600.00 / (600.00+400.00) x 330.000 = 198.000 mm, a = k1 x c = 168.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (330.00-198.00) / 198.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 7251.730 kN ≥ Pn = 691.814 kN
ΦPn = 0.78 x 691.814 = 541.921 kN ≥ Pu = 325.014 kN ∴ O.K
ΦMn = ΦPn x 0.447 = 242.052 kN.m ≥ Mu = 145.169 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 330.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 330.00 = 213.811 kN
≥ Vu (= 150.246 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
2) 상부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
3) 상부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 388.080 ----------> O.K !!!
4) 상부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
5) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
6) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
7) 하부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
8) 하부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 2292 |  | × | 0.2 |  | = | 458.4 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 458.400 ----------> O.K !!!
9) 하부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
10) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.002 |  | = | 1100 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1100.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
11) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
12) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 158.880 ----------> O.K !!!
13) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 158.880 ----------> O.K !!!
14) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!
15) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 260.240 ----------> O.K !!!
16) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 158.880 ----------> O.K !!!
17) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 158.880 ----------> O.K !!!
18) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 400 |  | × | 0.0025 |  | = | 1000 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 1000.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 317.760 ----------> O.K !!!

## 거더,기둥검토,내측벽체
21. 거더,기둥,내측벽체 검토
(1) 내측벽체 검토
(단위 : kN,m)
|  | 기둥부재 |  | 폭 | 두께 | 높이 |  | 길이 | 축력 |  | 모멘트 |  | 축력×길이 | 모멘트×길이 | Load Case
|  | P1 |  | 1 | 0.3 | 3.2 |  | 1 | 662.81 |  | 0 |  | 662.81 | 0 | 3
[9 empty] | 385.36 |  | 6.37 |  | 385.36 | 6.37 | 1
* 벽체와 기둥의 판별 (P1)
0.4Agfck = 0.4 × 1000 × 300 × 24
|  |  | = 2880000 N = 2880.00 kN | [6 empty] | ≥ 662.81 kN
∴ 벽체로 검토한다
1)벽체 1
① 축력 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 300 |  | 250 |  | 662.807 |  |  | 0 |  | 0 |  | 0
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0034) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (6120000.0 x 150.00 + 202720.0 x 50.000 + 202720.0 x 250.000) / 6525440.0
= 150.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 150.000 mm, ab = k1 x cb = 127.500 mm
fs' = 600 x (150.000 - 50.000) / 150.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 127.500 x 1000.000 = 2601.000 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 202.720 kN
Pb = 2601.000 + 192.381 - 202.720 = 2590.661 kN
Mb = 2601.000 x (250.000 - 127.500/2) + 192.381 x (250.000 - 50.00)
- 2590.661 x (150.000 - 50.000)
= 263.846 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 101.845 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 356.777 mm, a = k1 x c = 303.260 mm 를 사용.
fs = 600 x (250.000 - 356.777) / 356.777 (≤fy) = 179.569 MPa
fs' = 600 x (356.777 - 50.000) / 356.777 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 303.260 x 1000.000 = 6186.513 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 91.006 kN
Pn = 6186.513 + 192.381 - 91.006 = 6469.900 kN
Mn' = 6186.513 x (250.000 - 303.260/2) + 192.381 x (250.000 - 50.00)
= 647.042 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0079 ＜ 0.0100 (e' = e + Xp - dc = 100.000 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 50.00 = 250.000 mm
c = 600.00 / (600.00+400.00) x 250.000 = 150.000 mm, a = k1 x c = 127.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (250.00-150.00) / 150.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5203.810 kN ＜ Pn = 6469.900 kN
ΦPn = 0.78 x 5203.810 = 4076.318 kN ≥ Pu = 662.807 kN ∴ O.K
ΦMn = ΦPn x 0.000 = 0.001 kN.m ≥ Mu = 0.000 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 250.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 250.00 = 177.253 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
② 모멘트 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 300 |  | 250 |  | 385.359 |  |  | 6.368 |  | 0 |  | 16.525
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0034) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (6120000.0 x 150.00 + 202720.0 x 50.000 + 202720.0 x 250.000) / 6525440.0
= 150.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 150.000 mm, ab = k1 x cb = 127.500 mm
fs' = 600 x (150.000 - 50.000) / 150.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 127.500 x 1000.000 = 2601.000 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 202.720 kN
Pb = 2601.000 + 192.381 - 202.720 = 2590.661 kN
Mb = 2601.000 x (250.000 - 127.500/2) + 192.381 x (250.000 - 50.00)
- 2590.661 x (150.000 - 50.000)
= 263.846 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 101.845 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 317.691 mm, a = k1 x c = 270.037 mm 를 사용.
fs = 600 x (250.000 - 317.691) / 317.691 (≤fy) = 127.843 MPa
fs' = 600 x (317.691 - 50.000) / 317.691 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 270.037 x 1000.000 = 5508.762 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 64.791 kN
Pn = 5508.762 + 192.381 - 64.791 = 5765.934 kN
Mn' = 5508.762 x (250.000 - 270.037/2) + 192.381 x (250.000 - 50.00)
= 671.881 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0014 ＜ 0.0100 (e' = e + Xp - dc = 116.525 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 50.00 = 250.000 mm
c = 600.00 / (600.00+400.00) x 250.000 = 150.000 mm, a = k1 x c = 127.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (250.00-150.00) / 150.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5203.810 kN ＜ Pn = 5765.934 kN
ΦPn = 0.78 x 5203.810 = 4076.318 kN ≥ Pu = 385.359 kN ∴ O.K
ΦMn = ΦPn x 0.017 = 67.359 kN.m ≥ Mu = 6.368 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 250.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 250.00 = 167.140 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.

## 절점부 검토
22. 절점부 검토
1) 절점 32
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 94.773 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 94.773 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 883.883 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 94.77 × 10^6 |  |  | = | 0.607 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 883.883²× 1000
∴ 절점부 보강철근 필요없음 !!!
2) 절점 1
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 93.708 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 93.708 kN.m
R = √(T1² + T2²) = 680.074 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 93.71 × 10^6 |  |  | = | 1.013 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 680.074²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 93.71 × 10^6 |  |  | = | 1531.014 mm²
|  |  |  | R × fsa |  |  | 680.074 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1531.014 mm² - 794.400 mm²
[5 empty] | = | 736.614 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H22 @250 - 4EA
∴ Total As = 1548.400 mm² > Req'd As (= 736.614 mm²) -------------> O.K !!!
3) 절점 20
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 94.773 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 94.773 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 883.883 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 94.77 × 10^6 |  |  | = | 0.607 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 883.883²× 1000
∴ 절점부 보강철근 필요없음 !!!
4) 절점 15
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 93.708 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 93.708 kN.m
R = √(T1² + T2²) = 680.074 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 93.71 × 10^6 |  |  | = | 1.013 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 680.074²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 93.71 × 10^6 |  |  | = | 1531.014 mm²
|  |  |  | R × fsa |  |  | 680.074 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1531.014 mm² - 794.400 mm²
[5 empty] | = | 736.614 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H22 @250 - 4EA
∴ Total As = 1548.400 mm² > Req'd As (= 736.614 mm²) -------------> O.K !!!

## 사용성 검토
23. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 580 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 438.195 | O.K |  | 3.506
2 | 상부슬래브 : 제 1경간 중앙부 |  | 500 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 479.639 | O.K |  | 3.837
3 | 상부슬래브 : 제 2경간 지점부 |  | 580 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 445.583 | O.K |  | 3.565
4 | 상부슬래브 : 제 2경간 중앙부 |  | 500 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 479.639 | O.K |  | 3.837
5 | 상부슬래브 : 단지점부(우측) |  | 580 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 438.193 | O.K |  | 3.506
6 | 하부슬래브 : 단지점부(좌측) |  | 480 |  | H16 - 8.0EA |  |  | 125 | 444.587 | O.K |  | 3.557
7 | 하부슬래브 : 제 1경간 중앙부 |  | 500 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 443.298 | O.K |  | 3.546
8 | 하부슬래브 : 제 2경간 지점부 |  | 480 |  | H19 - 8.0EA |  |  | 125 | 444.14 | O.K |  | 3.553
9 | 하부슬래브 : 제 2경간 중앙부 |  | 500 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 443.298 | O.K |  | 3.546
10 | 하부슬래브 : 단지점부(우측) |  | 480 |  | H16 - 8.0EA |  |  | 125 | 444.587 | O.K |  | 3.557
11 | 좌측벽체 : 상부 |  | 430 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 281.138 | O.K |  | 2.249
12 | 좌측벽체 : 중앙부 |  | 350 |  | H16 - 4.0EA |  |  | 250 | 403.43 | O.K |  | 1.614
13 | 좌측벽체 : 중앙부(부모멘트) |  | 330 |  | H16 - 4.0EA |  |  | 250 | 459.529 | O.K |  | 1.838
14 | 좌측벽체 : 하부 |  | 330 |  | H16 - 8.0EA |  |  | 125 | 252.111 | O.K |  | 2.017
15 | 우측벽체 : 상부 |  | 430 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 281.136 | O.K |  | 2.249
16 | 우측벽체 : 중앙부 |  | 350 |  | H16 - 4.0EA |  |  | 250 | 403.43 | O.K |  | 1.614
17 | 우측벽체 : 중앙부(부모멘트) |  | 330 |  | H16 - 4.0EA |  |  | 250 | 459.524 | O.K |  | 1.838
18 | 우측벽체 : 하부 |  | 330 |  | H16 - 8.0EA |  |  | 125 | 252.111 | O.K |  | 2.017
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 94.773 x 1000000 / [1301.200 x (580.000 - 94.084/3)]
= 132.756 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x580.0/(7x1301.200)]
= 94.084 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 132.76) - 2.5 x 62.00 = 438.20 mm
300 x (210 / fs) = 300 x (210 / 132.76) = 474.56 mm
Sa는 작은 값인 438.20 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 438.20 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 80.513 x 1000000 / [1301.200 x (500.000 - 86.763/3)]
= 131.349 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x500.0/(7x1301.200)]
= 86.763 mm
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.35) - 2.5 x 42.00 = 494.55 mm
300 x (210 / fs) = 300 x (210 / 131.35) = 479.64 mm
Sa는 작은 값인 479.64 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 479.64 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 138.881 x 1000000 / [1940.400 x (580.000 - 112.673/3)]
= 131.946 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x580.0/(7x1940.400)]
= 112.673 mm
Use As = 1940.400 mm² (철근도심 : 70.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.95) - 2.5 x 60.50 = 445.58 mm
300 x (210 / fs) = 300 x (210 / 131.95) = 477.47 mm
Sa는 작은 값인 445.58 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 445.58 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 80.513 x 1000000 / [1301.200 x (500.000 - 86.763/3)]
= 131.349 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x500.0/(7x1301.200)]
= 86.763 mm
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.35) - 2.5 x 42.00 = 494.55 mm
300 x (210 / fs) = 300 x (210 / 131.35) = 479.64 mm
Sa는 작은 값인 479.64 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 479.64 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 94.773 x 1000000 / [1301.200 x (580.000 - 94.084/3)]
= 132.756 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x580.0/(7x1301.200)]
= 94.084 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 132.76) - 2.5 x 62.00 = 438.19 mm
300 x (210 / fs) = 300 x (210 / 132.76) = 474.55 mm
Sa는 작은 값인 438.19 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 438.19 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 93.708 x 1000000 / [1588.800 x (480.000 - 92.803/3)]
= 131.340 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x480.0/(7x1588.800)]
= 92.803 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.34) - 2.5 x 62.00 = 444.59 mm
300 x (210 / fs) = 300 x (210 / 131.34) = 479.67 mm
Sa는 작은 값인 444.59 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 444.59 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 87.113 x 1000000 / [1301.200 x (500.000 - 86.763/3)]
= 142.116 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x500.0/(7x1301.200)]
= 86.763 mm
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 142.12) - 2.5 x 42.00 = 449.12 mm
300 x (210 / fs) = 300 x (210 / 142.12) = 443.30 mm
Sa는 작은 값인 443.30 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 443.30 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 134.490 x 1000000 / [2292.000 x (480.000 - 109.095/3)]
= 132.266 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x2292.000/1000.0 + 7x2292.000/1000.0 x √[(1 + 2x1000.0x480.0/(7x2292.000)]
= 109.095 mm
Use As = 2292.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 8.0 EA (= 2292.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 132.27) - 2.5 x 60.50 = 444.14 mm
300 x (210 / fs) = 300 x (210 / 132.27) = 476.31 mm
Sa는 작은 값인 444.14 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 444.14 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 87.113 x 1000000 / [1301.200 x (500.000 - 86.763/3)]
= 142.116 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x500.0/(7x1301.200)]
= 86.763 mm
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 142.12) - 2.5 x 42.00 = 449.12 mm
300 x (210 / fs) = 300 x (210 / 142.12) = 443.30 mm
Sa는 작은 값인 443.30 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 443.30 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 93.708 x 1000000 / [1588.800 x (480.000 - 92.803/3)]
= 131.340 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x480.0/(7x1588.800)]
= 92.803 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.34) - 2.5 x 62.00 = 444.59 mm
300 x (210 / fs) = 300 x (210 / 131.34) = 479.67 mm
Sa는 작은 값인 444.59 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 444.59 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 94.773 x 1000000 / [1301.200 x (430.000 - 79.865/3)]
= 180.562 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x430.0/(7x1301.200)]
= 79.865 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 180.56) - 2.5 x 62.00 = 281.14 mm
300 x (210 / fs) = 300 x (210 / 180.56) = 348.91 mm
Sa는 작은 값인 281.14 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 281.14 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 40.724 x 1000000 / [794.400 x (350.000 - 57.077/3)]
= 154.889 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x350.0/(7x794.400)]
= 57.077 mm
Use As = 794.400 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.89) - 2.5 x 42.00 = 403.43 mm
300 x (210 / fs) = 300 x (210 / 154.89) = 406.74 mm
Sa는 작은 값인 403.43 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 403.43 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 31.718 x 1000000 / [794.400 x (330.000 - 55.275/3)]
= 128.147 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x330.0/(7x794.400)]
= 55.275 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 128.15) - 2.5 x 62.00 = 459.53 mm
300 x (210 / fs) = 300 x (210 / 128.15) = 491.62 mm
Sa는 작은 값인 459.53 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 459.53 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 93.708 x 1000000 / [1588.800 x (330.000 - 75.273/3)]
= 193.436 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x330.0/(7x1588.800)]
= 75.273 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 193.44) - 2.5 x 62.00 = 252.11 mm
300 x (210 / fs) = 300 x (210 / 193.44) = 325.69 mm
Sa는 작은 값인 252.11 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 252.11 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 94.773 x 1000000 / [1301.200 x (430.000 - 79.865/3)]
= 180.563 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x430.0/(7x1301.200)]
= 79.865 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 180.56) - 2.5 x 62.00 = 281.14 mm
300 x (210 / fs) = 300 x (210 / 180.56) = 348.91 mm
Sa는 작은 값인 281.14 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 281.14 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 40.724 x 1000000 / [794.400 x (350.000 - 57.077/3)]
= 154.888 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x350.0/(7x794.400)]
= 57.077 mm
Use As = 794.400 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.89) - 2.5 x 42.00 = 403.43 mm
300 x (210 / fs) = 300 x (210 / 154.89) = 406.74 mm
Sa는 작은 값인 403.43 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 403.43 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 31.719 x 1000000 / [794.400 x (330.000 - 55.275/3)]
= 128.148 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x330.0/(7x794.400)]
= 55.275 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 128.15) - 2.5 x 62.00 = 459.52 mm
300 x (210 / fs) = 300 x (210 / 128.15) = 491.62 mm
Sa는 작은 값인 459.52 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 459.52 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 93.708 x 1000000 / [1588.800 x (330.000 - 75.273/3)]
= 193.436 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x330.0/(7x1588.800)]
= 75.273 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 193.44) - 2.5 x 62.00 = 252.11 mm
300 x (210 / fs) = 300 x (210 / 193.44) = 325.69 mm
Sa는 작은 값인 252.11 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 252.11 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 3.850 m
- fy = 400 MPa
- 부재두께(T) = 0.55 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 3.850 / 28
T = 0.138 m < 0.550 m -----------> O.K

## 기초 지지력 검토
24. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  |  | = | 317.03 |  | / | 8.1 |  | = | 39.14 |  | kN/m²
|  |  | - 상부연직하중 |  |  |  | = | 76 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  |  | 10 |  | kN/m²
- 암거 내부 활하중
t = 0 mm (암거내부 포장두께)
T = 550 mm (하부 슬래브 두께)
b' = 0.500 + 2 × ( 0.550 + 0.000 ) × cot 45°
= 1.600 m
a' = 0.200 + 2 × ( 0.550 + 0.000 ) × cot 45°
= 1.300 m
|  |  |  | Qz = 96.0 / ( 1.600 × 1.300 ) = | [7 empty] | 46.154 |  | kN/m²
3) 최대 지반 반력
|  |  | Qmax |  | = | 39.14 |  | + | 76 |  | + | 10 |  | + | 46.154
[5 empty] | = | 171.293 |  | kN/m²

## 주철근 조립도
25. 주철근 조립도