## 표지
P2-5C 구조계산서
| ▣ 구조형식 |  | : | 지중 2 련 암거
( 내공 : 2@(3M ⅹ 2.5M) )
| ▣ 토 피(FH) |  | = | 8.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 거더,기둥,내측벽체 검토
[5 empty] | 22. | 절점부 검토
[5 empty] | 23. | 사용성 검토
[5 empty] | 24. | 기초 지지력 검토
[5 empty] | 25. | 주철근 조립도

## 설계요약표
1. 설계 요약표
P2-5C (토피=8.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 8.0m
안정(지지력)검토 | Qmax = 240.929 kN/m²
단면 위치 | 내구성검토 |  |  | 단 면 검 토 | [13 empty] | 절 점 부 보 강
| 균열검토 |  |  | 휨 검 토 | [6 empty] | 전 단 검 토
| 철근간격 mm | 최대간격 mm |  | 사용철근 | Mu kN.m |  | ΦMn kN.m |  | S.F |  | 사용철근 |  | Vu kN |  | ΦVn kN |  | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 598.486 |  | H16 - 8.0EA | 188.652 |  | 394.929 |  | 2.09 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.459 | 0.637
상부슬래브 : 제 1경간 중앙부 | 125 | 546.692 |  | H16 - 8.0EA | 175.393 |  | 342.711 |  | 1.95 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 지점부 | 125 | 474.96 |  | H19 - 4.0EA + H16 - 4.0EA | 262.142 |  | 480.052 |  | 1.83 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 중앙부 | 125 | 546.692 |  | H16 - 8.0EA | 175.393 |  | 342.711 |  | 1.95 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 단지점부(우측) | 125 | 598.485 |  | H16 - 8.0EA | 188.652 |  | 394.929 |  | 2.09 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.459 | 0.637
하부슬래브 : 단지점부(좌측) | 125 | 517.541 |  | H16 - 4.0EA + H13 - 4.0EA | 140.502 |  | 273.073 |  | 1.94 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.574 | 0.637 | H19 @250 - 4EA
하부슬래브 : 제 1경간 중앙부 | 125 | 429.5 |  | H16 - 4.0EA + H13 - 4.0EA | 178.424 |  | 281.921 |  | 1.58 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 지점부 | 125 | 427.72 |  | H19 - 8.0EA | 284.381 |  | 473.436 |  | 1.66 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 중앙부 | 125 | 429.5 |  | H16 - 4.0EA + H13 - 4.0EA | 178.424 |  | 281.921 |  | 1.58 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 단지점부(우측) | 125 | 517.541 |  | H16 - 4.0EA + H13 - 4.0EA | 140.502 |  | 273.073 |  | 1.94 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.574 | 0.637 | H19 @250 - 4EA
좌측벽체 : 상부 | 125 | 443.516 |  | H16 - 8.0EA | 188.652 |  | 711.418 |  | 3.77 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부 | 250 | 602.034 |  | H13 - 4.0EA | 44.633 |  | 595.834 |  | 13.35 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부(부모멘트) | 250 | 754.754 |  | H16 - 4.0EA | 89.12 |  | 664.508 |  | 7.46 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 하부 | 125 | 353.708 |  | H16 - 4.0EA + H13 - 4.0EA | 140.502 |  | 581.599 |  | 4.14 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 상부 | 125 | 443.515 |  | H16 - 8.0EA | 188.652 |  | 711.418 |  | 3.77 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부 | 250 | 602.036 |  | H13 - 4.0EA | 44.633 |  | 595.832 |  | 13.35 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부(부모멘트) | 250 | 754.754 |  | H16 - 4.0EA | 89.12 |  | 664.508 |  | 7.46 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 하부 | 125 | 353.708 |  | H16 - 4.0EA + H13 - 4.0EA | 140.502 |  | 581.599 |  | 4.14 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
기둥단면검토
기둥 위치 | 기둥 형태 |  | 사용 철근 |  |  | e |  | eb |  | Pu |  | ΦPn |  | Mu |  | ΦMn |  | 비 고
[6 empty] | (mm) |  | (mm) |  | (kN) |  | (kN) |  | (kN.m) |  | (kN.m)
P1 | 벽 체 |  | H13 |  |  | 0 |  | 127.387 |  | 976.325 |  | 4443.277 |  | 0 |  | 0.001 |  | 축력 최대시
[6 empty] | 36.853 |  | 127.387 |  | 539.219 |  | 5354.718 |  | 19.872 |  | 197.338 |  | 모멘트 최대시

## 설계조건
2. 설계조건
1) 구조형식
- 지중 2 련 암거 ( 내공 : 2@(3M ⅹ 2.5M), 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 10 |  | kN/m² |  | (∵ 토피 : | 8 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.700 × 1.000 = 0.700 |  |  |  | 0.02858 |  | 1~14,20~31
| 2 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 15~19,32~36
| 3 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 37
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.275 | 0.35 | 23 |  | 5.45 |  | 3.55
| 2 |  | 0.55 | 0.35 | 24 |  | 4.58 |  | 3.55
| 3 |  | 1.18 | 0.35 | 25 |  | 3.95 |  | 3.55
| 4 |  | 1.433 | 0.35 | 26 |  | 3.75 |  | 3.55
| 5 |  | 2.592 | 0.35 | 27 |  | 3.55 |  | 3.55
| 6 |  | 2.92 | 0.35 | 28 |  | 2.92 |  | 3.55
| 7 |  | 3.55 | 0.35 | 29 |  | 2.05 |  | 3.55
| 8 |  | 3.75 | 0.35 | 30 |  | 1.18 |  | 3.55
| 9 |  | 3.95 | 0.35 | 31 |  | 0.55 |  | 3.55
| 10 |  | 4.58 | 0.35 | 32 |  | 0.275 |  | 3.55
| 11 |  | 4.908 | 0.35 | 33 |  | 0.275 |  | 3.2
| 12 |  | 6.067 | 0.35 | 34 |  | 0.275 |  | 2.72
| 13 |  | 6.32 | 0.35 | 35 |  | 0.275 |  | 1.18
| 14 |  | 6.95 | 0.35 | 36 |  | 0.275 |  | 0.7
| 15 |  | 7.225 | 0.35 | 37 |  | 0.275 |  | -0.15
| 16 |  | 7.225 | 0.7 | 38 |  | 1.433 |  | -0.15
| 17 |  | 7.225 | 1.18 | 39 |  | 2.592 |  | -0.15
| 18 |  | 7.225 | 2.72 | 40 |  | 3.75 |  | -0.15
| 19 |  | 7.225 | 3.2 | 41 |  | 4.908 |  | -0.15
| 20 |  | 7.225 | 3.55 | 42 |  | 6.067 |  | -0.15
| 21 |  | 6.95 | 3.55 | 43 |  | 7.225 |  | -0.15
| 22 |  | 6.32 | 3.55

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.700 × 1.000 = 0.700 |  |  |  | 0.02858 |  | 1~14,23~28,30~36
| 2 | 0.550 × 1.000 = 0.550 |  |  |  | 0.01386 |  | 15~22,37~44
| 3 | 0.400 × 1.000 = 0.400 |  |  |  | 0.00533 |  | 45
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.275 | 0.35 | 34 |  | 1.433 |  | 3.55
| 2 |  | 0.55 | 0.35 | 35 |  | 1.18 |  | 3.55
| 3 |  | 1.18 | 0.35 | 36 |  | 0.55 |  | 3.55
| 4 |  | 1.433 | 0.35 | 37 |  | 0.275 |  | 3.55
| 5 |  | 2.592 | 0.35 | 38 |  | 0.275 |  | 3.2
| 6 |  | 2.92 | 0.35 | 39 |  | 0.275 |  | 2.72
| 7 |  | 3.55 | 0.35 | 40 |  | 0.275 |  | 2.483
| 8 |  | 3.75 | 0.35 | 41 |  | 0.275 |  | 1.95
| 9 |  | 3.95 | 0.35 | 42 |  | 0.275 |  | 1.417
| 10 |  | 4.58 | 0.35 | 43 |  | 0.275 |  | 1.18
| 11 |  | 4.908 | 0.35 | 44 |  | 0.275 |  | 0.7
| 12 |  | 6.067 | 0.35 | 45 |  | 0.275 |  | -0.15
| 13 |  | 6.32 | 0.35 | 46 |  | 1.433 |  | -0.15
| 14 |  | 6.95 | 0.35 | 47 |  | 2.592 |  | -0.15
| 15 |  | 7.225 | 0.35 | 48 |  | 3.75 |  | -0.15
| 16 |  | 7.225 | 0.7 | 49 |  | 4.908 |  | -0.15
| 17 |  | 7.225 | 1.18 | 50 |  | 6.067 |  | -0.15
| 18 |  | 7.225 | 1.417 | 51 |  | 7.225 |  | -0.15
| 19 |  | 7.225 | 1.95 | 52 |  | 7.725 |  | 0.35
| 20 |  | 7.225 | 2.483 | 53 |  | 7.725 |  | 1.417
| 21 |  | 7.225 | 2.72 | 54 |  | 7.725 |  | 2.483
| 22 |  | 7.225 | 3.2 | 55 |  | 7.725 |  | 3.55
| 23 |  | 7.225 | 3.55 | 56 |  | 7.225 |  | 4.05
| 24 |  | 6.95 | 3.55 | 57 |  | 6.067 |  | 4.05
| 25 |  | 6.32 | 3.55 | 58 |  | 4.908 |  | 4.05
| 26 |  | 6.067 | 3.55 | 59 |  | 3.75 |  | 4.05
| 27 |  | 4.908 | 3.55 | 60 |  | 2.592 |  | 4.05
| 28 |  | 4.58 | 3.55 | 61 |  | 1.433 |  | 4.05
| 29 |  | 3.95 | 3.55 | 62 |  | 0.275 |  | 4.05
| 30 |  | 3.75 | 3.55 | 63 |  | -0.225 |  | 3.55
| 31 |  | 3.55 | 3.55 | 64 |  | -0.225 |  | 2.483
| 32 |  | 2.92 | 3.55 | 65 |  | -0.225 |  | 1.417
| 33 |  | 2.592 | 3.55 | 66 |  | -0.225 |  | 0.35

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 7.500 × 7.500 ) |  |  | = | 7.5 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 7.500 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 12521.981 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.550/2 + 1.158/2) = 10694 kN/m |  |  |  |  | 1,15
| Kv2 |  |  | Kvⅹ(1.158/2 + 1.158/2) = 14500 kN/m |  |  |  |  | 4~5,8,11,12
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 3.200m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 7.500 × 7.500 ) |  |  |  |  | = | 7.5 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 7.500 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 31501.96 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 31501.960 |  |  |  |  | = | 10500.65 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 7.500 × 7.500 ) |  |  |  |  | = | 7.5 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 7.500 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 31501.96 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 31501.960 |  |  |  |  | = | 10500.65 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 3.900 × 3.900 ) |  |  |  |  | = | 3.9 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 3.900 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 51444.05 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 51444.050 |  |  |  |  | = | 17148.02 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(1.158/2 + 0.550/2) = 26903 kN/m | [8 empty] | 23,37
|  | Ksb1 |  |  | Ksbⅹ(1.158/2 + 0.550/2) = 8968 kN/m
|  | Kv2 |  |  | Kvⅹ(1.158/2 + 1.158/2) = 36479 kN/m | [8 empty] | 26~27,30,33,34
|  | Ksb2 |  |  | Ksbⅹ(1.158/2 + 1.158/2) = 12160 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(1.067/2 + 0.700/2) = 45451 kN/m | [8 empty] | 1,15,23,37
|  | Kss1 |  |  | Kssⅹ(1.067/2 + 0.700/2) = 15150 kN/m
|  | Kh2 |  |  | Khⅹ(1.067/2 + 1.067/2) = 54891 kN/m | [8 empty] | 18,20,40,42
|  | Kss2 |  |  | Kssⅹ(1.067/2 + 1.067/2) = 18297 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.550/2 + 1.158/2) = 26903 kN/m | [8 empty] | 1,15
|  | Ksb1 |  |  | Ksbⅹ(0.550/2 + 1.158/2) = 8968 kN/m
|  | Kv2 |  |  | Kvⅹ(1.158/2 + 1.158/2) = 36479 kN/m | [8 empty] | 4~5,8,11,12
|  | Ksb2 |  |  | Ksbⅹ(1.158/2 + 1.158/2) = 12160 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 8.00 × 19.00 |  |  |  |  | = | 152 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 152 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 상부 슬래브에 작용하는 하중 (Wl1) - 토피 4m 이상
|  |  | - Wl1 |  | = | 10.000 kN/m²
② 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (8.350 × 19.000) × 0.500 | [9 empty] | = | 79.325 | kN/m²
|  | - Wh2 |  | = | 79.325 + 0.350 × 19.000 × 0.500 | [9 empty] | = | 82.65 | kN/m²
|  | - Wh3 |  | = | 82.650 + 0.480 × 19.000 × 0.500 | [9 empty] | = | 87.21 | kN/m²
|  | - Wh4 |  | = | 87.210 + 1.540 × 19.000 × 0.500 | [9 empty] | = | 101.84 | kN/m²
|  | - Wh5 |  | = | 101.840 + 0.480 × 19.000 × 0.500 | [9 empty] | = | 106.4 | kN/m²
|  | - Wh6 |  | = | 106.400 + 0.350 × 19.000 × 0.500 | [9 empty] | = | 109.725 | kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 11.2 |  | 197.3 |  |  |  | 19 |  |  | 0.227
|  | 계 | [11 empty] | 0.227
Tg = 1.25 Tg' = 1.25 × 0.227 = 0.284 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.284 / 2π × 2.617 = 0.118 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 8.35 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 11.55 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.118 × 0.284 × cos(π× 8.350 / (2 × 30.000)) = 0.006152
U(Zb) = 2 / π²× 0.118 × 0.284 × cos(π× 11.550 / (2 × 30.000)) = 0.005587
Po = Ksb,top × (U(Zu) - U(Zb))
= 10500.650 × (0.006152 - 0.005587) = 5.933 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 8.35 |  | 51444.05 |  |  |  | 0.006152 |  |  |  |  | 0.000565 |  | 29.066
|  | 8.7 |  | 51444.05 |  |  |  | 0.006098 |  |  |  |  | 0.000511 |  | 26.288
|  | 9.18 |  | 51444.05 |  |  |  | 0.006021 |  |  |  |  | 0.000434 |  | 22.327
|  | 9.417 |  | 51444.05 |  |  |  | 0.005982 |  |  |  |  | 0.000395 |  | 20.32
|  | 9.95 |  | 51444.05 |  |  |  | 0.00589 |  |  |  |  | 0.000303 |  | 15.588
|  | 10.483 |  | 51444.05 |  |  |  | 0.005793 |  |  |  |  | 0.000206 |  | 10.598
|  | 10.72 |  | 51444.05 |  |  |  | 0.005749 |  |  |  |  | 0.000162 |  | 8.334
|  | 11.2 |  | 51444.05 |  |  |  | 0.005656 |  |  |  |  | 6.9e-05 |  | 3.55
|  | 11.55 |  | 51444.05 |  |  |  | 0.005587 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000151 = 2.850 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000202 = 3.810 kN/m²
Vs = (Vu - Vb) / 2 = (2.850 + 3.810) / 2 = 3.330 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.700 × 24.500 × 0.160 × (1 - 0.015 × 8.350) = 2.400 kN/m²
② 하부슬래브
fb = 0.700 × 24.500 × 0.160 × (1 - 0.015 × 11.550) = 2.269 kN/m²
③ 중간벽체
fu1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 8.350) = 1.372 kN/m²
fb1 = 0.400 × 24.500 × 0.160 × (1 - 0.015 × 11.550) = 1.296 kN/m²
④ 측벽
f1 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.350) = 1.886 kN/m²
f2 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 8.700) = 1.875 kN/m²
f3 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.180) = 1.859 kN/m²
f4 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.417) = 1.851 kN/m²
f5 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 9.950) = 1.834 kN/m²
f6 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.483) = 1.817 kN/m²
f7 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 10.720) = 1.809 kN/m²
f8 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.200) = 1.794 kN/m²
f9 = 0.550 × 24.500 × 0.160 × (1 - 0.015 × 11.550) = 1.782 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 0.875, h = 8.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
2) 극한하중 기둥최대편심 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.4 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.4 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.4 | 1.6 | 0.8 | 0.8
3) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1
| 2 |  | 1 | 0.875 |  | 1 | 1
| 3 |  | 1 | 0.875 | 1 | 0.5 | 0.5
4) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 0.875 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 9 J= 9, 10 SEC=1 NSEG=2 ANG=180
10 J= 10, 11 SEC=1 NSEG=1 ANG=180
| JOINT | 11 J= 11, 12 SEC=1 NSEG=4 ANG=180
| 1 X= 0.275 Y= 0.000 Z= 0.350 | 12 J= 12, 13 SEC=1 NSEG=1 ANG=180
| 2 X= 0.550 Y= 0.000 Z= 0.350 | 13 J= 13, 14 SEC=1 NSEG=2 ANG=180
| 3 X= 1.180 Y= 0.000 Z= 0.350 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=180
| 4 X= 1.433 Y= 0.000 Z= 0.350 | 15 J= 15, 16 SEC=2 NSEG=1 ANG=0
| 5 X= 2.592 Y= 0.000 Z= 0.350 | 16 J= 16, 17 SEC=2 NSEG=1 ANG=0
| 6 X= 2.920 Y= 0.000 Z= 0.350 | 17 J= 17, 18 SEC=2 NSEG=4 ANG=0
| 7 X= 3.550 Y= 0.000 Z= 0.350 | 18 J= 18, 19 SEC=2 NSEG=1 ANG=0
| 8 X= 3.750 Y= 0.000 Z= 0.350 | 19 J= 19, 20 SEC=2 NSEG=1 ANG=0
| 9 X= 3.950 Y= 0.000 Z= 0.350 | 20 J= 20, 21 SEC=1 NSEG=1 ANG=0
| 10 X= 4.580 Y= 0.000 Z= 0.350 | 21 J= 21, 22 SEC=1 NSEG=2 ANG=0
| 11 X= 4.908 Y= 0.000 Z= 0.350 | 22 J= 22, 23 SEC=1 NSEG=2 ANG=0
| 12 X= 6.067 Y= 0.000 Z= 0.350 | 23 J= 23, 24 SEC=1 NSEG=2 ANG=0
| 13 X= 6.320 Y= 0.000 Z= 0.350 | 24 J= 24, 25 SEC=1 NSEG=2 ANG=0
| 14 X= 6.950 Y= 0.000 Z= 0.350 | 25 J= 25, 26 SEC=1 NSEG=1 ANG=0
| 15 X= 7.225 Y= 0.000 Z= 0.350 | 26 J= 26, 27 SEC=1 NSEG=1 ANG=0
| 16 X= 7.225 Y= 0.000 Z= 0.700 | 27 J= 27, 28 SEC=1 NSEG=2 ANG=0
| 17 X= 7.225 Y= 0.000 Z= 1.180 | 28 J= 28, 29 SEC=1 NSEG=2 ANG=0
| 18 X= 7.225 Y= 0.000 Z= 2.720 | 29 J= 29, 30 SEC=1 NSEG=2 ANG=0
| 19 X= 7.225 Y= 0.000 Z= 3.200 | 30 J= 30, 31 SEC=1 NSEG=2 ANG=0
| 20 X= 7.225 Y= 0.000 Z= 3.550 | 31 J= 31, 32 SEC=1 NSEG=1 ANG=0
| 21 X= 6.950 Y= 0.000 Z= 3.550 | 32 J= 32, 33 SEC=2 NSEG=1 ANG=180
| 22 X= 6.320 Y= 0.000 Z= 3.550 | 33 J= 33, 34 SEC=2 NSEG=1 ANG=180
| 23 X= 5.450 Y= 0.000 Z= 3.550 | 34 J= 34, 35 SEC=2 NSEG=4 ANG=180
| 24 X= 4.580 Y= 0.000 Z= 3.550 | 35 J= 35, 36 SEC=2 NSEG=1 ANG=180
| 25 X= 3.950 Y= 0.000 Z= 3.550 | 36 J= 36, 1 SEC=2 NSEG=1 ANG=180
| 26 X= 3.750 Y= 0.000 Z= 3.550 | 37 J= 26, 8 SEC=3 NSEG=4 ANG=0
27 X= 3.550 Y= 0.000 Z= 3.550
| 28 X= 2.920 Y= 0.000 Z= 3.550 | NLLINK
| 29 X= 2.050 Y= 0.000 Z= 3.550 | 1 J=1,37 NLP=SP1 ANG=0
| 30 X= 1.180 Y= 0.000 Z= 3.550 | 2 J=4,38 NLP=SP2 ANG=0
| 31 X= 0.550 Y= 0.000 Z= 3.550 | 3 J=5,39 NLP=SP2 ANG=0
| 32 X= 0.275 Y= 0.000 Z= 3.550 | 4 J=8,40 NLP=SP2 ANG=0
| 33 X= 0.275 Y= 0.000 Z= 3.200 | 5 J=11,41 NLP=SP2 ANG=0
| 34 X= 0.275 Y= 0.000 Z= 2.720 | 6 J=12,42 NLP=SP2 ANG=0
| 35 X= 0.275 Y= 0.000 Z= 1.180 | 7 J=15,43 NLP=SP1 ANG=0
36 X= 0.275 Y= 0.000 Z= 0.700
| 37 X= 0.275 Y= 0.000 Z= -0.150 | LOAD
| 38 X= 1.433 Y= 0.000 Z= -0.150 | NAME=SELFWGT SW=1
| 39 X= 2.592 Y= 0.000 Z= -0.150 | NAME=NWDEAD
| 40 X= 3.750 Y= 0.000 Z= -0.150 | TYPE=Distributed Span
| 41 X= 4.908 Y= 0.000 Z= -0.150 | ADD=20 RD=0,1 UZ=-152,-152
| 42 X= 6.067 Y= 0.000 Z= -0.150 | ADD=21 RD=0,1 UZ=-152,-152
| 43 X= 7.225 Y= 0.000 Z= -0.150 | ADD=22 RD=0,1 UZ=-152,-152
ADD=23 RD=0,1 UZ=-152,-152
| RESTRAINT | ADD=24 RD=0,1 UZ=-152,-152
| ADD=37 DOF=U1, U2, U3, R1, R2, R3 | ADD=25 RD=0,1 UZ=-152,-152
| ADD=38 DOF=U1, U2, U3, R1, R2, R3 | ADD=26 RD=0,1 UZ=-152,-152
| ADD=39 DOF=U1, U2, U3, R1, R2, R3 | ADD=27 RD=0,1 UZ=-152,-152
| ADD=40 DOF=U1, U2, U3, R1, R2, R3 | ADD=28 RD=0,1 UZ=-152,-152
| ADD=41 DOF=U1, U2, U3, R1, R2, R3 | ADD=29 RD=0,1 UZ=-152,-152
| ADD=42 DOF=U1, U2, U3, R1, R2, R3 | ADD=30 RD=0,1 UZ=-152,-152
| ADD=43 DOF=U1, U2, U3, R1, R2, R3 | ADD=31 RD=0,1 UZ=-152,-152
NAME=LIVEFULL
| SPRING | TYPE=Distributed Span
| ADD=1 U1=1e+010 | ADD=20 RD=0,1 UZ=-10,-10
ADD=21 RD=0,1 UZ=-10,-10
| MATERIAL | ADD=22 RD=0,1 UZ=-10,-10
| NAME=CONC IDES=C M=0.0001 W=24.5 | ADD=23 RD=0,1 UZ=-10,-10
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | ADD=24 RD=0,1 UZ=-10,-10
ADD=25 RD=0,1 UZ=-10,-10
| NLPROP | ADD=26 RD=0,1 UZ=-10,-10
| NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=27 RD=0,1 UZ=-10,-10
| DOF=U1 KE=10693.8 CE=0.99999 K=10693.8 OPEN=0 | ADD=28 RD=0,1 UZ=-10,-10
| NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | ADD=29 RD=0,1 UZ=-10,-10
| DOF=U1 KE=14500.5 CE=0.99999 K=14500.5 OPEN=0 | ADD=30 RD=0,1 UZ=-10,-10
ADD=31 RD=0,1 UZ=-10,-10
| FRAME SECTION | NAME=HORLIVE
| NAME=1 MAT=CONC SH=R T=0.7, 1 | TYPE=Distributed Span
| NAME=2 MAT=CONC SH=R T=0.55, 1 | ADD=15 RD=0,1 UX=-5,-5
| NAME=3 MAT=CONC SH=R T=0.4, 1 | ADD=16 RD=0,1 UX=-5,-5
ADD=17 RD=0,1 UX=-5,-5
| FRAME | ADD=18 RD=0,1 UX=-5,-5
| 1 J= 1, 2 SEC=1 NSEG=1 ANG=180 | ADD=19 RD=0,1 UX=-5,-5
| 2 J= 2, 3 SEC=1 NSEG=2 ANG=180 | ADD=32 RD=0,1 UX=5,5
| 3 J= 3, 4 SEC=1 NSEG=1 ANG=180 | ADD=33 RD=0,1 UX=5,5
| 4 J= 4, 5 SEC=1 NSEG=4 ANG=180 | ADD=34 RD=0,1 UX=5,5
| 5 J= 5, 6 SEC=1 NSEG=1 ANG=180 | ADD=35 RD=0,1 UX=5,5
| 6 J= 6, 7 SEC=1 NSEG=2 ANG=180 | ADD=36 RD=0,1 UX=5,5
| 7 J= 7, 8 SEC=1 NSEG=1 ANG=180 | NAME=NWSOFULL
TYPE=Distributed Span
| ADD=15 RD=0,1 UX=-109.725,-106.4 | OUTPUT
| ADD=16 RD=0,1 UX=-106.4,-101.84 | ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
| ADD=17 RD=0,1 UX=-101.84,-87.21 | ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*
ADD=18 RD=0,1 UX=-87.21,-82.65
ADD=19 RD=0,1 UX=-82.65,-79.325
ADD=32 RD=0,1 UX=79.325,82.65
ADD=33 RD=0,1 UX=82.65,87.21
ADD=34 RD=0,1 UX=87.21,101.84
ADD=35 RD=0,1 UX=101.84,106.4
ADD=36 RD=0,1 UX=106.4,109.725
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=HORLIVE
LOAD=NWSOFULL
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.4 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST7 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
NAME=HIST8 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=HORLIVE SF=1 AT=1
LOAD=NWSOFULL SF=1 AT=1
NAME=HIST9 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=HORLIVE SF=0.5 AT=1
LOAD=NWSOFULL SF=0.5 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
HIST=HIST3 SF=1
HIST=HIST4 SF=1
HIST=HIST5 SF=1
HIST=HIST6 SF=1
NAME=SERVICE TYPE=ENVE
HIST=HIST7 SF=1
HIST=HIST8 SF=1
HIST=HIST9 SF=1

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | ADD=56 DOF=U1, U2, U3, R1, R2, R3
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | ADD=57 DOF=U1, U2, U3, R1, R2, R3
ADD=58 DOF=U1, U2, U3, R1, R2, R3
| JOINT | ADD=59 DOF=U1, U2, U3, R1, R2, R3
| 1 X= 0.275 Y= 0.000 Z= 0.350 | ADD=60 DOF=U1, U2, U3, R1, R2, R3
| 2 X= 0.550 Y= 0.000 Z= 0.350 | ADD=61 DOF=U1, U2, U3, R1, R2, R3
| 3 X= 1.180 Y= 0.000 Z= 0.350 | ADD=62 DOF=U1, U2, U3, R1, R2, R3
| 4 X= 1.433 Y= 0.000 Z= 0.350 | ADD=63 DOF=U1, U2, U3, R1, R2, R3
| 5 X= 2.592 Y= 0.000 Z= 0.350 | ADD=64 DOF=U1, U2, U3, R1, R2, R3
| 6 X= 2.920 Y= 0.000 Z= 0.350 | ADD=65 DOF=U1, U2, U3, R1, R2, R3
| 7 X= 3.550 Y= 0.000 Z= 0.350 | ADD=66 DOF=U1, U2, U3, R1, R2, R3
8 X= 3.750 Y= 0.000 Z= 0.350
| 9 X= 3.950 Y= 0.000 Z= 0.350 | SPRING
| 10 X= 4.580 Y= 0.000 Z= 0.350 | ADD=1 U1=8967.56 U3=15150.3
| 11 X= 4.908 Y= 0.000 Z= 0.350 | ADD=4 U1=12159.8
| 12 X= 6.067 Y= 0.000 Z= 0.350 | ADD=5 U1=12159.8
| 13 X= 6.320 Y= 0.000 Z= 0.350 | ADD=8 U1=12159.8
| 14 X= 6.950 Y= 0.000 Z= 0.350 | ADD=11 U1=12159.8
| 15 X= 7.225 Y= 0.000 Z= 0.350 | ADD=12 U1=12159.8
| 16 X= 7.225 Y= 0.000 Z= 0.700 | ADD=15 U1=8967.56 U3=15150.3
| 17 X= 7.225 Y= 0.000 Z= 1.180 | ADD=18 U3=18296.9
| 18 X= 7.225 Y= 0.000 Z= 1.417 | ADD=20 U3=18296.9
| 19 X= 7.225 Y= 0.000 Z= 1.950 | ADD=23 U1=8967.56 U3=15150.3
| 20 X= 7.225 Y= 0.000 Z= 2.483 | ADD=26 U1=12159.8
| 21 X= 7.225 Y= 0.000 Z= 2.720 | ADD=27 U1=12159.8
| 22 X= 7.225 Y= 0.000 Z= 3.200 | ADD=30 U1=12159.8
| 23 X= 7.225 Y= 0.000 Z= 3.550 | ADD=33 U1=12159.8
| 24 X= 6.950 Y= 0.000 Z= 3.550 | ADD=34 U1=12159.8
| 25 X= 6.320 Y= 0.000 Z= 3.550 | ADD=37 U1=8967.56 U3=15150.3
| 26 X= 6.067 Y= 0.000 Z= 3.550 | ADD=40 U3=18296.9
| 27 X= 4.908 Y= 0.000 Z= 3.550 | ADD=42 U3=18296.9
28 X= 4.580 Y= 0.000 Z= 3.550
| 29 X= 3.950 Y= 0.000 Z= 3.550 | MATERIAL
| 30 X= 3.750 Y= 0.000 Z= 3.550 | NAME=CONC IDES=C M=0.0001 W=24.5
| 31 X= 3.550 Y= 0.000 Z= 3.550 | T=0 E=2.7e+007 U=0.17 A=9.99e-006
32 X= 2.920 Y= 0.000 Z= 3.550
| 33 X= 2.592 Y= 0.000 Z= 3.550 | NLPROP
| 34 X= 1.433 Y= 0.000 Z= 3.550 | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 35 X= 1.180 Y= 0.000 Z= 3.550 | DOF=U1 KE=26902.7 CE=0.99999 K=26902.7 OPEN=0
| 36 X= 0.550 Y= 0.000 Z= 3.550 | NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 37 X= 0.275 Y= 0.000 Z= 3.550 | DOF=U1 KE=36479.3 CE=0.99999 K=36479.3 OPEN=0
| 38 X= 0.275 Y= 0.000 Z= 3.200 | NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 39 X= 0.275 Y= 0.000 Z= 2.720 | DOF=U1 KE=45450.8 CE=0.99999 K=45450.8 OPEN=0
| 40 X= 0.275 Y= 0.000 Z= 2.483 | NAME=SP4 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| 41 X= 0.275 Y= 0.000 Z= 1.950 | DOF=U1 KE=54890.8 CE=0.99999 K=54890.8 OPEN=0
42 X= 0.275 Y= 0.000 Z= 1.417
| 43 X= 0.275 Y= 0.000 Z= 1.180 | FRAME SECTION
| 44 X= 0.275 Y= 0.000 Z= 0.700 | NAME=1 MAT=CONC SH=R T=0.7, 1
| 45 X= 0.275 Y= 0.000 Z= -0.150 | NAME=2 MAT=CONC SH=R T=0.55, 1
| 46 X= 1.433 Y= 0.000 Z= -0.150 | NAME=3 MAT=CONC SH=R T=0.4, 1
47 X= 2.592 Y= 0.000 Z= -0.150
| 48 X= 3.750 Y= 0.000 Z= -0.150 | FRAME
| 49 X= 4.908 Y= 0.000 Z= -0.150 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 50 X= 6.067 Y= 0.000 Z= -0.150 | 2 J= 2, 3 SEC=1 NSEG=2 ANG=180
| 51 X= 7.225 Y= 0.000 Z= -0.150 | 3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 52 X= 7.725 Y= 0.000 Z= 0.350 | 4 J= 4, 5 SEC=1 NSEG=4 ANG=180
| 53 X= 7.725 Y= 0.000 Z= 1.417 | 5 J= 5, 6 SEC=1 NSEG=1 ANG=180
| 54 X= 7.725 Y= 0.000 Z= 2.483 | 6 J= 6, 7 SEC=1 NSEG=2 ANG=180
| 55 X= 7.725 Y= 0.000 Z= 3.550 | 7 J= 7, 8 SEC=1 NSEG=1 ANG=180
| 56 X= 7.225 Y= 0.000 Z= 4.050 | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| 57 X= 6.067 Y= 0.000 Z= 4.050 | 9 J= 9, 10 SEC=1 NSEG=2 ANG=180
| 58 X= 4.908 Y= 0.000 Z= 4.050 | 10 J= 10, 11 SEC=1 NSEG=1 ANG=180
| 59 X= 3.750 Y= 0.000 Z= 4.050 | 11 J= 11, 12 SEC=1 NSEG=4 ANG=180
| 60 X= 2.592 Y= 0.000 Z= 4.050 | 12 J= 12, 13 SEC=1 NSEG=1 ANG=180
| 61 X= 1.433 Y= 0.000 Z= 4.050 | 13 J= 13, 14 SEC=1 NSEG=2 ANG=180
| 62 X= 0.275 Y= 0.000 Z= 4.050 | 14 J= 14, 15 SEC=1 NSEG=1 ANG=180
| 63 X= -0.225 Y= 0.000 Z= 3.550 | 15 J= 15, 16 SEC=2 NSEG=1 ANG=0
| 64 X= -0.225 Y= 0.000 Z= 2.483 | 16 J= 16, 17 SEC=2 NSEG=1 ANG=0
| 65 X= -0.225 Y= 0.000 Z= 1.417 | 17 J= 17, 18 SEC=2 NSEG=1 ANG=0
| 66 X= -0.225 Y= 0.000 Z= 0.350 | 18 J= 18, 19 SEC=2 NSEG=2 ANG=0
19 J= 19, 20 SEC=2 NSEG=2 ANG=0
| RESTRAINT | 20 J= 20, 21 SEC=2 NSEG=1 ANG=0
| ADD=45 DOF=U1, U2, U3, R1, R2, R3 | 21 J= 21, 22 SEC=2 NSEG=1 ANG=0
| ADD=46 DOF=U1, U2, U3, R1, R2, R3 | 22 J= 22, 23 SEC=2 NSEG=1 ANG=0
| ADD=47 DOF=U1, U2, U3, R1, R2, R3 | 23 J= 23, 24 SEC=1 NSEG=1 ANG=0
| ADD=48 DOF=U1, U2, U3, R1, R2, R3 | 24 J= 24, 25 SEC=1 NSEG=2 ANG=0
| ADD=49 DOF=U1, U2, U3, R1, R2, R3 | 25 J= 25, 26 SEC=1 NSEG=1 ANG=0
| ADD=50 DOF=U1, U2, U3, R1, R2, R3 | 26 J= 26, 27 SEC=1 NSEG=4 ANG=0
| ADD=51 DOF=U1, U2, U3, R1, R2, R3 | 27 J= 27, 28 SEC=1 NSEG=1 ANG=0
| ADD=52 DOF=U1, U2, U3, R1, R2, R3 | 28 J= 28, 29 SEC=1 NSEG=2 ANG=0
| ADD=53 DOF=U1, U2, U3, R1, R2, R3 | 29 J= 29, 30 NSEG=1 ANG=0
| ADD=54 DOF=U1, U2, U3, R1, R2, R3 | 30 J= 30, 31 SEC=1 NSEG=1 ANG=0
| ADD=55 DOF=U1, U2, U3, R1, R2, R3 | 31 J= 31, 32 SEC=1 NSEG=2 ANG=0
| 32 J= 32, 33 SEC=1 NSEG=1 ANG=0 | ADD=34 RD=0,1 UX=5.9329,5.9329
| 33 J= 33, 34 SEC=1 NSEG=4 ANG=0 | ADD=35 RD=0,1 UX=5.9329,5.9329
| 34 J= 34, 35 SEC=1 NSEG=1 ANG=0 | ADD=36 RD=0,1 UX=5.9329,5.9329
| 35 J= 35, 36 SEC=1 NSEG=2 ANG=0 | NAME=SEWALL
| 36 J= 36, 37 SEC=1 NSEG=1 ANG=0 | TYPE=Distributed Span
| 37 J= 37, 38 SEC=2 NSEG=1 ANG=180 | ADD=15 RD=0,1 UX=0,3.5496
| 38 J= 38, 39 SEC=2 NSEG=1 ANG=180 | ADD=16 RD=0,1 UX=3.5496,8.3339
| 39 J= 39, 40 SEC=2 NSEG=1 ANG=180 | ADD=17 RD=0,1 UX=8.3339,10.5975
| 40 J= 40, 41 SEC=2 NSEG=2 ANG=180 | ADD=18 RD=0,1 UX=10.5975,15.5875
| 41 J= 41, 42 SEC=2 NSEG=2 ANG=180 | ADD=19 RD=0,1 UX=15.5875,20.3204
| 42 J= 42, 43 SEC=2 NSEG=1 ANG=180 | ADD=20 RD=0,1 UX=20.3204,22.3267
| 43 J= 43, 44 SEC=2 NSEG=1 ANG=180 | ADD=21 RD=0,1 UX=22.3267,26.2879
| 44 J= 44, 1 SEC=2 NSEG=1 ANG=180 | ADD=22 RD=0,1 UX=26.2879,29.0659
| 45 J= 30, 8 SEC=3 NSEG=4 ANG=0 | ADD=37 RD=0,1 UX=29.0659,26.2879
ADD=38 RD=0,1 UX=26.2879,22.3267
| NLLINK | ADD=39 RD=0,1 UX=22.3267,20.3204
| 1 J=1,45 NLP=SP1 ANG=0 | ADD=40 RD=0,1 UX=20.3204,15.5875
| 2 J=4,46 NLP=SP2 ANG=0 | ADD=41 RD=0,1 UX=15.5875,10.5975
| 3 J=5,47 NLP=SP2 ANG=0 | ADD=42 RD=0,1 UX=10.5975,8.3339
| 4 J=8,48 NLP=SP2 ANG=0 | ADD=43 RD=0,1 UX=8.3339,3.5496
| 5 J=11,49 NLP=SP2 ANG=0 | ADD=44 RD=0,1 UX=3.5496,0
| 6 J=12,50 NLP=SP2 ANG=0 | NAME=SEPRINSH
| 7 J=15,51 NLP=SP1 ANG=0 | TYPE=Distributed Span
| 8 J=15,52 NLP=SP3 ANG=180 | ADD=1 RD=0,1 UX=-3.81,-3.81
| 9 J=18,53 NLP=SP4 ANG=180 | ADD=2 RD=0,1 UX=-3.81,-3.81
| 10 J=20,54 NLP=SP4 ANG=180 | ADD=3 RD=0,1 UX=-3.81,-3.81
| 11 J=23,55 NLP=SP3 ANG=180 | ADD=4 RD=0,1 UX=-3.81,-3.81
| 12 J=23,56 NLP=SP1 ANG=0 | ADD=5 RD=0,1 UX=-3.81,-3.81
| 13 J=26,57 NLP=SP2 ANG=0 | ADD=6 RD=0,1 UX=-3.81,-3.81
| 14 J=27,58 NLP=SP2 ANG=0 | ADD=7 RD=0,1 UX=-3.81,-3.81
| 15 J=30,59 NLP=SP2 ANG=0 | ADD=8 RD=0,1 UX=-3.81,-3.81
| 16 J=33,60 NLP=SP2 ANG=0 | ADD=9 RD=0,1 UX=-3.81,-3.81
| 17 J=34,61 NLP=SP2 ANG=0 | ADD=10 RD=0,1 UX=-3.81,-3.81
| 18 J=37,62 NLP=SP1 ANG=0 | ADD=11 RD=0,1 UX=-3.81,-3.81
| 19 J=37,63 NLP=SP3 ANG=180 | ADD=12 RD=0,1 UX=-3.81,-3.81
| 20 J=40,64 NLP=SP4 ANG=180 | ADD=13 RD=0,1 UX=-3.81,-3.81
| 21 J=42,65 NLP=SP4 ANG=180 | ADD=14 RD=0,1 UX=-3.81,-3.81
| 22 J=1,66 NLP=SP3 ANG=180 | ADD=15 RD=0,1 UZ=3.33,3.33
ADD=16 RD=0,1 UZ=3.33,3.33
| LOAD | ADD=17 RD=0,1 UZ=3.33,3.33
| NAME=SELFWGT SW=1 | ADD=18 RD=0,1 UZ=3.33,3.33
| NAME=NWDEAD | ADD=19 RD=0,1 UZ=3.33,3.33
| TYPE=Distributed Span | ADD=20 RD=0,1 UZ=3.33,3.33
| ADD=23 RD=0,1 UZ=-152,-152 | ADD=21 RD=0,1 UZ=3.33,3.33
| ADD=24 RD=0,1 UZ=-152,-152 | ADD=22 RD=0,1 UZ=3.33,3.33
| ADD=25 RD=0,1 UZ=-152,-152 | ADD=23 RD=0,1 UX=2.85,2.85
| ADD=26 RD=0,1 UZ=-152,-152 | ADD=24 RD=0,1 UX=2.85,2.85
| ADD=27 RD=0,1 UZ=-152,-152 | ADD=25 RD=0,1 UX=2.85,2.85
| ADD=28 RD=0,1 UZ=-152,-152 | ADD=26 RD=0,1 UX=2.85,2.85
| ADD=29 RD=0,1 UZ=-152,-152 | ADD=27 RD=0,1 UX=2.85,2.85
| ADD=30 RD=0,1 UZ=-152,-152 | ADD=28 RD=0,1 UX=2.85,2.85
| ADD=31 RD=0,1 UZ=-152,-152 | ADD=29 RD=0,1 UX=2.85,2.85
| ADD=32 RD=0,1 UZ=-152,-152 | ADD=30 RD=0,1 UX=2.85,2.85
| ADD=33 RD=0,1 UZ=-152,-152 | ADD=31 RD=0,1 UX=2.85,2.85
| ADD=34 RD=0,1 UZ=-152,-152 | ADD=32 RD=0,1 UX=2.85,2.85
| ADD=35 RD=0,1 UZ=-152,-152 | ADD=33 RD=0,1 UX=2.85,2.85
| ADD=36 RD=0,1 UZ=-152,-152 | ADD=34 RD=0,1 UX=2.85,2.85
| NAME=LIVEFULL | ADD=35 RD=0,1 UX=2.85,2.85
| TYPE=Distributed Span | ADD=36 RD=0,1 UX=2.85,2.85
| ADD=23 RD=0,1 UZ=-10,-10 | ADD=37 RD=0,1 UZ=-3.33,-3.33
| ADD=24 RD=0,1 UZ=-10,-10 | ADD=38 RD=0,1 UZ=-3.33,-3.33
| ADD=25 RD=0,1 UZ=-10,-10 | ADD=39 RD=0,1 UZ=-3.33,-3.33
| ADD=26 RD=0,1 UZ=-10,-10 | ADD=40 RD=0,1 UZ=-3.33,-3.33
| ADD=27 RD=0,1 UZ=-10,-10 | ADD=41 RD=0,1 UZ=-3.33,-3.33
| ADD=28 RD=0,1 UZ=-10,-10 | ADD=42 RD=0,1 UZ=-3.33,-3.33
| ADD=29 RD=0,1 UZ=-10,-10 | ADD=43 RD=0,1 UZ=-3.33,-3.33
| ADD=30 RD=0,1 UZ=-10,-10 | ADD=44 RD=0,1 UZ=-3.33,-3.33
| ADD=31 RD=0,1 UZ=-10,-10 | NAME=SEINER
| ADD=32 RD=0,1 UZ=-10,-10 | TYPE=Distributed Span
| ADD=33 RD=0,1 UZ=-10,-10 | ADD=1 RD=0,1 UX=2.2686,2.2686
| ADD=34 RD=0,1 UZ=-10,-10 | ADD=2 RD=0,1 UX=2.2686,2.2686
| ADD=35 RD=0,1 UZ=-10,-10 | ADD=3 RD=0,1 UX=2.2686,2.2686
| ADD=36 RD=0,1 UZ=-10,-10 | ADD=4 RD=0,1 UX=2.2686,2.2686
| NAME=SEUPSLAB | ADD=5 RD=0,1 UX=2.2686,2.2686
| TYPE=Distributed Span | ADD=6 RD=0,1 UX=2.2686,2.2686
| ADD=23 RD=0,1 UX=5.9329,5.9329 | ADD=7 RD=0,1 UX=2.2686,2.2686
| ADD=24 RD=0,1 UX=5.9329,5.9329 | ADD=8 RD=0,1 UX=2.2686,2.2686
| ADD=25 RD=0,1 UX=5.9329,5.9329 | ADD=9 RD=0,1 UX=2.2686,2.2686
| ADD=26 RD=0,1 UX=5.9329,5.9329 | ADD=10 RD=0,1 UX=2.2686,2.2686
| ADD=27 RD=0,1 UX=5.9329,5.9329 | ADD=11 RD=0,1 UX=2.2686,2.2686
| ADD=28 RD=0,1 UX=5.9329,5.9329 | ADD=12 RD=0,1 UX=2.2686,2.2686
| ADD=29 RD=0,1 UX=5.9329,5.9329 | ADD=13 RD=0,1 UX=2.2686,2.2686
| ADD=30 RD=0,1 UX=5.9329,5.9329 | ADD=14 RD=0,1 UX=2.2686,2.2686
| ADD=31 RD=0,1 UX=5.9329,5.9329 | ADD=15 RD=0,1 UX=1.78247,1.79379
| ADD=32 RD=0,1 UX=5.9329,5.9329 | ADD=16 RD=0,1 UX=1.79379,1.80932
| ADD=33 RD=0,1 UX=5.9329,5.9329 | ADD=17 RD=0,1 UX=1.80932,1.81698
ADD=18 RD=0,1 UX=1.81698,1.83422
ADD=19 RD=0,1 UX=1.83422,1.85145
ADD=20 RD=0,1 UX=1.85145,1.85912
ADD=21 RD=0,1 UX=1.85912,1.87464
ADD=22 RD=0,1 UX=1.87464,1.88596
ADD=23 RD=0,1 UX=2.40031,2.40031
ADD=24 RD=0,1 UX=2.40031,2.40031
ADD=25 RD=0,1 UX=2.40031,2.40031
ADD=26 RD=0,1 UX=2.40031,2.40031
ADD=27 RD=0,1 UX=2.40031,2.40031
ADD=28 RD=0,1 UX=2.40031,2.40031
ADD=29 RD=0,1 UX=2.40031,2.40031
ADD=30 RD=0,1 UX=2.40031,2.40031
ADD=31 RD=0,1 UX=2.40031,2.40031
ADD=32 RD=0,1 UX=2.40031,2.40031
ADD=33 RD=0,1 UX=2.40031,2.40031
ADD=34 RD=0,1 UX=2.40031,2.40031
ADD=35 RD=0,1 UX=2.40031,2.40031
ADD=36 RD=0,1 UX=2.40031,2.40031
ADD=37 RD=0,1 UX=1.88596,1.87464
ADD=38 RD=0,1 UX=1.87464,1.85912
ADD=39 RD=0,1 UX=1.85912,1.85145
ADD=40 RD=0,1 UX=1.85145,1.83422
ADD=41 RD=0,1 UX=1.83422,1.81698
ADD=42 RD=0,1 UX=1.81698,1.80932
ADD=43 RD=0,1 UX=1.80932,1.79379
ADD=44 RD=0,1 UX=1.79379,1.78247
ADD=45 RD=0,1 UX=1.37161,1.29634
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=SEUPSLAB
LOAD=SEWALL
LOAD=SEPRINSH
LOAD=SEINER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=1 AT=1
LOAD=SEWALL SF=1 AT=1
LOAD=SEPRINSH SF=1 AT=1
LOAD=SEINER SF=1 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=0.875 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=-1 AT=1
LOAD=SEWALL SF=-1 AT=1
LOAD=SEPRINSH SF=-1 AT=1
LOAD=SEINER SF=-1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 15 | ULTIMATE MIN | 0 | -470.3956 | -252.8142 | -140.5018
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 15 | ULTIMATE MIN | 1 | -464.7361 | -189.4992 | -63.1886
| 1 | ULTIMATE MIN | 0 | -252.8142 | -239.6567 | -140.5018 | 16 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 1 | ULTIMATE MIN | 1 | -252.8142 | -245.3162 | -73.913 | 16 | ULTIMATE MAX | 1 | 0 | 0 | 12.7717
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 16 | ULTIMATE MIN | 0 | -464.7361 | -189.4992 | -63.1886
| 2 | ULTIMATE MAX | 0.5 | 0 | 0 | 44.3696 | 16 | ULTIMATE MIN | 1 | -456.9745 | -105.695 | -20.334
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 117.893 | 17 | ULTIMATE MAX | 0 | 0 | 0 | 12.7717
| 2 | ULTIMATE MIN | 0 | -252.8142 | -245.3162 | -73.913 | 17 | ULTIMATE MAX | 0.25 | 0 | 0 | 40.9378
| 2 | ULTIMATE MIN | 0.5 | -252.8142 | -251.7989 | -2.1736 | 17 | ULTIMATE MAX | 0.5 | 0 | 21.538 | 44.6332
| 2 | ULTIMATE MIN | 1 | -252.8142 | -258.2816 | 0 | 17 | ULTIMATE MAX | 0.75 | 0 | 81.7189 | 24.7253
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 117.893 | 17 | ULTIMATE MAX | 1 | 0 | 139.6468 | 0
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 178.4239 | 17 | ULTIMATE MIN | 0 | -456.9745 | -105.695 | -20.334
| 3 | ULTIMATE MIN | 0 | -252.8142 | -258.2816 | 0 | 17 | ULTIMATE MIN | 0.25 | -450.7491 | -41.0081 | -9.2724
| 3 | ULTIMATE MIN | 1 | -252.8142 | -263.4883 | 0 | 17 | ULTIMATE MIN | 0.5 | -444.5236 | 0 | -10.4462
| 4 | ULTIMATE MAX | 0 | 0 | 68.2546 | 178.4239 | 17 | ULTIMATE MIN | 0.75 | -438.2982 | 0 | -23.4217
| 4 | ULTIMATE MAX | 0.25 | 0 | 62.2916 | 159.511 | 17 | ULTIMATE MIN | 1 | -432.0727 | 0 | -47.7651
| 4 | ULTIMATE MAX | 0.5 | 0 | 56.3285 | 142.3259 | 18 | ULTIMATE MAX | 0 | 0 | 139.6445 | 0
| 4 | ULTIMATE MAX | 0.75 | 0 | 50.3655 | 126.8686 | 18 | ULTIMATE MAX | 1 | 0 | 208.7107 | 0
| 4 | ULTIMATE MAX | 1 | 0 | 44.4024 | 113.1391 | 18 | ULTIMATE MIN | 0 | -432.0727 | 0 | -47.7651
| 4 | ULTIMATE MIN | 0 | -252.8142 | 0 | 0 | 18 | ULTIMATE MIN | 1 | -424.3111 | 0 | -107.1238
| 4 | ULTIMATE MIN | 0.25 | -252.8142 | 0 | 0 | 19 | ULTIMATE MAX | 0 | 0 | 208.7103 | 0
| 4 | ULTIMATE MIN | 0.5 | -252.8142 | 0 | 0 | 19 | ULTIMATE MAX | 1 | 0 | 256.8633 | 0
| 4 | ULTIMATE MIN | 0.75 | -252.8142 | 0 | 0 | 19 | ULTIMATE MIN | 0 | -424.3111 | 0 | -107.1238
| 4 | ULTIMATE MIN | 1 | -252.8142 | 0 | 0 | 19 | ULTIMATE MIN | 1 | -418.6516 | 0 | -188.6525
| 5 | ULTIMATE MAX | 0 | 0 | 355.1973 | 113.1391 | 20 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 1 | 0 | 348.4471 | 1.9378 | 20 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 5 | ULTIMATE MIN | 0 | -252.8142 | 0 | 0 | 20 | ULTIMATE MIN | 0 | -256.8631 | -418.6516 | -188.6525
| 5 | ULTIMATE MIN | 1 | -252.8142 | 0 | -2.2654 | 20 | ULTIMATE MIN | 1 | -256.8631 | -350.0721 | -85.0438
| 6 | ULTIMATE MAX | 0 | 0 | 348.4471 | 1.9378 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 6 | ULTIMATE MAX | 0.5 | 0 | 341.9644 | 0 | 21 | ULTIMATE MAX | 0.5 | 0 | 0 | 54.0994
| 6 | ULTIMATE MAX | 1 | 0 | 335.4817 | 0 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 120.5132
| 6 | ULTIMATE MIN | 0 | -252.8142 | 0 | -2.2654 | 21 | ULTIMATE MIN | 0 | -256.8627 | -350.0721 | -85.0438
| 6 | ULTIMATE MIN | 0.5 | -252.8142 | 0 | -110.9983 | 21 | ULTIMATE MIN | 0.5 | -256.8627 | -271.5174 | 0
| 6 | ULTIMATE MIN | 1 | -252.8142 | 0 | -217.6961 | 21 | ULTIMATE MIN | 1 | -256.8627 | -192.9627 | 0
| 7 | ULTIMATE MAX | 0 | 0 | 335.4817 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 120.5132
| 7 | ULTIMATE MAX | 1 | 0 | 331.3657 | 0 | 22 | ULTIMATE MAX | 0.5 | 0 | 0 | 171.5474
| 7 | ULTIMATE MIN | 0 | -252.8142 | 0 | -217.6961 | 22 | ULTIMATE MAX | 1 | 0 | 45.4004 | 175.3927
| 7 | ULTIMATE MIN | 1 | -252.8142 | 0 | -284.3808 | 22 | ULTIMATE MIN | 0 | -256.8623 | -192.9638 | 0
| 8 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 22 | ULTIMATE MIN | 0.5 | -256.8623 | -84.4835 | 0
| 8 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 22 | ULTIMATE MIN | 1 | -256.8623 | 0 | 0
| 8 | ULTIMATE MIN | 0 | -252.8142 | -331.3657 | -284.3808 | 23 | ULTIMATE MAX | 0 | 0 | 45.4004 | 175.3927
| 8 | ULTIMATE MIN | 1 | -252.8142 | -335.4817 | -217.6961 | 23 | ULTIMATE MAX | 0.5 | 0 | 153.8807 | 132.049
| 9 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 262.361 | 46.3497
| 9 | ULTIMATE MAX | 0.5 | 0 | 0 | 0 | 23 | ULTIMATE MIN | 0 | -256.862 | 0 | 0
| 9 | ULTIMATE MAX | 1 | 0 | 0 | 1.9378 | 23 | ULTIMATE MIN | 0.5 | -256.862 | 0 | 0
| 9 | ULTIMATE MIN | 0 | -252.8142 | -335.4817 | -217.6961 | 23 | ULTIMATE MIN | 1 | -256.862 | 0 | 0
| 9 | ULTIMATE MIN | 0.5 | -252.8142 | -341.9644 | -110.9983 | 24 | ULTIMATE MAX | 0 | 0 | 262.361 | 46.3497
| 9 | ULTIMATE MIN | 1 | -252.8142 | -348.4471 | -2.2653 | 24 | ULTIMATE MAX | 0.5 | 0 | 340.9157 | 0
| 10 | ULTIMATE MAX | 0 | 0 | 0 | 1.9378 | 24 | ULTIMATE MAX | 1 | 0 | 419.4704 | 0
| 10 | ULTIMATE MAX | 1 | 0 | 0 | 113.1391 | 24 | ULTIMATE MIN | 0 | -256.8619 | 0 | 0
| 10 | ULTIMATE MIN | 0 | -252.8142 | -348.4471 | -2.2653 | 24 | ULTIMATE MIN | 0.5 | -256.8619 | 0 | -53.4996
| 10 | ULTIMATE MIN | 1 | -252.8142 | -355.1973 | 0 | 24 | ULTIMATE MIN | 1 | -256.8619 | 0 | -173.2604
| 11 | ULTIMATE MAX | 0 | 0 | 0 | 113.1391 | 25 | ULTIMATE MAX | 0 | 0 | 419.4704 | 0
| 11 | ULTIMATE MAX | 0.25 | 0 | 0 | 126.8686 | 25 | ULTIMATE MAX | 1 | 0 | 469.3464 | 0
| 11 | ULTIMATE MAX | 0.5 | 0 | 0 | 142.3259 | 25 | ULTIMATE MIN | 0 | -256.8618 | 0 | -173.2604
| 11 | ULTIMATE MAX | 0.75 | 0 | 0 | 159.511 | 25 | ULTIMATE MIN | 1 | -256.8618 | 0 | -262.1421
| 11 | ULTIMATE MAX | 1 | 0 | 0 | 178.4239 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MIN | 0 | -252.8142 | -44.4024 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 11 | ULTIMATE MIN | 0.25 | -252.8142 | -50.3655 | 0 | 26 | ULTIMATE MIN | 0 | -256.862 | -469.3464 | -262.1421
| 11 | ULTIMATE MIN | 0.5 | -252.8142 | -56.3285 | 0 | 26 | ULTIMATE MIN | 1 | -256.862 | -419.4704 | -173.2604
| 11 | ULTIMATE MIN | 0.75 | -252.8142 | -62.2916 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MIN | 1 | -252.8142 | -68.2546 | 0 | 27 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 12 | ULTIMATE MAX | 0 | 0 | 263.4883 | 178.4239 | 27 | ULTIMATE MAX | 1 | 0 | 0 | 46.3496
| 12 | ULTIMATE MAX | 1 | 0 | 258.2816 | 117.893 | 27 | ULTIMATE MIN | 0 | -256.862 | -419.4704 | -173.2604
| 12 | ULTIMATE MIN | 0 | -252.8142 | 0 | 0 | 27 | ULTIMATE MIN | 0.5 | -256.862 | -340.9157 | -53.4996
| 12 | ULTIMATE MIN | 1 | -252.8142 | 0 | 0 | 27 | ULTIMATE MIN | 1 | -256.862 | -262.361 | 0
| 13 | ULTIMATE MAX | 0 | 0 | 258.2816 | 117.893 | 28 | ULTIMATE MAX | 0 | 0 | 0 | 46.3496
| 13 | ULTIMATE MAX | 0.5 | 0 | 251.7989 | 44.3696 | 28 | ULTIMATE MAX | 0.5 | 0 | 0 | 132.049
| 13 | ULTIMATE MAX | 1 | 0 | 245.3162 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 0 | 175.3927
| 13 | ULTIMATE MIN | 0 | -252.8142 | 0 | 0 | 28 | ULTIMATE MIN | 0 | -256.862 | -262.361 | 0
| 13 | ULTIMATE MIN | 0.5 | -252.8142 | 0 | -2.1727 | 28 | ULTIMATE MIN | 0.5 | -256.862 | -153.8807 | 0
| 13 | ULTIMATE MIN | 1 | -252.8142 | 0 | -73.913 | 28 | ULTIMATE MIN | 1 | -256.862 | -45.4004 | 0
| 14 | ULTIMATE MAX | 0 | 0 | 245.3162 | 0 | 29 | ULTIMATE MAX | 0 | 0 | 0 | 175.3927
| 14 | ULTIMATE MAX | 1 | 0 | 239.6567 | 0 | 29 | ULTIMATE MAX | 0.5 | 0 | 84.4832 | 171.5474
| 14 | ULTIMATE MIN | 0 | -252.8142 | 0 | -73.913 | 29 | ULTIMATE MAX | 1 | 0 | 192.9635 | 120.5132
| 14 | ULTIMATE MIN | 1 | -252.8142 | 0 | -140.5018 | 29 | ULTIMATE MIN | 0 | -256.8622 | -45.4004 | 0
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 29 | ULTIMATE MIN | 0.5 | -256.8622 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 29 | ULTIMATE MIN | 1 | -256.8622 | 0 | 0
| FRAME | LOAD | DIST | P | V2 | M3
| 30 | ULTIMATE MAX | 0 | 0 | 192.9627 | 120.5132
| 30 | ULTIMATE MAX | 0.5 | 0 | 271.5174 | 54.0994
| 30 | ULTIMATE MAX | 1 | 0 | 350.0721 | 0
| 30 | ULTIMATE MIN | 0 | -256.8626 | 0 | 0
| 30 | ULTIMATE MIN | 0.5 | -256.8626 | 0 | 0
| 30 | ULTIMATE MIN | 1 | -256.8626 | 0 | -85.0431
| 31 | ULTIMATE MAX | 0 | 0 | 350.0721 | 0
| 31 | ULTIMATE MAX | 1 | 0 | 418.6516 | 0
| 31 | ULTIMATE MIN | 0 | -256.8629 | 0 | -85.0431
| 31 | ULTIMATE MIN | 1 | -256.8629 | 0 | -188.6525
| 32 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 32 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 32 | ULTIMATE MIN | 0 | -418.6516 | -256.863 | -188.6525
| 32 | ULTIMATE MIN | 1 | -424.3111 | -208.71 | -107.1238
| 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 33 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 33 | ULTIMATE MIN | 0 | -424.3111 | -208.7104 | -107.1238
| 33 | ULTIMATE MIN | 1 | -432.0727 | -139.6442 | -47.7651
| 34 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 34 | ULTIMATE MAX | 0.25 | 0 | 0 | 24.7256
| 34 | ULTIMATE MAX | 0.5 | 0 | 0 | 44.6334
| 34 | ULTIMATE MAX | 0.75 | 0 | 41.0081 | 40.9378
| 34 | ULTIMATE MAX | 1 | 0 | 105.695 | 12.7715
| 34 | ULTIMATE MIN | 0 | -432.0727 | -139.6463 | -47.7651
| 34 | ULTIMATE MIN | 0.25 | -438.2982 | -81.7185 | -23.4217
| 34 | ULTIMATE MIN | 0.5 | -444.5236 | -21.5376 | -10.4462
| 34 | ULTIMATE MIN | 0.75 | -450.7491 | 0 | -9.2724
| 34 | ULTIMATE MIN | 1 | -456.9745 | 0 | -20.334
| 35 | ULTIMATE MAX | 0 | 0 | 105.695 | 12.7715
| 35 | ULTIMATE MAX | 1 | 0 | 189.4992 | 0
| 35 | ULTIMATE MIN | 0 | -456.9745 | 0 | -20.334
| 35 | ULTIMATE MIN | 1 | -464.7361 | 0 | -63.1886
| 36 | ULTIMATE MAX | 0 | 0 | 189.4992 | 0
| 36 | ULTIMATE MAX | 1 | 0 | 252.8142 | 0
| 36 | ULTIMATE MIN | 0 | -464.7361 | 0 | -63.1886
| 36 | ULTIMATE MIN | 1 | -470.3956 | 0 | -140.5018
| 37 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0.25 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0.5 | 0 | 0 | 6e-06
| 37 | ULTIMATE MAX | 0.75 | 0 | 0 | 0.00017
| 37 | ULTIMATE MAX | 1 | 0 | 0 | 0.000334
| 37 | ULTIMATE MIN | 0 | -938.6928 | -0.000205 | -0.000321
| 37 | ULTIMATE MIN | 0.25 | -948.1008 | -0.000205 | -0.000157
| 37 | ULTIMATE MIN | 0.5 | -957.5088 | -0.000205 | 0
| 37 | ULTIMATE MIN | 0.75 | -966.9168 | -0.000205 | 0
| 37 | ULTIMATE MIN | 1 | -976.3248 | -0.000205 | 0
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 16 | SERVICE MAX | 1 | 0 | 0 | 4.078
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 16 | SERVICE MIN | 0 | -305.1234 | -120.4291 | -42.2709
| 1 | SERVICE MIN | 0 | -160.001 | -155.3812 | -90.9901 | 16 | SERVICE MIN | 1 | -298.6554 | -68.0515 | -14.9404
| 1 | SERVICE MIN | 1 | -160.001 | -160.0975 | -48.7777 | 17 | SERVICE MAX | 0 | 0 | 0 | 4.078
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 17 | SERVICE MAX | 0.25 | 0 | 0 | 22.4486
| 2 | SERVICE MAX | 0.5 | 0 | 0 | 28.6023 | 17 | SERVICE MAX | 0.5 | 0 | 12.3232 | 25.525
| 2 | SERVICE MAX | 1 | 0 | 0 | 77.3267 | 17 | SERVICE MAX | 0.75 | 0 | 49.9363 | 13.8492
| 2 | SERVICE MIN | 0 | -160.001 | -160.0975 | -48.7777 | 17 | SERVICE MAX | 1 | 0 | 86.1412 | 0
| 2 | SERVICE MIN | 0.5 | -160.001 | -165.4997 | 0 | 17 | SERVICE MIN | 0 | -298.6554 | -68.0515 | -14.9404
| 2 | SERVICE MIN | 1 | -160.001 | -170.902 | 0 | 17 | SERVICE MIN | 0.25 | -293.4675 | -27.6222 | -7.5886
| 3 | SERVICE MAX | 0 | 0 | 0 | 77.3267 | 17 | SERVICE MIN | 0.5 | -288.2796 | 0 | -7.884
| 3 | SERVICE MAX | 1 | 0 | 0 | 117.6931 | 17 | SERVICE MIN | 0.75 | -283.0918 | 0 | -15.5554
| 3 | SERVICE MIN | 0 | -160.001 | -170.902 | 0 | 17 | SERVICE MIN | 1 | -277.9039 | 0 | -30.3317
| 3 | SERVICE MIN | 1 | -160.001 | -175.2409 | 0 | 18 | SERVICE MAX | 0 | 0 | 86.1398 | 0
| 4 | SERVICE MAX | 0 | 0 | 45.8189 | 117.6931 | 18 | SERVICE MAX | 1 | 0 | 129.3062 | 0
| 4 | SERVICE MAX | 0.25 | 0 | 40.8497 | 105.137 | 18 | SERVICE MIN | 0 | -277.9039 | 0 | -30.3317
| 4 | SERVICE MAX | 0.5 | 0 | 35.8805 | 94.0207 | 18 | SERVICE MIN | 1 | -271.4359 | 0 | -66.8845
| 4 | SERVICE MAX | 0.75 | 0 | 30.9113 | 84.3442 | 19 | SERVICE MAX | 0 | 0 | 129.3059 | 0
| 4 | SERVICE MAX | 1 | 0 | 25.9421 | 76.1076 | 19 | SERVICE MAX | 1 | 0 | 159.4015 | 0
| 4 | SERVICE MIN | 0 | -160.001 | 0 | 0 | 19 | SERVICE MIN | 0 | -271.4359 | 0 | -66.8845
| 4 | SERVICE MIN | 0.25 | -160.001 | 0 | 0 | 19 | SERVICE MIN | 1 | -266.7196 | 0 | -117.4416
| 4 | SERVICE MIN | 0.5 | -160.001 | 0 | 0 | 20 | SERVICE MAX | 0 | 0 | 0 | 0
| 4 | SERVICE MIN | 0.75 | -160.001 | 0 | 0 | 20 | SERVICE MAX | 1 | 0 | 0 | 0
| 4 | SERVICE MIN | 1 | -160.001 | 0 | 0 | 20 | SERVICE MIN | 0 | -159.4014 | -266.7196 | -117.4416
| 5 | SERVICE MAX | 0 | 0 | 233.8587 | 76.1076 | 20 | SERVICE MIN | 1 | -159.4014 | -222.6784 | -50.1846
| 5 | SERVICE MAX | 1 | 0 | 228.2335 | 3.5936 | 21 | SERVICE MAX | 0 | 0 | 0 | 0
| 5 | SERVICE MIN | 0 | -160.001 | 0 | 0 | 21 | SERVICE MAX | 0.5 | 0 | 0 | 36.5189
| 5 | SERVICE MIN | 1 | -160.001 | 0 | 0 | 21 | SERVICE MAX | 1 | 0 | 0 | 78.6127
| 6 | SERVICE MAX | 0 | 0 | 228.2335 | 3.5936 | 21 | SERVICE MIN | 0 | -159.4012 | -222.6784 | -50.1846
| 6 | SERVICE MAX | 0.5 | 0 | 222.8312 | 0 | 21 | SERVICE MIN | 0.5 | -159.4012 | -172.2311 | 0
| 6 | SERVICE MAX | 1 | 0 | 217.429 | 0 | 21 | SERVICE MIN | 1 | -159.4012 | -121.7839 | 0
| 6 | SERVICE MIN | 0 | -160.001 | 0 | 0 | 22 | SERVICE MAX | 0 | 0 | 0 | 78.6127
| 6 | SERVICE MIN | 0.5 | -160.001 | 0 | -70.7182 | 22 | SERVICE MAX | 0.5 | 0 | 0 | 110.6177
| 6 | SERVICE MIN | 1 | -160.001 | 0 | -140.0592 | 22 | SERVICE MAX | 1 | 0 | 30.9232 | 112.3183
| 7 | SERVICE MAX | 0 | 0 | 217.429 | 0 | 22 | SERVICE MIN | 0 | -159.4009 | -121.7848 | 0
| 7 | SERVICE MAX | 1 | 0 | 213.999 | 0 | 22 | SERVICE MIN | 0.5 | -159.4009 | -52.1195 | 0
| 7 | SERVICE MIN | 0 | -160.001 | 0 | -140.0592 | 22 | SERVICE MIN | 1 | -159.4009 | 0 | 0
| 7 | SERVICE MIN | 1 | -160.001 | 0 | -183.202 | 23 | SERVICE MAX | 0 | 0 | 30.9232 | 112.3183
| 8 | SERVICE MAX | 0 | 0 | 0 | 0 | 23 | SERVICE MAX | 0.5 | 0 | 100.5884 | 83.7145
| 8 | SERVICE MAX | 1 | 0 | 0 | 0 | 23 | SERVICE MAX | 1 | 0 | 170.2537 | 27.8274
| 8 | SERVICE MIN | 0 | -160.001 | -213.999 | -183.202 | 23 | SERVICE MIN | 0 | -159.4007 | 0 | 0
| 8 | SERVICE MIN | 1 | -160.001 | -217.429 | -140.0592 | 23 | SERVICE MIN | 0.5 | -159.4007 | 0 | 0
| 9 | SERVICE MAX | 0 | 0 | 0 | 0 | 23 | SERVICE MIN | 1 | -159.4007 | 0 | 0
| 9 | SERVICE MAX | 0.5 | 0 | 0 | 0 | 24 | SERVICE MAX | 0 | 0 | 170.2537 | 27.8274
| 9 | SERVICE MAX | 1 | 0 | 0 | 3.5936 | 24 | SERVICE MAX | 0.5 | 0 | 220.7009 | 0
| 9 | SERVICE MIN | 0 | -160.001 | -217.429 | -140.0592 | 24 | SERVICE MAX | 1 | 0 | 271.1482 | 0
| 9 | SERVICE MIN | 0.5 | -160.001 | -222.8312 | -70.7182 | 24 | SERVICE MIN | 0 | -159.4006 | 0 | 0
| 9 | SERVICE MIN | 1 | -160.001 | -228.2335 | 0 | 24 | SERVICE MIN | 0.5 | -159.4006 | 0 | -36.769
| 10 | SERVICE MAX | 0 | 0 | 0 | 3.5936 | 24 | SERVICE MIN | 1 | -159.4006 | 0 | -114.2352
| 10 | SERVICE MAX | 1 | 0 | 0 | 76.1076 | 25 | SERVICE MAX | 0 | 0 | 271.1482 | 0
| 10 | SERVICE MIN | 0 | -160.001 | -228.2335 | 0 | 25 | SERVICE MAX | 1 | 0 | 303.1782 | 0
| 10 | SERVICE MIN | 1 | -160.001 | -233.8587 | 0 | 25 | SERVICE MIN | 0 | -159.4006 | 0 | -114.2352
| 11 | SERVICE MAX | 0 | 0 | 0 | 76.1076 | 25 | SERVICE MIN | 1 | -159.4006 | 0 | -171.6679
| 11 | SERVICE MAX | 0.25 | 0 | 0 | 84.3442 | 26 | SERVICE MAX | 0 | 0 | 0 | 0
| 11 | SERVICE MAX | 0.5 | 0 | 0 | 94.0207 | 26 | SERVICE MAX | 1 | 0 | 0 | 0
| 11 | SERVICE MAX | 0.75 | 0 | 0 | 105.137 | 26 | SERVICE MIN | 0 | -159.4007 | -303.1782 | -171.6679
| 11 | SERVICE MAX | 1 | 0 | 0 | 117.6931 | 26 | SERVICE MIN | 1 | -159.4007 | -271.1482 | -114.2352
| 11 | SERVICE MIN | 0 | -160.001 | -25.9421 | 0 | 27 | SERVICE MAX | 0 | 0 | 0 | 0
| 11 | SERVICE MIN | 0.25 | -160.001 | -30.9113 | 0 | 27 | SERVICE MAX | 0.5 | 0 | 0 | 0
| 11 | SERVICE MIN | 0.5 | -160.001 | -35.8805 | 0 | 27 | SERVICE MAX | 1 | 0 | 0 | 27.8273
| 11 | SERVICE MIN | 0.75 | -160.001 | -40.8497 | 0 | 27 | SERVICE MIN | 0 | -159.4007 | -271.1482 | -114.2352
| 11 | SERVICE MIN | 1 | -160.001 | -45.8189 | 0 | 27 | SERVICE MIN | 0.5 | -159.4007 | -220.7009 | -36.769
| 12 | SERVICE MAX | 0 | 0 | 175.2409 | 117.6931 | 27 | SERVICE MIN | 1 | -159.4007 | -170.2537 | 0
| 12 | SERVICE MAX | 1 | 0 | 170.902 | 77.3267 | 28 | SERVICE MAX | 0 | 0 | 0 | 27.8273
| 12 | SERVICE MIN | 0 | -160.001 | 0 | 0 | 28 | SERVICE MAX | 0.5 | 0 | 0 | 83.7145
| 12 | SERVICE MIN | 1 | -160.001 | 0 | 0 | 28 | SERVICE MAX | 1 | 0 | 0 | 112.3183
| 13 | SERVICE MAX | 0 | 0 | 170.902 | 77.3267 | 28 | SERVICE MIN | 0 | -159.4007 | -170.2537 | 0
| 13 | SERVICE MAX | 0.5 | 0 | 165.4997 | 28.6023 | 28 | SERVICE MIN | 0.5 | -159.4007 | -100.5884 | 0
| 13 | SERVICE MAX | 1 | 0 | 160.0975 | 0 | 28 | SERVICE MIN | 1 | -159.4007 | -30.9232 | 0
| 13 | SERVICE MIN | 0 | -160.001 | 0 | 0 | 29 | SERVICE MAX | 0 | 0 | 0 | 112.3183
| 13 | SERVICE MIN | 0.5 | -160.001 | 0 | 0 | 29 | SERVICE MAX | 0.5 | 0 | 52.1193 | 110.6177
| 13 | SERVICE MIN | 1 | -160.001 | 0 | -48.7777 | 29 | SERVICE MAX | 1 | 0 | 121.7846 | 78.6127
| 14 | SERVICE MAX | 0 | 0 | 160.0975 | 0 | 29 | SERVICE MIN | 0 | -159.4009 | -30.9232 | 0
| 14 | SERVICE MAX | 1 | 0 | 155.3812 | 0 | 29 | SERVICE MIN | 0.5 | -159.4009 | 0 | 0
| 14 | SERVICE MIN | 0 | -160.001 | 0 | -48.7777 | 29 | SERVICE MIN | 1 | -159.4009 | 0 | 0
| 14 | SERVICE MIN | 1 | -160.001 | 0 | -90.9901 | 30 | SERVICE MAX | 0 | 0 | 121.7839 | 78.6127
| 15 | SERVICE MAX | 0 | 0 | 0 | 0 | 30 | SERVICE MAX | 0.5 | 0 | 172.2311 | 36.5189
| 15 | SERVICE MAX | 1 | 0 | 0 | 0 | 30 | SERVICE MAX | 1 | 0 | 222.6784 | 0
| 15 | SERVICE MIN | 0 | -309.8396 | -160.001 | -90.9901 | 30 | SERVICE MIN | 0 | -159.4011 | 0 | 0
| 15 | SERVICE MIN | 1 | -305.1234 | -120.4291 | -42.2709 | 30 | SERVICE MIN | 0.5 | -159.4011 | 0 | 0
| 16 | SERVICE MAX | 0 | 0 | 0 | 0 | 30 | SERVICE MIN | 1 | -159.4011 | 0 | -50.1842
| FRAME | LOAD | DIST | P | V2 | M3
| 31 | SERVICE MAX | 0 | 0 | 222.6784 | 0
| 31 | SERVICE MAX | 1 | 0 | 266.7196 | 0
| 31 | SERVICE MIN | 0 | -159.4012 | 0 | -50.1842
| 31 | SERVICE MIN | 1 | -159.4012 | 0 | -117.4415
| 32 | SERVICE MAX | 0 | 0 | 0 | 0
| 32 | SERVICE MAX | 1 | 0 | 0 | 0
| 32 | SERVICE MIN | 0 | -266.7196 | -159.4014 | -117.4415
| 32 | SERVICE MIN | 1 | -271.4359 | -129.3057 | -66.8845
| 33 | SERVICE MAX | 0 | 0 | 0 | 0
| 33 | SERVICE MAX | 1 | 0 | 0 | 0
| 33 | SERVICE MIN | 0 | -271.4359 | -129.306 | -66.8845
| 33 | SERVICE MIN | 1 | -277.9039 | -86.1396 | -30.3317
| 34 | SERVICE MAX | 0 | 0 | 0 | 0
| 34 | SERVICE MAX | 0.25 | 0 | 0 | 13.8494
| 34 | SERVICE MAX | 0.5 | 0 | 0 | 25.525
| 34 | SERVICE MAX | 0.75 | 0 | 27.6222 | 22.4485
| 34 | SERVICE MAX | 1 | 0 | 68.0515 | 4.0778
| 34 | SERVICE MIN | 0 | -277.9039 | -86.1409 | -30.3317
| 34 | SERVICE MIN | 0.25 | -283.0918 | -49.936 | -15.5554
| 34 | SERVICE MIN | 0.5 | -288.2796 | -12.3229 | -7.884
| 34 | SERVICE MIN | 0.75 | -293.4675 | 0 | -7.5886
| 34 | SERVICE MIN | 1 | -298.6554 | 0 | -14.9404
| 35 | SERVICE MAX | 0 | 0 | 68.0515 | 4.0778
| 35 | SERVICE MAX | 1 | 0 | 120.4291 | 0
| 35 | SERVICE MIN | 0 | -298.6554 | 0 | -14.9404
| 35 | SERVICE MIN | 1 | -305.1234 | 0 | -42.2709
| 36 | SERVICE MAX | 0 | 0 | 120.4291 | 0
| 36 | SERVICE MAX | 1 | 0 | 160.001 | 0
| 36 | SERVICE MIN | 0 | -305.1234 | 0 | -42.2709
| 36 | SERVICE MIN | 1 | -309.8396 | 0 | -90.9901
| 37 | SERVICE MAX | 0 | 0 | 0 | 0
| 37 | SERVICE MAX | 0.25 | 0 | 0 | 0
| 37 | SERVICE MAX | 0.5 | 0 | 0 | 4e-06
| 37 | SERVICE MAX | 0.75 | 0 | 0 | 0.000107
| 37 | SERVICE MAX | 1 | 0 | 0 | 0.00021
| 37 | SERVICE MIN | 0 | -606.3564 | -0.000128 | -0.000202
| 37 | SERVICE MIN | 0.25 | -614.1964 | -0.000128 | -9.9e-05
| 37 | SERVICE MIN | 0.5 | -622.0364 | -0.000128 | 0
| 37 | SERVICE MIN | 0.75 | -629.8764 | -0.000128 | 0
| 37 | SERVICE MIN | 1 | -637.7164 | -0.000128 | 0

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 48.6049 | 0 | 85.5244 | 15 | ULTIMATE MIN | 0 | -169.0183 | 0 | 0
| 1 | ULTIMATE MAX | 1 | 48.181 | 0 | 87.795 | 15 | ULTIMATE MIN | 1 | -163.1365 | 0 | 0
| 1 | ULTIMATE MIN | 0 | 0 | -24.6955 | 0 | 16 | ULTIMATE MAX | 0 | 0 | 66.0191 | 62.1631
| 1 | ULTIMATE MIN | 1 | 0 | -29.4118 | 0 | 16 | ULTIMATE MAX | 1 | 0 | 62.3023 | 31.2738
| 2 | ULTIMATE MAX | 0 | 48.181 | 0 | 87.795 | 16 | ULTIMATE MIN | 0 | -163.1365 | 0 | 0
| 2 | ULTIMATE MAX | 0.5 | 47.6955 | 0 | 91.9896 | 16 | ULTIMATE MIN | 1 | -155.0701 | 0 | 0
| 2 | ULTIMATE MAX | 1 | 47.21 | 0 | 97.8859 | 17 | ULTIMATE MAX | 0 | 0 | 62.3023 | 31.2738
| 2 | ULTIMATE MIN | 0 | 0 | -29.4101 | 0 | 17 | ULTIMATE MAX | 1 | 0 | 59.6292 | 16.8143
| 2 | ULTIMATE MIN | 0.5 | 0 | -34.8123 | 0 | 17 | ULTIMATE MIN | 0 | -155.0701 | 0 | 0
| 2 | ULTIMATE MIN | 1 | 0 | -40.2146 | 0 | 17 | ULTIMATE MIN | 1 | -151.0873 | 0 | 0
| 3 | ULTIMATE MAX | 0 | 47.21 | 0 | 97.8859 | 18 | ULTIMATE MAX | 0 | 0 | 85.5729 | 16.8143
| 3 | ULTIMATE MAX | 1 | 46.82 | 0 | 103.8539 | 18 | ULTIMATE MAX | 0.5 | 0 | 81.9309 | 0
| 3 | ULTIMATE MIN | 0 | 0 | -40.2146 | 0 | 18 | ULTIMATE MAX | 1 | 0 | 77.6216 | 0
| 3 | ULTIMATE MIN | 1 | 0 | -44.5535 | 0 | 18 | ULTIMATE MIN | 0 | -214.0921 | 0 | 0
| 4 | ULTIMATE MAX | 0 | 42.6857 | 106.8601 | 103.8539 | 18 | ULTIMATE MIN | 0.5 | -209.6136 | 0 | -9.7617
| 4 | ULTIMATE MAX | 0.25 | 42.2391 | 101.8908 | 73.6111 | 18 | ULTIMATE MIN | 1 | -206.1975 | 0 | -26.7956
| 4 | ULTIMATE MAX | 0.5 | 41.7924 | 96.9216 | 44.8081 | 19 | ULTIMATE MAX | 0 | 0 | 77.6216 | 0
| 4 | ULTIMATE MAX | 0.75 | 41.3458 | 91.9524 | 17.445 | 19 | ULTIMATE MAX | 0.5 | 0 | 72.6622 | 0
| 4 | ULTIMATE MAX | 1 | 40.8992 | 86.9832 | 0 | 19 | ULTIMATE MAX | 1 | 0 | 67.0699 | 0
| 4 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 19 | ULTIMATE MIN | 0 | -206.1975 | 0 | -26.7956
| 4 | ULTIMATE MIN | 0.25 | 0 | 0 | 0 | 19 | ULTIMATE MIN | 0.5 | -203.4938 | 0 | -46.835
| 4 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 19 | ULTIMATE MIN | 1 | -200.7902 | 0 | -65.4683
| 4 | ULTIMATE MIN | 0.75 | 0 | 0 | 0 | 20 | ULTIMATE MAX | 0 | 0 | 102.5028 | 0
| 4 | ULTIMATE MIN | 1 | 0 | 0 | -14.2043 | 20 | ULTIMATE MAX | 1 | 0 | 97.0094 | 0
| 5 | ULTIMATE MAX | 0 | 42.881 | 227.2523 | 0 | 20 | ULTIMATE MIN | 0 | -266.8474 | 0 | -65.4683
| 5 | ULTIMATE MAX | 1 | 43.3866 | 221.6271 | 0 | 20 | ULTIMATE MIN | 1 | -264.443 | 0 | -89.1199
| 5 | ULTIMATE MIN | 0 | 0 | 0 | -14.2043 | 21 | ULTIMATE MAX | 0 | 0 | 97.0094 | 0
| 5 | ULTIMATE MIN | 1 | 0 | 0 | -82.0945 | 21 | ULTIMATE MAX | 1 | 0 | 84.4458 | 0
| 6 | ULTIMATE MAX | 0 | 43.3866 | 221.6271 | 0 | 21 | ULTIMATE MIN | 0 | -264.443 | 0 | -89.1199
| 6 | ULTIMATE MAX | 0.5 | 43.8721 | 216.2249 | 0 | 21 | ULTIMATE MIN | 1 | -259.5734 | 0 | -132.7455
| 6 | ULTIMATE MAX | 1 | 44.3576 | 210.8226 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 84.4458 | 0
| 6 | ULTIMATE MIN | 0 | 0 | 0 | -82.0945 | 22 | ULTIMATE MAX | 1 | 0 | 82.8487 | 0
| 6 | ULTIMATE MIN | 0.5 | 0 | 0 | -151.0562 | 22 | ULTIMATE MIN | 0 | -259.5734 | 0 | -132.7455
| 6 | ULTIMATE MIN | 1 | 0 | 0 | -218.3162 | 22 | ULTIMATE MIN | 1 | -256.0227 | 0 | -160.5196
| 7 | ULTIMATE MAX | 0 | 44.3576 | 210.8226 | 0 | 23 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 7 | ULTIMATE MAX | 1 | 44.6659 | 207.3926 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 7 | ULTIMATE MIN | 0 | 0 | 0 | -218.3162 | 23 | ULTIMATE MIN | 0 | -107.2459 | -311.0036 | -160.5196
| 7 | ULTIMATE MIN | 1 | 0 | 0 | -260.1378 | 23 | ULTIMATE MIN | 1 | -104.1705 | -266.9624 | -81.0493
| 8 | ULTIMATE MAX | 0 | 44.6659 | 0 | 0 | 24 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 8 | ULTIMATE MAX | 1 | 44.3576 | 0 | 0 | 24 | ULTIMATE MAX | 0.5 | 0 | 0 | 26.3156
| 8 | ULTIMATE MIN | 0 | 0 | -207.3926 | -260.1378 | 24 | ULTIMATE MAX | 1 | 0 | 0 | 81.2746
| 8 | ULTIMATE MIN | 1 | 0 | -210.8226 | -218.3162 | 24 | ULTIMATE MIN | 0 | -104.1705 | -266.9624 | -81.0493
| 9 | ULTIMATE MAX | 0 | 44.3576 | 0 | 0 | 24 | ULTIMATE MIN | 0.5 | -100.6478 | -216.5151 | -4.9016
| 9 | ULTIMATE MAX | 0.5 | 43.8721 | 0 | 0 | 24 | ULTIMATE MIN | 1 | -97.1251 | -166.0678 | 0
| 9 | ULTIMATE MAX | 1 | 43.3866 | 0 | 0 | 25 | ULTIMATE MAX | 0 | 0 | 0 | 81.2746
| 9 | ULTIMATE MIN | 0 | 0 | -210.8226 | -218.3162 | 25 | ULTIMATE MAX | 1 | 0 | 0 | 113.9094
| 9 | ULTIMATE MIN | 0.5 | 0 | -216.2249 | -151.0562 | 25 | ULTIMATE MIN | 0 | -97.1251 | -166.0678 | 0
| 9 | ULTIMATE MIN | 1 | 0 | -221.6271 | -82.0945 | 25 | ULTIMATE MIN | 1 | -94.2957 | -125.5499 | 0
| 10 | ULTIMATE MAX | 0 | 43.3866 | 0 | 0 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 113.9094
| 10 | ULTIMATE MAX | 1 | 42.881 | 0 | 0 | 26 | ULTIMATE MAX | 0.25 | 0 | 0 | 138.6915
| 10 | ULTIMATE MIN | 0 | 0 | -221.6271 | -82.0945 | 26 | ULTIMATE MAX | 0.5 | 0 | 0 | 150.0282
| 10 | ULTIMATE MIN | 1 | 0 | -227.2523 | -14.2043 | 26 | ULTIMATE MAX | 0.75 | 0 | 30.4844 | 147.9195
| 11 | ULTIMATE MAX | 0 | 40.8992 | 0 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 76.8879 | 132.3654
| 11 | ULTIMATE MAX | 0.25 | 41.3458 | 0 | 17.445 | 26 | ULTIMATE MIN | 0 | -101.7771 | -125.5488 | 0
| 11 | ULTIMATE MAX | 0.5 | 41.7924 | 0 | 44.8081 | 26 | ULTIMATE MIN | 0.25 | -98.5367 | -79.1453 | 0
| 11 | ULTIMATE MAX | 0.75 | 42.2391 | 0 | 73.6111 | 26 | ULTIMATE MIN | 0.5 | -95.2964 | -32.7419 | 0
| 11 | ULTIMATE MAX | 1 | 42.6857 | 0 | 103.8539 | 26 | ULTIMATE MIN | 0.75 | -92.0561 | 0 | 0
| 11 | ULTIMATE MIN | 0 | 0 | -86.9832 | -14.2043 | 26 | ULTIMATE MIN | 1 | -95.2392 | 0 | 0
| 11 | ULTIMATE MIN | 0.25 | 0 | -91.9524 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 76.884 | 132.3654
| 11 | ULTIMATE MIN | 0.5 | 0 | -96.9216 | 0 | 27 | ULTIMATE MAX | 1 | 0 | 129.4132 | 101.8762
| 11 | ULTIMATE MIN | 0.75 | 0 | -101.8908 | 0 | 27 | ULTIMATE MIN | 0 | -96.3681 | 0 | 0
| 11 | ULTIMATE MIN | 1 | 0 | -106.8601 | 0 | 27 | ULTIMATE MIN | 1 | -92.7001 | 0 | 0
| 12 | ULTIMATE MAX | 0 | 46.82 | 44.5535 | 103.8539 | 28 | ULTIMATE MAX | 0 | 0 | 129.4132 | 101.8762
| 12 | ULTIMATE MAX | 1 | 47.21 | 40.2146 | 97.8859 | 28 | ULTIMATE MAX | 0.5 | 0 | 179.8604 | 58.4632
| 12 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 230.3077 | 0
| 12 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 0 | -92.7001 | 0 | 0
| 13 | ULTIMATE MAX | 0 | 47.21 | 40.2146 | 97.8859 | 28 | ULTIMATE MIN | 0.5 | -94.7405 | 0 | 0
| 13 | ULTIMATE MAX | 0.5 | 47.6955 | 34.8123 | 91.9896 | 28 | ULTIMATE MIN | 1 | -98.2632 | 0 | -14.7848
| 13 | ULTIMATE MAX | 1 | 48.181 | 29.4101 | 87.795 | 29 | ULTIMATE MAX | 0 | 0 | 230.3077 | 0
| 13 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 29 | ULTIMATE MAX | 1 | 0 | 262.3377 | 0
| 13 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 29 | ULTIMATE MIN | 0 | -98.2632 | 0 | -14.7848
| 13 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 29 | ULTIMATE MIN | 1 | -100.4999 | 0 | -64.0455
| 14 | ULTIMATE MAX | 0 | 48.181 | 29.4118 | 87.795 | 30 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 14 | ULTIMATE MAX | 1 | 48.6049 | 24.6955 | 85.5244 | 30 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 14 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 30 | ULTIMATE MIN | 0 | -100.4999 | -262.3377 | -64.0455
| 14 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 30 | ULTIMATE MIN | 1 | -98.2632 | -230.3077 | -14.7848
| 15 | ULTIMATE MAX | 0 | 0 | 67.2661 | 85.5244 | 31 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 66.0191 | 62.1631 | 31 | ULTIMATE MAX | 0.5 | 0 | 0 | 58.4632
| FRAME | LOAD | DIST | P | V2 | M3
| 31 | ULTIMATE MAX | 1 | 0 | 0 | 101.8762
| 31 | ULTIMATE MIN | 0 | -98.2632 | -230.3077 | -14.7848
| 31 | ULTIMATE MIN | 0.5 | -94.7405 | -179.8604 | 0
| 31 | ULTIMATE MIN | 1 | -92.7001 | -129.4132 | 0
| 32 | ULTIMATE MAX | 0 | 0 | 0 | 101.8762
| 32 | ULTIMATE MAX | 1 | 0 | 0 | 132.3654
| 32 | ULTIMATE MIN | 0 | -92.7001 | -129.4132 | 0
| 32 | ULTIMATE MIN | 1 | -96.3681 | -76.884 | 0
| 33 | ULTIMATE MAX | 0 | 0 | 0 | 132.3654
| 33 | ULTIMATE MAX | 0.25 | 0 | 0 | 147.9195
| 33 | ULTIMATE MAX | 0.5 | 0 | 32.7419 | 150.0282
| 33 | ULTIMATE MAX | 0.75 | 0 | 79.1453 | 138.6915
| 33 | ULTIMATE MAX | 1 | 0 | 125.5488 | 113.9094
| 33 | ULTIMATE MIN | 0 | -95.2392 | -76.8879 | 0
| 33 | ULTIMATE MIN | 0.25 | -92.0561 | -30.4844 | 0
| 33 | ULTIMATE MIN | 0.5 | -95.2964 | 0 | 0
| 33 | ULTIMATE MIN | 0.75 | -98.5367 | 0 | 0
| 33 | ULTIMATE MIN | 1 | -101.7771 | 0 | 0
| 34 | ULTIMATE MAX | 0 | 0 | 125.5499 | 113.9094
| 34 | ULTIMATE MAX | 1 | 0 | 166.0678 | 81.2746
| 34 | ULTIMATE MIN | 0 | -94.2957 | 0 | 0
| 34 | ULTIMATE MIN | 1 | -97.1251 | 0 | 0
| 35 | ULTIMATE MAX | 0 | 0 | 166.0678 | 81.2746
| 35 | ULTIMATE MAX | 0.5 | 0 | 216.5151 | 26.3156
| 35 | ULTIMATE MAX | 1 | 0 | 266.9624 | 0
| 35 | ULTIMATE MIN | 0 | -97.1251 | 0 | 0
| 35 | ULTIMATE MIN | 0.5 | -100.6478 | 0 | -4.9016
| 35 | ULTIMATE MIN | 1 | -104.1705 | 0 | -81.0493
| 36 | ULTIMATE MAX | 0 | 0 | 266.9624 | 0
| 36 | ULTIMATE MAX | 1 | 0 | 311.0036 | 0
| 36 | ULTIMATE MIN | 0 | -104.1705 | 0 | -81.0493
| 36 | ULTIMATE MIN | 1 | -107.2459 | 0 | -160.5196
| 37 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 37 | ULTIMATE MIN | 0 | -256.0227 | -82.8487 | -160.5196
| 37 | ULTIMATE MIN | 1 | -259.5734 | -84.4458 | -132.7455
| 38 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 38 | ULTIMATE MIN | 0 | -259.5734 | -84.4458 | -132.7455
| 38 | ULTIMATE MIN | 1 | -264.443 | -97.0094 | -89.1199
| 39 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 39 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 39 | ULTIMATE MIN | 0 | -264.443 | -97.0094 | -89.1199
| 39 | ULTIMATE MIN | 1 | -266.8474 | -102.5028 | -65.4683
| 40 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 40 | ULTIMATE MIN | 0 | -200.7902 | -67.0699 | -65.4683
| 40 | ULTIMATE MIN | 0.5 | -203.4938 | -72.6622 | -46.835
| 40 | ULTIMATE MIN | 1 | -206.1975 | -77.6216 | -26.7956
| 41 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 41 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 41 | ULTIMATE MAX | 1 | 0 | 0 | 16.8143
| 41 | ULTIMATE MIN | 0 | -206.1975 | -77.6216 | -26.7956
| 41 | ULTIMATE MIN | 0.5 | -209.6136 | -81.9309 | -9.7617
| 41 | ULTIMATE MIN | 1 | -214.0921 | -85.5729 | 0
| 42 | ULTIMATE MAX | 0 | 0 | 0 | 16.8143
| 42 | ULTIMATE MAX | 1 | 0 | 0 | 31.2738
| 42 | ULTIMATE MIN | 0 | -151.0873 | -59.6292 | 0
| 42 | ULTIMATE MIN | 1 | -155.0701 | -62.3023 | 0
| 43 | ULTIMATE MAX | 0 | 0 | 0 | 31.2738
| 43 | ULTIMATE MAX | 1 | 0 | 0 | 62.1631
| 43 | ULTIMATE MIN | 0 | -155.0701 | -62.3023 | 0
| 43 | ULTIMATE MIN | 1 | -163.1365 | -66.0191 | 0
| 44 | ULTIMATE MAX | 0 | 0 | 0 | 62.1631
| 44 | ULTIMATE MAX | 1 | 0 | 0 | 85.5244
| 44 | ULTIMATE MIN | 0 | -163.1365 | -66.0191 | 0
| 44 | ULTIMATE MIN | 1 | -169.0183 | -67.2661 | 0
| 45 | ULTIMATE MAX | 0 | 0 | 9.4625 | 17.3022
| 45 | ULTIMATE MAX | 0.25 | 0 | 10.5523 | 9.2953
| 45 | ULTIMATE MAX | 0.5 | 0 | 11.627 | 0.42265
| 45 | ULTIMATE MAX | 0.75 | 0 | 12.6866 | 9.3038
| 45 | ULTIMATE MAX | 1 | 0 | 13.7312 | 19.8719
| 45 | ULTIMATE MIN | 0 | -507.8587 | -9.4625 | -17.3022
| 45 | ULTIMATE MIN | 0.25 | -515.6987 | -10.5523 | -9.2953
| 45 | ULTIMATE MIN | 0.5 | -523.5387 | -11.627 | -0.42265
| 45 | ULTIMATE MIN | 0.75 | -531.3787 | -12.6866 | -9.3038
| 45 | ULTIMATE MIN | 1 | -539.2187 | -13.7312 | -19.8719

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 188.652 | 192.964 | 256.863 | 117.442 | 1000 | 816.667
|  | 제 1경간 중앙부 | 175.393 | - | 256.862 | 112.318 | 1000 | 700
|  | 제 1경간 지점부 | 262.142 | 262.361 | 256.862 | 171.668 | 1000 | 816.667
|  | 제 2경간 중앙부 | 175.393 | - | 256.862 | 112.318 | 1000 | 700
|  | 단지점부(우측) | 188.652 | 192.964 | 256.863 | 117.442 | 1000 | 816.667
| 하부슬래브 | 단지점부(좌측) | 140.502 | 258.282 | 252.814 | 90.99 | 1000 | 700
|  | 제 1경간 중앙부 | 178.424 | - | 252.814 | 117.693 | 1000 | 700
|  | 제 1경간 지점부 | 284.381 | 348.447 | 252.814 | 183.202 | 1000 | 700
|  | 제 2경간 중앙부 | 178.424 | - | 252.814 | 117.693 | 1000 | 700
|  | 단지점부(우측) | 140.502 | 258.282 | 252.814 | 90.99 | 1000 | 700
| 좌측벽체 | 상부 | 188.652 | 139.646 | 418.652 | 117.442 | 1000 | 666.667
|  | 중앙부 | 44.633 | - | 444.524 | 25.525 | 1000 | 550
|  | 중앙부(부모멘트) | -47.765 | - | 444.524 | -30.332 | 1000 | 550 | 부모멘트
|  | 하부 | 140.502 | 105.695 | 470.396 | 90.99 | 1000 | 550
| 우측벽체 | 상부 | 188.652 | 139.647 | 418.652 | 117.442 | 1000 | 666.667
|  | 중앙부 | 44.633 | - | 444.524 | 25.525 | 1000 | 550
|  | 중앙부(부모멘트) | -47.765 | - | 444.524 | -30.332 | 1000 | 550 | 부모멘트
|  | 하부 | 140.502 | 105.695 | 470.396 | 90.99 | 1000 | 550

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 160.52 | 166.068 | 107.246 | 1000 | 816.667
|  | 제 1경간 중앙부 | 150.028 | - | 95.296 | 1000 | 700
|  | 제 1경간 지점부 | 64.045 | 129.413 | 100.5 | 1000 | 816.667
|  | 제 2경간 중앙부 | 150.028 | - | 95.296 | 1000 | 700
|  | 단지점부(우측) | 160.52 | 166.068 | 107.246 | 1000 | 816.667
| 하부슬래브 | 단지점부(좌측) | 0 | 40.215 | 48.605 | 1000 | 700
|  | 제 1경간 중앙부 | 103.854 | - | 46.82 | 1000 | 700
|  | 제 1경간 지점부 | 260.138 | 221.627 | 44.666 | 1000 | 700
|  | 제 2경간 중앙부 | 103.854 | - | 42.686 | 1000 | 700
|  | 단지점부(우측) | 0 | 40.215 | 48.605 | 1000 | 700
| 좌측벽체 | 상부 | 160.52 | 97.009 | 256.023 | 1000 | 666.667
|  | 중앙부 | 31.274 | - | 155.07 | 1000 | 550
|  | 중앙부(부모멘트) | -89.12 | - | 155.07 | 1000 | 550 | 부모멘트
|  | 하부 | 0 | 62.302 | 169.018 | 1000 | 550
| 우측벽체 | 상부 | 160.52 | 97.009 | 256.023 | 1000 | 666.667
|  | 중앙부 | 31.274 | - | 155.07 | 1000 | 550
|  | 중앙부(부모멘트) | -89.12 | - | 155.07 | 1000 | 550 | 부모멘트
|  | 하부 | 0 | 62.302 | 169.018 | 1000 | 550

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 746.667 | 188.652 | 394.929 |  | 750.512 | H16 - 8.0EA |  |  | 1588.8 | 2.093
상부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 650 | 175.393 | 342.711 |  | 803.367 | H16 - 8.0EA |  |  | 1588.8 | 1.954
상부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 746.667 | 262.142 | 480.052 |  | 1046.991 | H19 - 4.0EA + H16 - 4.0EA |  |  | 1940.4 | 1.831
상부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 650 | 175.393 | 342.711 |  | 803.367 | H16 - 8.0EA |  |  | 1588.8 | 1.954
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 746.667 | 188.652 | 394.929 |  | 750.512 | H16 - 8.0EA |  |  | 1588.8 | 2.093
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 630 | 140.502 | 273.073 |  | 662.773 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.944
하부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 650 | 178.424 | 281.921 |  | 817.426 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.58
하부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 630 | 284.381 | 473.436 |  | 1356.267 | H19 - 8.0EA |  |  | 2292 | 1.665
하부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 650 | 178.424 | 281.921 |  | 817.426 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.58
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 630 | 140.502 | 273.073 |  | 662.773 | H16 - 4.0EA + H13 - 4.0EA |  |  | 1301.2 | 1.944
좌측벽체 : 상부 |  |  |  | 1000 |  | 596.667 | 188.652 | 711.418 |  | - | H16 - 8.0EA |  |  | - | 3.771
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 500 | 44.633 | 595.834 |  | - | H13 - 4.0EA |  |  | - | 13.35
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 480 | 89.12 | 664.508 |  | - | H16 - 4.0EA |  |  | - | 7.456
좌측벽체 : 하부 |  |  |  | 1000 |  | 480 | 140.502 | 581.599 |  | - | H16 - 4.0EA + H13 - 4.0EA |  |  | - | 4.139
우측벽체 : 상부 |  |  |  | 1000 |  | 596.667 | 188.652 | 711.418 |  | - | H16 - 8.0EA |  |  | - | 3.771
우측벽체 : 중앙부 |  |  |  | 1000 |  | 500 | 44.633 | 595.832 |  | - | H13 - 4.0EA |  |  | - | 13.35
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 480 | 89.12 | 664.508 |  | - | H16 - 4.0EA |  |  | - | 7.456
우측벽체 : 하부 |  |  |  | 1000 |  | 480 | 140.502 | 581.599 |  | - | H16 - 4.0EA + H13 - 4.0EA |  |  | - | 4.139
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 385.795 |  | 192.964 | 385.795 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 1경간 중앙부 |  |  |  | 398.042 |  | - | 398.042 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 지점부 |  |  |  | 385.795 |  | 262.361 | 385.795 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 중앙부 |  |  |  | 398.042 |  | - | 398.042 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 385.795 |  | 192.964 | 385.795 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 385.795 |  | 258.282 | 385.795 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 1경간 중앙부 |  |  |  | 398.042 |  | - | 398.042 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 지점부 |  |  |  | 385.795 |  | 348.447 | 385.795 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 중앙부 |  |  |  | 398.042 |  | - | 398.042 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 385.795 |  | 258.282 | 385.795 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 309.92 |  | 139.646 | 309.92 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 323.862 |  | - | 323.862 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 311.896 |  | 105.695 | 311.896 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 309.92 |  | 139.647 | 309.92 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 323.862 |  | - | 323.862 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 311.896 |  | 105.695 | 311.896 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 816.667 |  | 746.667 |  | 70 |  | 188.652 |  | 192.964
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (746.67 - 36.651) / 36.651 = 0.0581
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 750.512 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00213
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (746.67 - a/2) = 394.929 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 188.652 kN.m) ∴ O.K [안전률 2.093]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 192.964 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 650 |  | 50 |  | 175.393 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (650.00 - 36.651) / 36.651 = 0.0502
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 803.367 mm²
Use As = 1588.800 mm² (철근도심 : 50.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00244
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (650.00 - a/2) = 342.711 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 175.393 kN.m) ∴ O.K [안전률 1.954]
＊ 전단에 대한 검토 (d = 650.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 650.00 = 398.042 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 816.667 |  | 746.667 |  | 70 |  | 262.142 |  | 262.361
＊ 강도감소계수(Φ) 산정
T = As x fy = 1940.400 x 400.00 = 776160.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 38.047 mm, c = 38.047 / β1 = 38.047 / 0.85 = 44.761 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (746.67 - 44.761) / 44.761 = 0.0470
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1046.991 mm²
Use As = 1940.400 mm² (철근도심 : 70.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00260
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1940.400 x 400 x (746.67 - a/2) = 480.052 kN.m
; a = As x fy / (0.85 x fck x b) = 38.047 mm
≥ Mu (= 262.142 kN.m) ∴ O.K [안전률 1.831]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 262.361 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 650 |  | 50 |  | 175.393 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (650.00 - 36.651) / 36.651 = 0.0502
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 803.367 mm²
Use As = 1588.800 mm² (철근도심 : 50.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00244
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (650.00 - a/2) = 342.711 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 175.393 kN.m) ∴ O.K [안전률 1.954]
＊ 전단에 대한 검토 (d = 650.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 650.00 = 398.042 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 816.667 |  | 746.667 |  | 70 |  | 188.652 |  | 192.964
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 400.00 = 635520.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.153 mm, c = 31.153 / β1 = 31.153 / 0.85 = 36.651 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (746.67 - 36.651) / 36.651 = 0.0581
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 750.512 mm²
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00213
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 400 x (746.67 - a/2) = 394.929 kN.m
; a = As x fy / (0.85 x fck x b) = 31.153 mm
≥ Mu (= 188.652 kN.m) ∴ O.K [안전률 2.093]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 192.964 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 630 |  | 70 |  | 140.502 |  | 258.282
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (630.00 - 30.016) / 30.016 = 0.0600
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 662.773 mm²
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00207
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (630.00 - a/2) = 273.073 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 140.502 kN.m) ∴ O.K [안전률 1.944]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 258.282 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 650 |  | 50 |  | 178.424 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (650.00 - 30.016) / 30.016 = 0.0620
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 817.426 mm²
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00200
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (650.00 - a/2) = 281.921 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 178.424 kN.m) ∴ O.K [안전률 1.580]
＊ 전단에 대한 검토 (d = 650.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 650.00 = 398.042 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 630 |  | 70 |  | 284.381 |  | 348.447
＊ 강도감소계수(Φ) 산정
T = As x fy = 2292.000 x 400.00 = 916800.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 44.941 mm, c = 44.941 / β1 = 44.941 / 0.85 = 52.872 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (630.00 - 52.872) / 52.872 = 0.0327
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1356.267 mm²
Use As = 2292.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 8.0 EA (= 2292.000 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00364
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 2292.000 x 400 x (630.00 - a/2) = 473.436 kN.m
; a = As x fy / (0.85 x fck x b) = 44.941 mm
≥ Mu (= 284.381 kN.m) ∴ O.K [안전률 1.665]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 348.447 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 650 |  | 50 |  | 178.424 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (650.00 - 30.016) / 30.016 = 0.0620
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 817.426 mm²
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00200
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (650.00 - a/2) = 281.921 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 178.424 kN.m) ∴ O.K [안전률 1.580]
＊ 전단에 대한 검토 (d = 650.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 650.00 = 398.042 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 700 |  | 630 |  | 70 |  | 140.502 |  | 258.282
＊ 강도감소계수(Φ) 산정
T = As x fy = 1301.200 x 400.00 = 520480.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.514 mm, c = 25.514 / β1 = 25.514 / 0.85 = 30.016 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (630.00 - 30.016) / 30.016 = 0.0600
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 662.773 mm²
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00207
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1301.200 x 400 x (630.00 - a/2) = 273.073 kN.m
; a = As x fy / (0.85 x fck x b) = 25.514 mm
≥ Mu (= 140.502 kN.m) ∴ O.K [안전률 1.944]
＊ 전단에 대한 검토 (d = 630.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 630.00 = 385.795 kN
≥ Vu (= 258.282 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 666.667 |  | 596.667 |  | 418.652 |  | 188.652 |  | 139.646 |  | 450.619
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0031) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 666.7 x 1000.0 = 13600000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (13600000.0 x 333.33 + 635520.0 x 70.000 + 202720.0 x 616.667) / 14438240.0
= 325.720 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 358.000 mm, ab = k1 x cb = 304.300 mm
fs' = 600 x (358.000 - 50.000) / 358.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 304.300 x 1000.000 = 6207.720 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 635.520 kN
Pb = 6207.720 + 192.381 - 635.520 = 5764.581 kN
Mb = 6207.720 x (596.667 - 304.300/2) + 192.381 x (596.667 - 50.00)
- 5764.581 x (325.720 - 70.000)
= 1390.482 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 241.211 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 142.111 mm, a = k1 x c = 120.794 mm 를 사용.
fs = 600 x (596.667 - 142.111) / 142.111 (≤fy) = 400.000 MPa
fs' = 600 x (142.111 - 50.000) / 142.111 (≤fy) = 388.897 MPa
Cc = 0.85 x 24.0 x 120.794 x 1000.000 = 2464.200 kN
Cs = As' x (fs' - 0.85 x fck) = 186.754 kN
Ts = As x fs = 635.520 kN
Pn = 2464.200 + 186.754 - 635.520 = 2015.435 kN
Mn' = 2464.200 x (596.667 - 120.794/2) + 186.754 x (596.667 - 50.00)
= 1423.568 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0067 ＜ 0.0100 (e' = e + Xp - dc = 706.340 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 11516.392 kN ≥ Pn = 2015.435 kN
ΦPn = 0.78 x 2015.435 = 1578.757 kN ≥ Pu = 418.652 kN ∴ O.K
ΦMn = ΦPn x 0.451 = 711.418 kN.m ≥ Mu = 188.652 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 309.920 kN
≥ Vu (= 139.646 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 500 |  | 444.524 |  | 44.633 |  | 0 |  | 100.407
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0024) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 202720.0 x 50.000 + 317760.0 x 480.000) / 11740480.0
= 276.663 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 300.000 mm, ab = k1 x cb = 255.000 mm
fs' = 600 x (300.000 - 70.000) / 300.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 255.000 x 1000.000 = 5202.000 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 202.720 kN
Pb = 5202.000 + 301.554 - 202.720 = 5300.834 kN
Mb = 5202.000 x (500.000 - 255.000/2) + 301.554 x (500.000 - 70.00)
- 5300.834 x (276.663 - 50.000)
= 865.908 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 163.353 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 422.699 mm, a = k1 x c = 359.294 mm 를 사용.
fs = 600 x (500.000 - 422.699) / 422.699 (≤fy) = 109.725 MPa
fs' = 600 x (422.699 - 70.000) / 422.699 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 359.294 x 1000.000 = 7329.600 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 55.609 kN
Pn = 7329.600 + 301.554 - 55.609 = 7575.546 kN
Mn' = 7329.600 x (500.000 - 359.294/2) + 301.554 x (500.000 - 70.00)
= 2477.727 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0014 ＜ 0.0100 (e' = e + Xp - dc = 327.071 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 50.00 = 500.000 mm
c = 600.00 / (600.00+400.00) x 500.000 = 300.000 mm, a = k1 x c = 255.000 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (500.00-300.00) / 300.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9371.148 kN ≥ Pn = 7575.546 kN
ΦPn = 0.78 x 7575.546 = 5934.178 kN ≥ Pu = 444.524 kN ∴ O.K
ΦMn = ΦPn x 0.100 = 595.834 kN.m ≥ Mu = 44.633 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 500.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 500.00 = 323.862 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 444.524 |  | 89.12 |  | 0 |  | 200.484
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0024) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (11220000.0 x 275.00 + 317760.0 x 70.000 + 202720.0 x 500.000) / 11740480.0
= 273.337 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 50.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 317.760 kN
Pb = 4993.920 + 192.381 - 317.760 = 4868.541 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 192.381 x (480.000 - 50.00)
- 4868.541 x (273.337 - 70.000)
= 878.597 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 180.464 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 251.250 mm, a = k1 x c = 213.563 mm 를 사용.
fs = 600 x (480.000 - 251.250) / 251.250 (≤fy) = 400.000 MPa
fs' = 600 x (251.250 - 50.000) / 251.250 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 213.563 x 1000.000 = 4356.675 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 317.760 kN
Pn = 4356.675 + 192.381 - 317.760 = 4231.296 kN
Mn' = 4356.675 x (480.000 - 213.563/2) + 192.381 x (480.000 - 50.00)
= 1708.717 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0074 ＜ 0.0100 (e' = e + Xp - dc = 403.821 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9371.148 kN ≥ Pn = 4231.296 kN
ΦPn = 0.78 x 4231.296 = 3314.515 kN ≥ Pu = 444.524 kN ∴ O.K
ΦMn = ΦPn x 0.200 = 664.508 kN.m ≥ Mu = 89.120 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 310.908 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 470.396 |  | 140.502 |  | 105.695 |  | 298.689
＊ 철근비 검토
As = 1301.200 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA + H13- 4.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0033) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 520480.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (11220000.0 x 275.00 + 520480.0 x 70.000 + 202720.0 x 500.000) / 11943200.0
= 269.885 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 50.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 520.480 kN
Pb = 4993.920 + 192.381 - 520.480 = 4665.821 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 192.381 x (480.000 - 50.00)
- 4665.821 x (269.885 - 70.000)
= 935.921 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 200.591 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 162.275 mm, a = k1 x c = 137.934 mm 를 사용.
fs = 600 x (480.000 - 162.275) / 162.275 (≤fy) = 400.000 MPa
fs' = 600 x (162.275 - 50.000) / 162.275 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 137.934 x 1000.000 = 2813.855 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 520.480 kN
Pn = 2813.855 + 192.381 - 520.480 = 2485.757 kN
Mn' = 2813.855 x (480.000 - 137.934/2) + 192.381 x (480.000 - 50.00)
= 1239.311 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0089 ＜ 0.0100 (e' = e + Xp - dc = 498.574 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9525.053 kN ≥ Pn = 2485.757 kN
ΦPn = 0.78 x 2485.757 = 1947.176 kN ≥ Pu = 470.396 kN ∴ O.K
ΦMn = ΦPn x 0.299 = 581.599 kN.m ≥ Mu = 140.502 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 311.896 kN
≥ Vu (= 105.695 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 666.667 |  | 596.667 |  | 418.652 |  | 188.652 |  | 139.647 |  | 450.619
＊ 철근비 검토
As = 1588.800 mm² (인장중심 = 70.00 mm) , 1단 : H16- 8.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0031) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 666.7 x 1000.0 = 13600000.0 N
Cs = As x fy = 635520.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (13600000.0 x 333.33 + 635520.0 x 70.000 + 202720.0 x 616.667) / 14438240.0
= 325.720 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 358.000 mm, ab = k1 x cb = 304.300 mm
fs' = 600 x (358.000 - 50.000) / 358.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 304.300 x 1000.000 = 6207.720 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 635.520 kN
Pb = 6207.720 + 192.381 - 635.520 = 5764.581 kN
Mb = 6207.720 x (596.667 - 304.300/2) + 192.381 x (596.667 - 50.00)
- 5764.581 x (325.720 - 70.000)
= 1390.482 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 241.211 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 142.111 mm, a = k1 x c = 120.794 mm 를 사용.
fs = 600 x (596.667 - 142.111) / 142.111 (≤fy) = 400.000 MPa
fs' = 600 x (142.111 - 50.000) / 142.111 (≤fy) = 388.897 MPa
Cc = 0.85 x 24.0 x 120.794 x 1000.000 = 2464.200 kN
Cs = As' x (fs' - 0.85 x fck) = 186.754 kN
Ts = As x fs = 635.520 kN
Pn = 2464.200 + 186.754 - 635.520 = 2015.435 kN
Mn' = 2464.200 x (596.667 - 120.794/2) + 186.754 x (596.667 - 50.00)
= 1423.568 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0067 ＜ 0.0100 (e' = e + Xp - dc = 706.340 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 11516.392 kN ≥ Pn = 2015.435 kN
ΦPn = 0.78 x 2015.435 = 1578.757 kN ≥ Pu = 418.652 kN ∴ O.K
ΦMn = ΦPn x 0.451 = 711.418 kN.m ≥ Mu = 188.652 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 309.920 kN
≥ Vu (= 139.647 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 500 |  | 444.524 |  | 44.633 |  | 0 |  | 100.407
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Asf = 794.400 mm² (압축중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0024) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 317760.0 N
Xp = (11220000.0 x 275.00 + 202720.0 x 50.000 + 317760.0 x 480.000) / 11740480.0
= 276.663 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 300.000 mm, ab = k1 x cb = 255.000 mm
fs' = 600 x (300.000 - 70.000) / 300.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 255.000 x 1000.000 = 5202.000 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 202.720 kN
Pb = 5202.000 + 301.554 - 202.720 = 5300.834 kN
Mb = 5202.000 x (500.000 - 255.000/2) + 301.554 x (500.000 - 70.00)
- 5300.834 x (276.663 - 50.000)
= 865.908 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 163.353 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 422.699 mm, a = k1 x c = 359.294 mm 를 사용.
fs = 600 x (500.000 - 422.699) / 422.699 (≤fy) = 109.725 MPa
fs' = 600 x (422.699 - 70.000) / 422.699 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 359.294 x 1000.000 = 7329.600 kN
Cs = As' x (fs' - 0.85 x fck) = 301.554 kN
Ts = As x fs = 55.609 kN
Pn = 7329.600 + 301.554 - 55.609 = 7575.546 kN
Mn' = 7329.600 x (500.000 - 359.294/2) + 301.554 x (500.000 - 70.00)
= 2477.727 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0011 ＜ 0.0100 (e' = e + Xp - dc = 327.070 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 50.00 = 500.000 mm
c = 600.00 / (600.00+400.00) x 500.000 = 300.000 mm, a = k1 x c = 255.000 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (500.00-300.00) / 300.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9371.148 kN ≥ Pn = 7575.546 kN
ΦPn = 0.78 x 7575.546 = 5934.178 kN ≥ Pu = 444.524 kN ∴ O.K
ΦMn = ΦPn x 0.100 = 595.832 kN.m ≥ Mu = 44.633 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 500.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 500.00 = 323.862 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 444.524 |  | 89.12 |  | 0 |  | 200.484
＊ 철근비 검토
As = 794.400 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0024) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 317760.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (11220000.0 x 275.00 + 317760.0 x 70.000 + 202720.0 x 500.000) / 11740480.0
= 273.337 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 50.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 317.760 kN
Pb = 4993.920 + 192.381 - 317.760 = 4868.541 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 192.381 x (480.000 - 50.00)
- 4868.541 x (273.337 - 70.000)
= 878.597 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 180.464 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 251.250 mm, a = k1 x c = 213.563 mm 를 사용.
fs = 600 x (480.000 - 251.250) / 251.250 (≤fy) = 400.000 MPa
fs' = 600 x (251.250 - 50.000) / 251.250 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 213.563 x 1000.000 = 4356.675 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 317.760 kN
Pn = 4356.675 + 192.381 - 317.760 = 4231.296 kN
Mn' = 4356.675 x (480.000 - 213.563/2) + 192.381 x (480.000 - 50.00)
= 1708.717 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0074 ＜ 0.0100 (e' = e + Xp - dc = 403.821 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9371.148 kN ≥ Pn = 4231.296 kN
ΦPn = 0.78 x 4231.296 = 3314.515 kN ≥ Pu = 444.524 kN ∴ O.K
ΦMn = ΦPn x 0.200 = 664.508 kN.m ≥ Mu = 89.120 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 310.908 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 550 |  | 480 |  | 470.396 |  | 140.502 |  | 105.695 |  | 298.689
＊ 철근비 검토
As = 1301.200 mm² (인장중심 = 70.00 mm) , 1단 : H16- 4.0EA + H13- 4.0EA , d1 = 70.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0033) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 550.0 x 1000.0 = 11220000.0 N
Cs = As x fy = 520480.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (11220000.0 x 275.00 + 520480.0 x 70.000 + 202720.0 x 500.000) / 11943200.0
= 269.885 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 288.000 mm, ab = k1 x cb = 244.800 mm
fs' = 600 x (288.000 - 50.000) / 288.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 244.800 x 1000.000 = 4993.920 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 520.480 kN
Pb = 4993.920 + 192.381 - 520.480 = 4665.821 kN
Mb = 4993.920 x (480.000 - 244.800/2) + 192.381 x (480.000 - 50.00)
- 4665.821 x (269.885 - 70.000)
= 935.921 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 200.591 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 162.275 mm, a = k1 x c = 137.934 mm 를 사용.
fs = 600 x (480.000 - 162.275) / 162.275 (≤fy) = 400.000 MPa
fs' = 600 x (162.275 - 50.000) / 162.275 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 137.934 x 1000.000 = 2813.855 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 520.480 kN
Pn = 2813.855 + 192.381 - 520.480 = 2485.757 kN
Mn' = 2813.855 x (480.000 - 137.934/2) + 192.381 x (480.000 - 50.00)
= 1239.311 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0089 ＜ 0.0100 (e' = e + Xp - dc = 498.574 mm)
＊ 강도감소계수(Φ) 산정
dt = 550.00 - 70.00 = 480.000 mm
c = 600.00 / (600.00+400.00) x 480.000 = 288.000 mm, a = k1 x c = 244.800 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (480.00-288.00) / 288.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 9525.053 kN ≥ Pn = 2485.757 kN
ΦPn = 0.78 x 2485.757 = 1947.176 kN ≥ Pu = 470.396 kN ∴ O.K
ΦMn = ΦPn x 0.299 = 581.599 kN.m ≥ Mu = 140.502 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 480.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 480.00 = 311.896 kN
≥ Vu (= 105.695 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
2) 상부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
3) 상부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1940.4 |  | × | 0.2 |  | = | 388.08 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 388.080 ----------> O.K !!!
4) 상부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
5) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
6) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 260.240 ----------> O.K !!!
7) 하부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 260.240 ----------> O.K !!!
8) 하부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 2292 |  | × | 0.2 |  | = | 458.4 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 458.400 ----------> O.K !!!
9) 하부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 260.240 ----------> O.K !!!
10) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 700 |  | × | 0.002 |  | = | 1400 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1400.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 260.240 ----------> O.K !!!
11) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
12) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
13) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
14) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 260.240 ----------> O.K !!!
15) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1588.8 |  | × | 0.2 |  | = | 317.76 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 317.760 ----------> O.K !!!
16) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
17) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 794.4 |  | × | 0.2 |  | = | 158.88 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 158.880 ----------> O.K !!!
18) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 550 |  | × | 0.0025 |  | = | 1375 | mm²
|  | ∴ Used As | = | H16 - 10EA |  |  |  | = | 1986 |  |  | mm² > 1375.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1301.2 |  | × | 0.2 |  | = | 260.24 |  | mm²
|  | ∴ Used As | = | H16 - 5EA |  |  |  | = | 993 |  |  | mm² > 260.240 ----------> O.K !!!

## 거더,기둥검토,내측벽체
21. 거더,기둥,내측벽체 검토
(1) 내측벽체 검토
(단위 : kN,m)
|  | 기둥부재 |  | 폭 | 두께 | 높이 |  | 길이 | 축력 |  | 모멘트 |  | 축력×길이 | 모멘트×길이 | Load Case
|  | P1 |  | 1 | 0.4 | 2.15 |  | 1 | 976.32 |  | 0 |  | 976.32 | 0 | 3
[9 empty] | 539.22 |  | 19.87 |  | 539.22 | 19.87 | 1
* 벽체와 기둥의 판별 (P1)
0.4Agfck = 0.4 × 1000 × 400 × 24
|  |  | = 3840000 N = 3840.00 kN | [6 empty] | ≥ 976.32 kN
∴ 벽체로 검토한다
1)벽체 1
① 축력 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 350 |  | 976.325 |  |  | 0 |  | 0 |  | 0
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 50.000 + 202720.0 x 350.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 210.000 mm, ab = k1 x cb = 178.500 mm
fs' = 600 x (210.000 - 50.000) / 210.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 178.500 x 1000.000 = 3641.400 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 202.720 kN
Pb = 3641.400 + 192.381 - 202.720 = 3631.061 kN
Mb = 3641.400 x (350.000 - 178.500/2) + 192.381 x (350.000 - 50.00)
- 3631.061 x (200.000 - 50.000)
= 462.550 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 127.387 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 475.368 mm, a = k1 x c = 404.063 mm 를 사용.
fs = 600 x (350.000 - 475.368) / 475.368 (≤fy) = 158.237 MPa
fs' = 600 x (475.368 - 50.000) / 475.368 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 404.063 x 1000.000 = 8242.884 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 80.195 kN
Pn = 8242.884 + 192.381 - 80.195 = 8515.460 kN
Mn' = 8242.884 x (350.000 - 404.063/2) + 192.381 x (350.000 - 50.00)
= 1277.402 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0096 ＜ 0.0100 (e' = e + Xp - dc = 150.000 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 50.00 = 350.000 mm
c = 600.00 / (600.00+400.00) x 350.000 = 210.000 mm, a = k1 x c = 178.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (350.00-210.00) / 210.00 = 0.0020
εt ≤ εy 이므로 압축지배단면이며, Φ = 0.65 를 적용한다.
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ＜ Pn = 8515.460 kN
ΦPn = 0.65 x 6835.810 = 4443.277 kN ≥ Pu = 976.325 kN ∴ O.K
ΦMn = ΦPn x 0.000 = 0.001 kN.m ≥ Mu = 0.000 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 350.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 350.00 = 251.698 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
② 모멘트 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 400 |  | 350 |  | 539.219 |  |  | 19.872 |  | 0 |  | 36.853
＊ 철근비 검토
As = 506.800 mm² (인장중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Asf = 506.800 mm² (압축중심 = 50.00 mm) , 1단 : H13- 4.0EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0025) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 400.0 x 1000.0 = 8160000.0 N
Cs = As x fy = 202720.0 N, Cs' = Asf x fy = 202720.0 N
Xp = (8160000.0 x 200.00 + 202720.0 x 50.000 + 202720.0 x 350.000) / 8565440.0
= 200.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 210.000 mm, ab = k1 x cb = 178.500 mm
fs' = 600 x (210.000 - 50.000) / 210.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 178.500 x 1000.000 = 3641.400 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 202.720 kN
Pb = 3641.400 + 192.381 - 202.720 = 3631.061 kN
Mb = 3641.400 x (350.000 - 178.500/2) + 192.381 x (350.000 - 50.00)
- 3631.061 x (200.000 - 50.000)
= 462.550 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 127.387 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 389.441 mm, a = k1 x c = 331.025 mm 를 사용.
fs = 600 x (350.000 - 389.441) / 389.441 (≤fy) = 60.766 MPa
fs' = 600 x (389.441 - 50.000) / 389.441 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 331.025 x 1000.000 = 6752.907 kN
Cs = As' x (fs' - 0.85 x fck) = 192.381 kN
Ts = As x fs = 30.796 kN
Pn = 6752.907 + 192.381 - 30.796 = 6976.085 kN
Mn' = 6752.907 x (350.000 - 331.025/2) + 192.381 x (350.000 - 50.00)
= 1303.542 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0055 ＜ 0.0100 (e' = e + Xp - dc = 186.853 mm)
＊ 강도감소계수(Φ) 산정
dt = 400.00 - 50.00 = 350.000 mm
c = 600.00 / (600.00+400.00) x 350.000 = 210.000 mm, a = k1 x c = 178.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (350.00-210.00) / 210.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6835.810 kN ＜ Pn = 6976.085 kN
ΦPn = 0.78 x 6835.810 = 5354.718 kN ≥ Pu = 539.219 kN ∴ O.K
ΦMn = ΦPn x 0.037 = 197.338 kN.m ≥ Mu = 19.872 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 350.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 350.00 = 234.968 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.

## 절점부 검토
22. 절점부 검토
1) 절점 32
[10 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[10 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[10 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 117.442 kN.m
[10 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 117.442 kN.m
[11 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[11 empty] | = | 1131.371 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo | = | 5 × 117.44 × 10^6 |  |  | = | 0.459 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  | 1131.371²× 1000
∴ 절점부 보강철근 필요없음 !!!
2) 절점 1
[10 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[10 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[10 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 90.990 kN.m
[10 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 90.990 kN.m
R = √(T1² + T2²) = 890.225 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo | = | 5 × 90.99 × 10^6 |  |  | = | 0.574 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  | 890.225²× 1000
∴ 절점부 보강철근 필요없음 !!!
3) 절점 20
[10 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[10 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[10 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 117.442 kN.m
[10 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 117.442 kN.m
[11 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[11 empty] | = | 1131.371 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H16 @250 - 4EA |  |  |  | = | 794.4 | mm²
∴ Total Asb = 794.400 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo | = | 5 × 117.44 × 10^6 |  |  | = | 0.459 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  | 1131.371²× 1000
∴ 절점부 보강철근 필요없음 !!!
4) 절점 15
[10 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[10 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[10 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 90.990 kN.m
[10 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 90.990 kN.m
R = √(T1² + T2²) = 890.225 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @250 - 4EA |  |  |  | = | 506.8 | mm²
∴ Total Asb = 506.800 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo | = | 5 × 90.99 × 10^6 |  |  | = | 0.574 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  | 890.225²× 1000
∴ 절점부 보강철근 필요없음 !!!

## 사용성 검토
23. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 746.667 |  | H16 - 8.0EA |  |  | 125 | 598.486 | O.K |  | 4.788
2 | 상부슬래브 : 제 1경간 중앙부 |  | 650 |  | H16 - 8.0EA |  |  | 125 | 546.692 | O.K |  | 4.374
3 | 상부슬래브 : 제 2경간 지점부 |  | 746.667 |  | H19 - 4.0EA + H16 - 4.0EA |  |  | 125 | 474.96 | O.K |  | 3.8
4 | 상부슬래브 : 제 2경간 중앙부 |  | 650 |  | H16 - 8.0EA |  |  | 125 | 546.692 | O.K |  | 4.374
5 | 상부슬래브 : 단지점부(우측) |  | 746.667 |  | H16 - 8.0EA |  |  | 125 | 598.485 | O.K |  | 4.788
6 | 하부슬래브 : 단지점부(좌측) |  | 630 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 517.541 | O.K |  | 4.14
7 | 하부슬래브 : 제 1경간 중앙부 |  | 650 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 429.5 | O.K |  | 3.436
8 | 하부슬래브 : 제 2경간 지점부 |  | 630 |  | H19 - 8.0EA |  |  | 125 | 427.72 | O.K |  | 3.422
9 | 하부슬래브 : 제 2경간 중앙부 |  | 650 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 429.5 | O.K |  | 3.436
10 | 하부슬래브 : 단지점부(우측) |  | 630 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 517.541 | O.K |  | 4.14
11 | 좌측벽체 : 상부 |  | 596.667 |  | H16 - 8.0EA |  |  | 125 | 443.516 | O.K |  | 3.548
12 | 좌측벽체 : 중앙부 |  | 500 |  | H13 - 4.0EA |  |  | 250 | 602.034 | O.K |  | 2.408
13 | 좌측벽체 : 중앙부(부모멘트) |  | 480 |  | H16 - 4.0EA |  |  | 250 | 754.754 | O.K |  | 3.019
14 | 좌측벽체 : 하부 |  | 480 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 353.708 | O.K |  | 2.83
15 | 우측벽체 : 상부 |  | 596.667 |  | H16 - 8.0EA |  |  | 125 | 443.515 | O.K |  | 3.548
16 | 우측벽체 : 중앙부 |  | 500 |  | H13 - 4.0EA |  |  | 250 | 602.036 | O.K |  | 2.408
17 | 우측벽체 : 중앙부(부모멘트) |  | 480 |  | H16 - 4.0EA |  |  | 250 | 754.754 | O.K |  | 3.019
18 | 우측벽체 : 하부 |  | 480 |  | H16 - 4.0EA + H13 - 4.0EA |  |  | 125 | 353.708 | O.K |  | 2.83
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 117.442 x 1000000 / [1588.800 x (746.667 - 118.230/3)]
= 104.514 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x746.7/(7x1588.800)]
= 118.230 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 104.51) - 2.5 x 62.00 = 598.49 mm
300 x (210 / fs) = 300 x (210 / 104.51) = 602.79 mm
Sa는 작은 값인 598.49 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 598.49 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 112.318 x 1000000 / [1588.800 x (650.000 - 109.633/3)]
= 115.239 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x650.0/(7x1588.800)]
= 109.633 mm
Use As = 1588.800 mm² (철근도심 : 50.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 115.24) - 2.5 x 42.00 = 578.36 mm
300 x (210 / fs) = 300 x (210 / 115.24) = 546.69 mm
Sa는 작은 값인 546.69 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 546.69 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 171.668 x 1000000 / [1940.400 x (746.667 - 129.484/3)]
= 125.756 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1940.400/1000.0 + 7x1940.400/1000.0 x √[(1 + 2x1000.0x746.7/(7x1940.400)]
= 129.484 mm
Use As = 1940.400 mm² (철근도심 : 70.000 mm)
1단 : H19 - 4.0 EA + H16 - 4.0 EA (= 1940.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 125.76) - 2.5 x 60.50 = 474.96 mm
300 x (210 / fs) = 300 x (210 / 125.76) = 500.97 mm
Sa는 작은 값인 474.96 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 474.96 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 112.318 x 1000000 / [1588.800 x (650.000 - 109.633/3)]
= 115.239 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x650.0/(7x1588.800)]
= 109.633 mm
Use As = 1588.800 mm² (철근도심 : 50.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 115.24) - 2.5 x 42.00 = 578.36 mm
300 x (210 / fs) = 300 x (210 / 115.24) = 546.69 mm
Sa는 작은 값인 546.69 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 546.69 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 117.442 x 1000000 / [1588.800 x (746.667 - 118.230/3)]
= 104.514 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x746.7/(7x1588.800)]
= 118.230 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 104.51) - 2.5 x 62.00 = 598.49 mm
300 x (210 / fs) = 300 x (210 / 104.51) = 602.79 mm
Sa는 작은 값인 598.49 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 598.49 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 90.990 x 1000000 / [1301.200 x (630.000 - 98.407/3)]
= 117.093 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x630.0/(7x1301.200)]
= 98.407 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 117.09) - 2.5 x 62.00 = 517.54 mm
300 x (210 / fs) = 300 x (210 / 117.09) = 538.03 mm
Sa는 작은 값인 517.54 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 517.54 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 117.693 x 1000000 / [1301.200 x (650.000 - 100.088/3)]
= 146.682 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x650.0/(7x1301.200)]
= 100.088 mm
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 146.68) - 2.5 x 42.00 = 431.88 mm
300 x (210 / fs) = 300 x (210 / 146.68) = 429.50 mm
Sa는 작은 값인 429.50 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 429.50 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 183.202 x 1000000 / [2292.000 x (630.000 - 127.039/3)]
= 136.017 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x2292.000/1000.0 + 7x2292.000/1000.0 x √[(1 + 2x1000.0x630.0/(7x2292.000)]
= 127.039 mm
Use As = 2292.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 8.0 EA (= 2292.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 136.02) - 2.5 x 60.50 = 427.72 mm
300 x (210 / fs) = 300 x (210 / 136.02) = 463.18 mm
Sa는 작은 값인 427.72 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 427.72 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 117.693 x 1000000 / [1301.200 x (650.000 - 100.088/3)]
= 146.682 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x650.0/(7x1301.200)]
= 100.088 mm
Use As = 1301.200 mm² (철근도심 : 50.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 146.68) - 2.5 x 42.00 = 431.88 mm
300 x (210 / fs) = 300 x (210 / 146.68) = 429.50 mm
Sa는 작은 값인 429.50 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 429.50 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 90.990 x 1000000 / [1301.200 x (630.000 - 98.407/3)]
= 117.093 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x630.0/(7x1301.200)]
= 98.407 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 117.09) - 2.5 x 62.00 = 517.54 mm
300 x (210 / fs) = 300 x (210 / 117.09) = 538.03 mm
Sa는 작은 값인 517.54 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 517.54 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 117.442 x 1000000 / [1588.800 x (596.667 - 104.617/3)]
= 131.576 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x596.7/(7x1588.800)]
= 104.617 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.58) - 2.5 x 62.00 = 443.52 mm
300 x (210 / fs) = 300 x (210 / 131.58) = 478.81 mm
Sa는 작은 값인 443.52 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 443.52 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 25.525 x 1000000 / [506.800 x (500.000 - 56.120/3)]
= 104.645 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x506.800/1000.0 + 7x506.800/1000.0 x √[(1 + 2x1000.0x500.0/(7x506.800)]
= 56.120 mm
Use As = 506.800 mm² (철근도심 : 50.000 mm)
1단 : H13 - 4.0 EA (= 506.800 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 13/2 = 43.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 104.65) - 2.5 x 43.50 = 643.79 mm
300 x (210 / fs) = 300 x (210 / 104.65) = 602.03 mm
Sa는 작은 값인 602.03 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 602.03 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 30.332 x 1000000 / [794.400 x (480.000 - 67.715/3)]
= 83.471 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x480.0/(7x794.400)]
= 67.715 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 83.47) - 2.5 x 62.00 = 788.44 mm
300 x (210 / fs) = 300 x (210 / 83.47) = 754.75 mm
Sa는 작은 값인 754.75 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 754.75 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 90.990 x 1000000 / [1301.200 x (480.000 - 84.844/3)]
= 154.804 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x480.0/(7x1301.200)]
= 84.844 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.80) - 2.5 x 62.00 = 353.71 mm
300 x (210 / fs) = 300 x (210 / 154.80) = 406.97 mm
Sa는 작은 값인 353.71 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 353.71 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 117.442 x 1000000 / [1588.800 x (596.667 - 104.617/3)]
= 131.576 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1588.800/1000.0 + 7x1588.800/1000.0 x √[(1 + 2x1000.0x596.7/(7x1588.800)]
= 104.617 mm
Use As = 1588.800 mm² (철근도심 : 70.000 mm)
1단 : H16 - 8.0 EA (= 1588.800 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 131.58) - 2.5 x 62.00 = 443.52 mm
300 x (210 / fs) = 300 x (210 / 131.58) = 478.81 mm
Sa는 작은 값인 443.52 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 443.52 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 25.525 x 1000000 / [506.800 x (500.000 - 56.120/3)]
= 104.645 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x506.800/1000.0 + 7x506.800/1000.0 x √[(1 + 2x1000.0x500.0/(7x506.800)]
= 56.120 mm
Use As = 506.800 mm² (철근도심 : 50.000 mm)
1단 : H13 - 4.0 EA (= 506.800 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 13/2 = 43.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 104.64) - 2.5 x 43.50 = 643.79 mm
300 x (210 / fs) = 300 x (210 / 104.64) = 602.04 mm
Sa는 작은 값인 602.04 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 602.04 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 30.332 x 1000000 / [794.400 x (480.000 - 67.715/3)]
= 83.471 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x794.400/1000.0 + 7x794.400/1000.0 x √[(1 + 2x1000.0x480.0/(7x794.400)]
= 67.715 mm
Use As = 794.400 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA (= 794.400 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 83.47) - 2.5 x 62.00 = 788.44 mm
300 x (210 / fs) = 300 x (210 / 83.47) = 754.75 mm
Sa는 작은 값인 754.75 mm 를 적용
S = 1000.00 / 4.00 Ea = 250.00 ≤ Sa (= 754.75 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 90.990 x 1000000 / [1301.200 x (480.000 - 84.844/3)]
= 154.804 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1301.200/1000.0 + 7x1301.200/1000.0 x √[(1 + 2x1000.0x480.0/(7x1301.200)]
= 84.844 mm
Use As = 1301.200 mm² (철근도심 : 70.000 mm)
1단 : H16 - 4.0 EA + H13 - 4.0 EA (= 1301.200 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.80) - 2.5 x 62.00 = 353.71 mm
300 x (210 / fs) = 300 x (210 / 154.80) = 406.97 mm
Sa는 작은 값인 353.71 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 353.71 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 3.475 m
- fy = 400 MPa
- 부재두께(T) = 0.70 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 3.475 / 28
T = 0.124 m < 0.700 m -----------> O.K

## 기초 지지력 검토
24. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  |  | = | 355.128 |  | / | 7.5 |  | = | 47.35 |  | kN/m²
|  |  | - 상부연직하중 |  |  |  | = | 152 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  |  | 10 |  | kN/m²
- 암거 내부 활하중
t = 0 mm (암거내부 포장두께)
T = 700 mm (하부 슬래브 두께)
b' = 0.500 + 2 × ( 0.700 + 0.000 ) × cot 45°
= 1.900 m
a' = 0.200 + 2 × ( 0.700 + 0.000 ) × cot 45°
= 1.600 m
|  |  |  | Qz = 96.0 / ( 1.900 × 1.600 ) = | [7 empty] | 31.579 |  | kN/m²
3) 최대 지반 반력
|  |  | Qmax |  | = | 47.35 |  | + | 152 |  | + | 10 |  | + | 31.579
[5 empty] | = | 240.929 |  | kN/m²

## 주철근 조립도
25. 주철근 조립도