## 표지
P2-6A 구조계산서
| ▣ 구조형식 |  | : | 지중 2 련 암거
( 내공 : 2@(3M ⅹ 3M) )
| ▣ 토 피(FH) |  | = | 2.00 m
| ▣ 지반 조건 |  | : | 토사
[5 empty] | 1. | 설계요약표
[5 empty] | 2. | 설계조건
[5 empty] | 3. | 단면가정
[5 empty] | 4. | 해석모델 및 단면제원(상시)
[5 empty] | 5. | 해석모델 및 단면제원(붕괴방지)
[5 empty] | 6. | 지반반력계수(상시)
[5 empty] | 7. | 지반반력계수(붕괴방지)
[5 empty] | 8. | 하중계산(상시)
[5 empty] | 9. | 하중계산(붕괴방지)
[5 empty] | 10. | 하중재하도(상시)
[5 empty] | 11. | 하중재하도(붕괴방지)
[5 empty] | 12. | 하중계수 및 하중조합
[5 empty] | 13. | INPUT DATA(상시)
[5 empty] | 14. | INPUT DATA(붕괴방지)
[5 empty] | 15. | OUTPUT DATA(상시)
[5 empty] | 16. | OUTPUT DATA(붕괴방지)
[5 empty] | 17. | 단면력정리(상시)
[5 empty] | 18. | 단면력정리(붕괴방지)
[5 empty] | 19. | 단면검토 및 철근량 산정
[5 empty] | 20. | 수평철근 검토
[5 empty] | 21. | 거더,기둥,내측벽체 검토
[5 empty] | 22. | 절점부 검토
[5 empty] | 23. | 사용성 검토
[5 empty] | 24. | 기초 지지력 검토
[5 empty] | 25. | 주철근 조립도

## 설계요약표
1. 설계 요약표
P2-6A (토피=2.0M)
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 2.0m
안정(지지력)검토 | Qmax = 169.396 kN/m²
단면 위치 | 내구성검토 |  |  | 단 면 검 토 | [13 empty] | 절 점 부 보 강
| 균열검토 |  |  | 휨 검 토 | [6 empty] | 전 단 검 토
| 철근간격 mm | 최대간격 mm |  | 사용철근 | Mu kN.m |  | ΦMn kN.m |  | S.F |  | 사용철근 |  | Vu kN |  | ΦVn kN |  | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 150 | 512.441 |  | H16 - 3.3EA + H13 - 3.3EA | 67.481 |  | 123.887 |  | 1.84 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.575 | 0.637
상부슬래브 : 제 1경간 중앙부 | 150 | 399.539 |  | H13 - 6.7EA | 56.614 |  | 83.778 |  | 1.48 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 지점부 | 150 | 324.98 |  | H16 - 6.7EA | 105.707 |  | 150.212 |  | 1.42 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 제 2경간 중앙부 | 150 | 399.539 |  | H13 - 6.7EA | 56.614 |  | 83.778 |  | 1.48 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
상부슬래브 : 단지점부(우측) | 150 | 512.439 |  | H16 - 3.3EA + H13 - 3.3EA | 67.481 |  | 123.887 |  | 1.84 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 0.575 | 0.637
하부슬래브 : 단지점부(좌측) | 150 | 326.365 |  | H16 - 3.3EA + H13 - 3.3EA | 70.653 |  | 99.309 |  | 1.41 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 1.088 | 0.637 | H19 @300 - 3.3EA
하부슬래브 : 제 1경간 중앙부 | 150 | 349.902 |  | H13 - 6.7EA | 60.359 |  | 83.778 |  | 1.39 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 지점부 | 150 | 293.212 |  | H19 - 3.3EA + H16 - 3.3EA | 111.561 |  | 145.223 |  | 1.3 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 제 2경간 중앙부 | 150 | 349.902 |  | H13 - 6.7EA | 60.359 |  | 83.778 |  | 1.39 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
하부슬래브 : 단지점부(우측) | 150 | 326.365 |  | H16 - 3.3EA + H13 - 3.3EA | 70.653 |  | 99.309 |  | 1.41 |  | ∴ 전단보강 불필요 | [5 empty] | O.K | 1.088 | 0.637 | H19 @300 - 3.3EA
좌측벽체 : 상부 | 150 | 413.421 |  | H16 - 3.3EA + H13 - 3.3EA | 67.481 |  | 141.908 |  | 2.1 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부 | 300 | 553.095 |  | H16 - 3.3EA | 30.46 |  | 130.2 |  | 4.27 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 중앙부(부모멘트) | 300 | 415.794 |  | H16 - 3.3EA | 32.946 |  | 113.744 |  | 3.45 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
좌측벽체 : 하부 | 150 | 237.758 |  | H16 - 3.3EA + H13 - 3.3EA | 70.653 |  | 106.794 |  | 1.51 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 상부 | 150 | 413.42 |  | H16 - 3.3EA + H13 - 3.3EA | 67.481 |  | 141.908 |  | 2.1 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부 | 300 | 553.096 |  | H16 - 3.3EA | 30.46 |  | 130.2 |  | 4.27 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 중앙부(부모멘트) | 300 | 415.791 |  | H16 - 3.3EA | 32.946 |  | 113.744 |  | 3.45 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
우측벽체 : 하부 | 150 | 237.758 |  | H16 - 3.3EA + H13 - 3.3EA | 70.653 |  | 106.794 |  | 1.51 |  | ∴ 전단보강 불필요 | [5 empty] | O.K
기둥단면검토
기둥 위치 | 기둥 형태 |  | 사용 철근 |  |  | e |  | eb |  | Pu |  | ΦPn |  | Mu |  | ΦMn |  | 비 고
[6 empty] | (mm) |  | (mm) |  | (kN) |  | (kN) |  | (kN.m) |  | (kN.m)
P1 | 벽 체 |  | H13 |  |  | 0 |  | 99.237 |  | 383.025 |  | 4036.132 |  | 0 |  | 0.001 |  | 축력 최대시
[6 empty] | 9.882 |  | 99.237 |  | 226.591 |  | 4036.132 |  | 2.239 |  | 39.887 |  | 모멘트 최대시

## 설계조건
2. 설계조건
1) 구조형식
- 지중 2 련 암거 ( 내공 : 2@(3M ⅹ 3M), 사각 : 90°)
2) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
3) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 24 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 27000 |  |  | MPa
| - 철근(SD400) |  | (fy) |  | = | 400 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
4) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
5) 지진계수
| - 내진등급 : | II등급 (위험도 계수 : 1.000)
| - 지진구역 : | I 구역 (지진구역계수 : 0.110)
| - 지반종류 : | Sd
- 붕괴방지수준
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 15.486 |  | kN/m² |  | (∵ 토피 : | 2 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 한국콘크리트학회(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)
| - 도시철도 내진설계기준 |  |  |  |  | : 건설교통부(2005)

## 단면가정
3. 단면 가정

## 해석모델 및 단면제원(상시)
4. 해석모델 및 단면제원 (상시)
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.350 × 1.000 = 0.350 |  |  |  | 0.00357 |  | 1~20,26~37
| 2 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 21~25,38~43
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.15 | 0.175 | 29 |  | 5.1 |  | 3.525
| 2 |  | 0.3 | 0.175 | 30 |  | 3.88 |  | 3.525
| 3 |  | 0.58 | 0.175 | 31 |  | 3.6 |  | 3.525
| 4 |  | 0.7 | 0.175 | 32 |  | 3.45 |  | 3.525
| 5 |  | 1.25 | 0.175 | 33 |  | 3.3 |  | 3.525
| 6 |  | 1.8 | 0.175 | 34 |  | 3.02 |  | 3.525
| 7 |  | 2.35 | 0.175 | 35 |  | 1.8 |  | 3.525
| 8 |  | 2.9 | 0.175 | 36 |  | 0.58 |  | 3.525
| 9 |  | 3.02 | 0.175 | 37 |  | 0.3 |  | 3.525
| 10 |  | 3.3 | 0.175 | 38 |  | 0.15 |  | 3.525
| 11 |  | 3.45 | 0.175 | 39 |  | 0.15 |  | 3.35
| 12 |  | 3.6 | 0.175 | 40 |  | 0.15 |  | 3.12
| 13 |  | 3.88 | 0.175 | 41 |  | 0.15 |  | 0.58
| 14 |  | 4 | 0.175 | 42 |  | 0.15 |  | 0.35
| 15 |  | 4.55 | 0.175 | 43 |  | 0.15 |  | -0.325
| 16 |  | 5.1 | 0.175 | 44 |  | 0.7 |  | -0.325
| 17 |  | 5.65 | 0.175 | 45 |  | 1.25 |  | -0.325
| 18 |  | 6.2 | 0.175 | 46 |  | 1.8 |  | -0.325
| 19 |  | 6.32 | 0.175 | 47 |  | 2.35 |  | -0.325
| 20 |  | 6.6 | 0.175 | 48 |  | 2.9 |  | -0.325
| 21 |  | 6.75 | 0.175 | 49 |  | 3.45 |  | -0.325
| 22 |  | 6.75 | 0.35 | 50 |  | 4 |  | -0.325
| 23 |  | 6.75 | 0.58 | 51 |  | 4.55 |  | -0.325
| 24 |  | 6.75 | 3.12 | 52 |  | 5.1 |  | -0.325
| 25 |  | 6.75 | 3.35 | 53 |  | 5.65 |  | -0.325
| 26 |  | 6.75 | 3.525 | 54 |  | 6.2 |  | -0.325
| 27 |  | 6.6 | 3.525 | 55 |  | 6.75 |  | -0.325
| 28 |  | 6.32 | 3.525

## 해석모델 및 단면제원(붕괴방지)
5. 해석모델 및 단면제원 (지진시)
1) Modeling
지중구조물의 경우 구조물의 겉보기 중량이 주변지반의 중량과 비교하여 가볍거나 혹은 같은 정도이고
지중구조물의 대부분이 주위가 지반으로 둘러 싸여 있음으로 인하여 발산감쇠(Radiation damping)가 커서
진동이 발생하여도 짧은 시간 안에 진정되는 특성을 갖고있다. 이 때문에 지중구조물의 경우 관성력에
의한 응답의 증폭은 크지 않으며, 주변 지반의 움직임에 따라서 거동하게 된다. 따라서, 지중구조물에
발생하는 응력은 관성력에 의한 영향보다도 구조물 주변지반의 상대적인 변위에 의해 크게 영향을 받게
된다.이와같은 사실에 근거하여, 지진시에 발생하는 지반의 변위를 구조물에 작용시켜서 지중구조물에
발생하는 응력을 정적으로 구하는 방법인 응답변위법을 적용한다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.350 × 1.000 = 0.350 |  |  |  | 0.00357 |  | 1~20,31~50
| 2 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 21~30,51~61
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.15 | 0.175 | 51 |  | 0.15 |  | 3.525
| 2 |  | 0.3 | 0.175 | 52 |  | 0.15 |  | 3.35
| 3 |  | 0.58 | 0.175 | 53 |  | 0.15 |  | 3.12
| 4 |  | 0.7 | 0.175 | 54 |  | 0.15 |  | 2.967
| 5 |  | 1.25 | 0.175 | 55 |  | 0.15 |  | 2.408
| 6 |  | 1.8 | 0.175 | 56 |  | 0.15 |  | 1.85
| 7 |  | 2.35 | 0.175 | 57 |  | 0.15 |  | 1.292
| 8 |  | 2.9 | 0.175 | 58 |  | 0.15 |  | 0.733
| 9 |  | 3.02 | 0.175 | 59 |  | 0.15 |  | 0.58
| 10 |  | 3.3 | 0.175 | 60 |  | 0.15 |  | 0.35
| 11 |  | 3.45 | 0.175 | 61 |  | 0.15 |  | -0.325
| 12 |  | 3.6 | 0.175 | 62 |  | 0.7 |  | -0.325
| 13 |  | 3.88 | 0.175 | 63 |  | 1.25 |  | -0.325
| 14 |  | 4 | 0.175 | 64 |  | 1.8 |  | -0.325
| 15 |  | 4.55 | 0.175 | 65 |  | 2.35 |  | -0.325
| 16 |  | 5.1 | 0.175 | 66 |  | 2.9 |  | -0.325
| 17 |  | 5.65 | 0.175 | 67 |  | 3.45 |  | -0.325
| 18 |  | 6.2 | 0.175 | 68 |  | 4 |  | -0.325
| 19 |  | 6.32 | 0.175 | 69 |  | 4.55 |  | -0.325
| 20 |  | 6.6 | 0.175 | 70 |  | 5.1 |  | -0.325
| 21 |  | 6.75 | 0.175 | 71 |  | 5.65 |  | -0.325
| 22 |  | 6.75 | 0.35 | 72 |  | 6.2 |  | -0.325
| 23 |  | 6.75 | 0.58 | 73 |  | 6.75 |  | -0.325
| 24 |  | 6.75 | 0.733 | 74 |  | 7.25 |  | 0.175
| 25 |  | 6.75 | 1.292 | 75 |  | 7.25 |  | 0.733
| 26 |  | 6.75 | 1.85 | 76 |  | 7.25 |  | 1.292
| 27 |  | 6.75 | 2.408 | 77 |  | 7.25 |  | 1.85
| 28 |  | 6.75 | 2.967 | 78 |  | 7.25 |  | 2.408
| 29 |  | 6.75 | 3.12 | 79 |  | 7.25 |  | 2.967
| 30 |  | 6.75 | 3.35 | 80 |  | 7.25 |  | 3.525
| 31 |  | 6.75 | 3.525 | 81 |  | 6.75 |  | 4.025
| 32 |  | 6.6 | 3.525 | 82 |  | 6.2 |  | 4.025
| 33 |  | 6.32 | 3.525 | 83 |  | 5.65 |  | 4.025
| 34 |  | 6.2 | 3.525 | 84 |  | 5.1 |  | 4.025
| 35 |  | 5.65 | 3.525 | 85 |  | 4.55 |  | 4.025
| 36 |  | 5.1 | 3.525 | 86 |  | 4 |  | 4.025
| 37 |  | 4.55 | 3.525 | 87 |  | 3.45 |  | 4.025
| 38 |  | 4 | 3.525 | 88 |  | 2.9 |  | 4.025
| 39 |  | 3.88 | 3.525 | 89 |  | 2.35 |  | 4.025
| 40 |  | 3.6 | 3.525 | 90 |  | 1.8 |  | 4.025
| 41 |  | 3.45 | 3.525 | 91 |  | 1.25 |  | 4.025
| 42 |  | 3.3 | 3.525 | 92 |  | 0.7 |  | 4.025
| 43 |  | 3.02 | 3.525 | 93 |  | 0.15 |  | 4.025
| 44 |  | 2.9 | 3.525 | 94 |  | -0.35 |  | 3.525
| 45 |  | 2.35 | 3.525 | 95 |  | -0.35 |  | 2.967
| 46 |  | 1.8 | 3.525 | 96 |  | -0.35 |  | 2.408
| 47 |  | 1.25 | 3.525 | 97 |  | -0.35 |  | 1.85
| 48 |  | 0.7 | 3.525 | 98 |  | -0.35 |  | 1.292
| 49 |  | 0.58 | 3.525 | 99 |  | -0.35 |  | 0.733
| 50 |  | 0.3 | 3.525 | 100 |  | -0.35 |  | 0.175

## 지반반력계수(상시)
6. 지반반력계수 (상시)
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 15
|  | Eo | = | 2800 × N |  | = | 42000 | kN/m²
|  | Bv | = | √( B × B ) |  | = | √( 6.900 × 6.900 ) |  |  | = | 6.9 | m (L > B)
|  | Kvo | = | 1 / 0.3 × 1 × 42000 |  | = | 140000 | kN/m³
|  | Kv | = | 140000.000 × ( 6.900 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 13330.062 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.300/2 + 0.550/2) = 5665 kN/m |  |  |  |  | 1,21
| Kv2 |  |  | Kvⅹ(0.550/2 + 0.550/2) = 7332 kN/m |  |  |  |  | 4~8,11,14~18
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 1

## 지반반력계수(붕괴방지)
7. 지반반력계수 (붕괴방지)
1) 지반탄성계수의 산정
※ 성토재 (심도 : 3.350m ~ 0.000m)
- Vo (초기상태 전단파 속도) = 80 × N^(1/3) = 80 × 15^(1/3) = 197.3 m/sec
- Vs (붕괴방지수준의 전단파 속도) =0.5 × Vo = 0.5 × 197.3 = 98.7 m/sec
- Gd (전단탄성계수) = w / g × Vs² ( w : 흙의 단위중량, g : 중력계수 )
= 19 / 9.810 × 98.7² = 18868.0 kN/m²
- Ed (탄성계수) = 2 × ( 1 + ν ) × Gd ( ν : 흙의 포아슨 비 )
= 2 × ( 1 + 0.4 ) × 18868.0 = 52830.4 kN/m²
2) 지반반력계수의 산정
① 상부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 6.900 × 6.900 ) |  |  |  |  | = | 6.9 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 6.900 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 33534.88 |  |  | kN/m³
② 상부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 33534.880 |  |  |  |  | = | 11178.29 |  |  | kN/m³
③ 하부슬래브의 연직방향 지반반력계수 - (제0토층,성토재)
|  |  | Bv | = | √( B × B ) |  |  |  | = | √( 6.900 × 6.900 ) |  |  |  |  | = | 6.9 |  |  | m
|  |  | Kvo | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kv | = | 352202.670 × ( 6.900 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 33534.88 |  |  | kN/m³
④ 하부슬래브의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Ksb | = | λ × Kv |  |  |  | = | 1/3.0 × 33534.880 |  |  |  |  | = | 11178.29 |  |  | kN/m³
⑤ 측벽의 수평방향 지반반력계수 - (제0토층,성토재)
|  |  | Bh | = | √( H × H ) |  |  |  | = | √( 3.700 × 3.700 ) |  |  |  |  | = | 3.7 |  |  | m
|  |  | Kho | = | 1 / 0.3 × α × Ed |  |  |  | = | 1 / 0.3 × 2 × 52830.4 |  |  |  |  | = | 352202.67 |  |  | kN/m³
|  |  | Kh | = | 352202.670 × ( 3.700 / 0.3 )^( -3 / 4 ) | [9 empty] | = | 53515.83 |  |  | kN/m³
⑥ 측벽의 전단 지반반력계수 - (제0토층,성토재)
|  |  | Kss | = | λ × Kh |  |  |  | = | 1/3.0 × 53515.830 |  |  |  |  | = | 17838.61 |  |  | kN/m³
⑦ 적용 지반반력계수
- 상부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.550/2 + 0.300/2) = 14252 kN/m | [8 empty] | 31,51
|  | Ksb1 |  |  | Ksbⅹ(0.550/2 + 0.300/2) = 4751 kN/m
|  | Kv2 |  |  | Kvⅹ(0.550/2 + 0.550/2) = 18444 kN/m | [8 empty] | 34~38,41,44~48
|  | Ksb2 |  |  | Ksbⅹ(0.550/2 + 0.550/2) = 6148 kN/m
- 측벽
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kh1 |  |  | Khⅹ(0.558/2 + 0.350/2) = 24296 kN/m | [8 empty] | 1,21,31,51
|  | Kss1 |  |  | Kssⅹ(0.558/2 + 0.350/2) = 8099 kN/m
|  | Kh2 |  |  | Khⅹ(0.558/2 + 0.558/2) = 29862 kN/m | [8 empty] | 24~28,54~58
|  | Kss2 |  |  | Kssⅹ(0.558/2 + 0.558/2) = 9954 kN/m
- 하부슬래브
|  | 지반반력계수 |  |  | 계 산 식 | [8 empty] | 해당 절점
|  | Kv1 |  |  | Kvⅹ(0.300/2 + 0.550/2) = 14252 kN/m | [8 empty] | 1,21
|  | Ksb1 |  |  | Ksbⅹ(0.300/2 + 0.550/2) = 4751 kN/m
|  | Kv2 |  |  | Kvⅹ(0.550/2 + 0.550/2) = 18444 kN/m | [8 empty] | 4~8,11,14~18
|  | Ksb2 |  |  | Ksbⅹ(0.550/2 + 0.550/2) = 6148 kN/m
3) 지반계수 산정
① 위험도 계수 (I)
- 내진성능 목표
|  | 설 계 지 진 | 성능기준 재현주기 | [5 empty] | 기 능 수 행 |  |  |  |  | 붕 괴 방 지
|  |  | 50년 | [5 empty] | II 등급
|  |  | 100년 | [5 empty] | I 등급
|  |  | 200년 | [5 empty] | 특 등급
|  |  | 500년 | [10 empty] | II 등급
|  |  | 1000년 | [10 empty] | I 등급
|  |  | 2400년 | [10 empty] | 특 등급
- 위험도 계수
|  | 재현주기 (년) |  |  |  | 50 |  | 100 |  |  | 200 |  | 500 |  | 1000 |  |  | 2400
|  | 위험도계수,I |  |  |  | 0.4 |  | 0.57 |  |  | 0.73 |  | 1 |  | 1.4 |  |  | 2
② 지진구역 계수(Z)
- 지진구역 구분
|  | 지진구역 |  |  |  | 행정구역 | [10 empty] | 구역계수, Z
|  | I |  |  |  | 시 | 서울특별시, 인천광역시, 대전광역시, 부산광역시, 대구광역시, 울산광역시, 광주광역시 | [9 empty] | 0.11
[6 empty] | 도 | 경기도, 강원도 남부, 충청북도, 충청남도, 경상북도, 경상남도, 전라북도, 전라남도 북동부
|  | II |  |  |  | 도 | 강원도 북부, 전라남도 남서부, 제주도 | [9 empty] | 0.07
③ 설계 지반 종류
|  | 지반 분류 |  | 지반종류의 호칭 |  |  |  | 상부 30m 에 대한 평균 지반 특성
[8 empty] | 전단파 속도 Z(m/s) |  |  |  | 표준관입시험 N(Nch) (blow/foot) |  |  |  | 비배수전단강도 Su(kPa)
|  | Sa |  | 경암지반 |  |  |  | 1500초과 |  |  |  | - |  |  |  | -
|  | Sb |  | 보통암지반 |  |  |  | 760에서 1500
|  | Sc |  | 매우 조밀한 토사지반 또는 연암지반 |  |  |  | 360에서 760 |  |  |  | > 50 |  |  |  | > 100
|  | Sd |  | 단단한 토사지반 |  |  |  | 180에서 360 |  |  |  | 15에서 50 |  |  |  | 50에서 100
|  | Se |  | 연약한 토사지반 |  |  |  | 180미만 |  |  |  | < 15 |  |  |  | < 50
|  | Sf |  | 부지 고유의 특성평가가 요구되는 지반
④ 지진계수 Ca, Cv
|  | 지역계수 |  |  |  | 지반종류 |  |  |  |  | 지진계수
[11 empty] | Ca |  |  |  | Cv
|  | 1 |  |  |  | Sa |  |  |  |  | 0.09 |  |  |  | 0.09
[6 empty] | Sb |  |  |  |  | 0.11 |  |  |  | 0.11
[6 empty] | Sc |  |  |  |  | 0.13 |  |  |  | 0.18
[6 empty] | Sd |  |  |  |  | 0.16 |  |  |  | 0.23
[6 empty] | Se |  |  |  |  | 0.22 |  |  |  | 0.37
|  | 2 |  |  |  | Sa |  |  |  |  | 0.05 |  |  |  | 0.05
[6 empty] | Sb |  |  |  |  | 0.07 |  |  |  | 0.07
[6 empty] | Sc |  |  |  |  | 0.08 |  |  |  | 0.11
[6 empty] | Sd |  |  |  |  | 0.11 |  |  |  | 0.16
[6 empty] | Se |  |  |  |  | 0.17 |  |  |  | 0.23
⑤ 설계 수평 지진계수 (KH)
- 지표면의 설계 수평지진 계수(붕괴방지수준) : KH = I × Ca = 1.00 × 0.16 = 0.160

## 하중계산(상시)
8. 하 중 계 산 (상시)
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우 )
|  | - 토 사 |  |  |  |  | : | 2.00 × 19.00 |  |  |  |  | = | 38 |  | kN/m²
[12 empty] | ∴ Total Wd1 | = | 38 |  | kN/m²
3) 활 하 중
- 노면 활하중(DB-24 적용)
① 충격계수
|  | 토피두께 D(m) |  |  |  | 0.15 ≤ D ≤ 1 |  |  | 1 < D ≤ 2 |  |  | 2 < D ≤ 3 | 3 < D
|  | 충격계수 i |  |  |  | 0.3 |  |  | 0.2 |  |  | 0.1 | 0
i = 0.2 ( 토피 D = 2.00 m )
② 상부 슬래브에 작용하는 하중 (Wl1)
- P = 2 × Pr / 3.0 = 2 × 96.0 / 3.0 = 64.0 kN/m
- Wl1 = 2 × P × (1 + i) × (Bo - D - 0.1) / Bo²
= 2 × 64.0 × (1 + 0.2) × (6.90 - 2.0 - 0.1 ) / 6.90²
= 15.486 kN/m²
③ 측벽에 작용하는 하중 (Wl2)
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  | = | 5 | kN/m²
4) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (2.175 × 19.000) × 0.500 | [9 empty] | = | 20.662 | kN/m²
|  | - Wh2 |  | = | 20.662 + 0.175 × 19.000 × 0.500 | [9 empty] | = | 22.324 | kN/m²
|  | - Wh3 |  | = | 22.324 + 0.230 × 19.000 × 0.500 | [9 empty] | = | 24.509 | kN/m²
|  | - Wh4 |  | = | 24.509 + 2.540 × 19.000 × 0.500 | [9 empty] | = | 48.639 | kN/m²
|  | - Wh5 |  | = | 48.639 + 0.230 × 19.000 × 0.500 | [9 empty] | = | 50.824 | kN/m²
|  | - Wh6 |  | = | 50.824 + 0.175 × 19.000 × 0.500 | [9 empty] | = | 52.487 | kN/m²

## 하중계산(붕괴방지)
9. 하 중 계 산 (붕괴방지)
1) 고유주기(Tg)
|  | 지 반 |  |  | Hi(m) |  | Vsi(m/sec) |  |  |  | γ(kN/m³) |  |  | Tg'(sec)
|  | 성토재 |  |  | 5.35 |  | 197.3 |  |  |  | 19 |  |  | 0.108
|  | 계 | [11 empty] | 0.108
Tg = 1.25 Tg' = 1.25 × 0.108 = 0.135 sec
2) 통제주기(Ts)
Ts = Cv / (2.5 × Ca) = 0.230 / (2.5 × 0.160) = 0.575 sec
To = 0.2 × Ts = 0.2 × 0.575 = 0.115 sec
3) 감쇠율에 대한 보정계수(Cd)
① 성능수준별 감쇠율(h)
- 붕괴방지수준 : h = 0.2
|  | ② 보정계수 | [5 empty] | = | 0.667
| 4) 가속도 응답스펙트럼(Sa) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
- 0 ≤ Tg ＜ To 일때
Sa = [Ca+(2.5×Ca-Ca)/To×Tg]×g×I×Cd
- To ≤ Tg ＜ Ts 일때
Sa = 2.5×Ca×g×I×Cd
= 2.617 m/s²
- Tg ≥ Ts 일때
Sa = Cv×g×I×Cd/Tg
| 5) 속도 응답스펙트럼(Sv) |  |  |  |  | - 붕괴방지수준시(재현주기 500년적용)
Sv = Tg/2π × Sa = 0.135 / 2π × 2.617 = 0.056 m/s
6) 설계응답 응답스펙트럼
7) 상부슬래브 지반변위 하중
|  | - 상부슬래브 심도 | [6 empty] | = | 2.175 |  | m
|  | - 하부슬래브 심도 | [6 empty] | = | 5.525 |  | m
|  | - 기반암 심도(H) | [6 empty] | = | 30 |  | m
U(Zu) = 2 / π²× 0.056 × 0.135 × cos(π× 2.175 / (2 × 30.000)) = 0.001522
U(Zb) = 2 / π²× 0.056 × 0.135 × cos(π× 5.525 / (2 × 30.000)) = 0.001468
Po = Ksb,top × (U(Zu) - U(Zb))
= 11178.290 × (0.001522 - 0.001468) = 0.604 kN/m²
8) 측벽 지반변위 하중
P(z) = Kh × (Uh(z) - Uh(b))
|  | z(m) |  | Kh (kN/m³) |  |  |  | U(Zh) (m) |  |  |  |  | U(Zh) - U(Zb) (m) |  | P(z) (kN/m²)
|  | 2.175 |  | 53515.83 |  |  |  | 0.001522 |  |  |  |  | 5.4e-05 |  | 2.89
|  | 2.35 |  | 53515.83 |  |  |  | 0.00152 |  |  |  |  | 5.2e-05 |  | 2.783
|  | 2.58 |  | 53515.83 |  |  |  | 0.001518 |  |  |  |  | 5e-05 |  | 2.676
|  | 2.733 |  | 53515.83 |  |  |  | 0.001516 |  |  |  |  | 4.8e-05 |  | 2.569
|  | 3.292 |  | 53515.83 |  |  |  | 0.001509 |  |  |  |  | 4.1e-05 |  | 2.194
|  | 3.85 |  | 53515.83 |  |  |  | 0.001501 |  |  |  |  | 3.3e-05 |  | 1.766
|  | 4.408 |  | 53515.83 |  |  |  | 0.001491 |  |  |  |  | 2.3e-05 |  | 1.231
|  | 4.967 |  | 53515.83 |  |  |  | 0.00148 |  |  |  |  | 1.2e-05 |  | 0.642
|  | 5.12 |  | 53515.83 |  |  |  | 0.001477 |  |  |  |  | 9e-06 |  | 0.482
|  | 5.35 |  | 53515.83 |  |  |  | 0.001472 |  |  |  |  | 4e-06 |  | 0.214
|  | 5.525 |  | 53515.83 |  |  |  | 0.001468 |  |  |  |  | 0 |  | 0
9) 주면 전단력
Uh1 = 1 /(π×H) × Sv × Tg × sin(π×Zu/(2 × H))
Uh2 = 1 /(π×H) × Sv × Tg × sin(π×Zb/(2 × H))
Vu = Gd × f'(Uh1) = 18868.000 × 0.000009 = 0.170 kN/m²
Vb = Gd × f'(Uh2) = 18868.000 × 0.000023 = 0.430 kN/m²
Vs = (Vu - Vb) / 2 = (0.170 + 0.430) / 2 = 0.300 kN/m²
10) 구체 관성력
fi = (Ai × rcon'c × KH × (1 - 0.015 × Zi)
① 상부슬래브
fu = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 2.175) = 1.327 kN/m²
② 하부슬래브
fb = 0.350 × 24.500 × 0.160 × (1 - 0.015 × 5.525) = 1.258 kN/m²
③ 중간벽체
fu1 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 2.175) = 1.138 kN/m²
fb1 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.525) = 1.079 kN/m²
④ 측벽
f1 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 2.175) = 1.138 kN/m²
f2 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 2.350) = 1.135 kN/m²
f3 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 2.580) = 1.130 kN/m²
f4 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 2.733) = 1.128 kN/m²
f5 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.292) = 1.118 kN/m²
f6 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 3.850) = 1.108 kN/m²
f7 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 4.408) = 1.098 kN/m²
f8 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 4.967) = 1.088 kN/m²
f9 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.120) = 1.086 kN/m²
f10 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.350) = 1.082 kN/m²
f11 = 0.300 × 24.500 × 0.160 × (1 - 0.015 × 5.525) = 1.079 kN/m²

## 하중재하도(상시)
10. 하중 재하 (상시)
1) CASE1 - 구체자중
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 활하중 만재하
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 수평토압 (양측, 지하수 없는경우)

## 하중재하도(붕괴방지)
11. 하중 재하 (붕괴방지)
1) CASE1 - 상부 슬래브에 작용하는 지반변위하중
2) CASE2 - 측벽에 작용하는 지반변위하중
3) CASE3 - 주면전단력
4) CASE4 - 관성력

## 하중계수 및 하중조합
12. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 1.000, h = 2.000 m
1) 극한하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.6 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.6 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.6 | 1.6 | 0.8 | 0.8
2) 극한하중 기둥최대편심 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1.2 | 1.6 | 1.6 | 1.6 | 1.6
| 2 |  | 0.9 | 1.6 |  | 1.6 | 1.6
| 3 |  | 1.2 | 1.6 | 1.6 | 0.8 | 0.8
3) 사용하중 검토시
| 구분 |  | 고정하중 |  | 활하중 | 수평하중 | 토압
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 1 | 1 | 1 | 1
| 2 |  | 1 | 1 |  | 1 | 1
| 3 |  | 1 | 1 | 1 | 0.5 | 0.5
4) 지진시 (붕괴방지수준)
| 구분 |  | 고정하중 |  | 활하중 | 토압 | 지진하중
|  |  | 구체자중 | 지하수 無 | 만재하
|  |  | 1 | 2 | 3 | 4 | 5
| 1 |  | 1 | 1 | 1 | 1 | 1

## INPUT(상시)
13. INPUT DATA (상시)
| SYSTEM | NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | DOF=U1 KE=5665.28 CE=0.99999 K=5665.28 OPEN=0
NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005
| JOINT | DOF=U1 KE=7331.53 CE=0.99999 K=7331.53 OPEN=0
1 X= 0.150 Y= 0.000 Z= 0.175
| 2 X= 0.300 Y= 0.000 Z= 0.175 | FRAME SECTION
| 3 X= 0.580 Y= 0.000 Z= 0.175 | NAME=1 MAT=CONC SH=R T=0.35, 1
| 4 X= 0.700 Y= 0.000 Z= 0.175 | NAME=2 MAT=CONC SH=R T=0.3, 1
5 X= 1.250 Y= 0.000 Z= 0.175
| 6 X= 1.800 Y= 0.000 Z= 0.175 | FRAME
| 7 X= 2.350 Y= 0.000 Z= 0.175 | 1 J= 1, 2 SEC=1 NSEG=1 ANG=180
| 8 X= 2.900 Y= 0.000 Z= 0.175 | 2 J= 2, 3 SEC=1 NSEG=1 ANG=180
| 9 X= 3.020 Y= 0.000 Z= 0.175 | 3 J= 3, 4 SEC=1 NSEG=1 ANG=180
| 10 X= 3.300 Y= 0.000 Z= 0.175 | 4 J= 4, 5 SEC=1 NSEG=2 ANG=180
| 11 X= 3.450 Y= 0.000 Z= 0.175 | 5 J= 5, 6 SEC=1 NSEG=2 ANG=180
| 12 X= 3.600 Y= 0.000 Z= 0.175 | 6 J= 6, 7 SEC=1 NSEG=2 ANG=180
| 13 X= 3.880 Y= 0.000 Z= 0.175 | 7 J= 7, 8 SEC=1 NSEG=2 ANG=180
| 14 X= 4.000 Y= 0.000 Z= 0.175 | 8 J= 8, 9 SEC=1 NSEG=1 ANG=180
| 15 X= 4.550 Y= 0.000 Z= 0.175 | 9 J= 9, 10 SEC=1 NSEG=1 ANG=180
| 16 X= 5.100 Y= 0.000 Z= 0.175 | 10 J= 10, 11 SEC=1 NSEG=1 ANG=180
| 17 X= 5.650 Y= 0.000 Z= 0.175 | 11 J= 11, 12 SEC=1 NSEG=1 ANG=180
| 18 X= 6.200 Y= 0.000 Z= 0.175 | 12 J= 12, 13 SEC=1 NSEG=1 ANG=180
| 19 X= 6.320 Y= 0.000 Z= 0.175 | 13 J= 13, 14 SEC=1 NSEG=1 ANG=180
| 20 X= 6.600 Y= 0.000 Z= 0.175 | 14 J= 14, 15 SEC=1 NSEG=2 ANG=180
| 21 X= 6.750 Y= 0.000 Z= 0.175 | 15 J= 15, 16 SEC=1 NSEG=2 ANG=180
| 22 X= 6.750 Y= 0.000 Z= 0.350 | 16 J= 16, 17 SEC=1 NSEG=2 ANG=180
| 23 X= 6.750 Y= 0.000 Z= 0.580 | 17 J= 17, 18 SEC=1 NSEG=2 ANG=180
| 24 X= 6.750 Y= 0.000 Z= 3.120 | 18 J= 18, 19 SEC=1 NSEG=1 ANG=180
| 25 X= 6.750 Y= 0.000 Z= 3.350 | 19 J= 19, 20 SEC=1 NSEG=1 ANG=180
| 26 X= 6.750 Y= 0.000 Z= 3.525 | 20 J= 20, 21 SEC=1 NSEG=1 ANG=180
| 27 X= 6.600 Y= 0.000 Z= 3.525 | 21 J= 21, 22 SEC=2 NSEG=1 ANG=0
| 28 X= 6.320 Y= 0.000 Z= 3.525 | 22 J= 22, 23 SEC=2 NSEG=1 ANG=0
| 29 X= 5.100 Y= 0.000 Z= 3.525 | 23 J= 23, 24 SEC=2 NSEG=4 ANG=0
| 30 X= 3.880 Y= 0.000 Z= 3.525 | 24 J= 24, 25 SEC=2 NSEG=1 ANG=0
| 31 X= 3.600 Y= 0.000 Z= 3.525 | 25 J= 25, 26 SEC=2 NSEG=1 ANG=0
| 32 X= 3.450 Y= 0.000 Z= 3.525 | 26 J= 26, 27 SEC=1 NSEG=1 ANG=0
| 33 X= 3.300 Y= 0.000 Z= 3.525 | 27 J= 27, 28 SEC=1 NSEG=1 ANG=0
| 34 X= 3.020 Y= 0.000 Z= 3.525 | 28 J= 28, 29 SEC=1 NSEG=4 ANG=0
| 35 X= 1.800 Y= 0.000 Z= 3.525 | 29 J= 29, 30 SEC=1 NSEG=4 ANG=0
| 36 X= 0.580 Y= 0.000 Z= 3.525 | 30 J= 30, 31 SEC=1 NSEG=1 ANG=0
| 37 X= 0.300 Y= 0.000 Z= 3.525 | 31 J= 31, 32 SEC=1 NSEG=1 ANG=0
| 38 X= 0.150 Y= 0.000 Z= 3.525 | 32 J= 32, 33 SEC=1 NSEG=1 ANG=0
| 39 X= 0.150 Y= 0.000 Z= 3.350 | 33 J= 33, 34 SEC=1 NSEG=1 ANG=0
| 40 X= 0.150 Y= 0.000 Z= 3.120 | 34 J= 34, 35 SEC=1 NSEG=4 ANG=0
| 41 X= 0.150 Y= 0.000 Z= 0.580 | 35 J= 35, 36 SEC=1 NSEG=4 ANG=0
| 42 X= 0.150 Y= 0.000 Z= 0.350 | 36 J= 36, 37 SEC=1 NSEG=1 ANG=0
| 43 X= 0.150 Y= 0.000 Z= -0.325 | 37 J= 37, 38 SEC=1 NSEG=1 ANG=0
| 44 X= 0.700 Y= 0.000 Z= -0.325 | 38 J= 38, 39 SEC=2 NSEG=1 ANG=180
| 45 X= 1.250 Y= 0.000 Z= -0.325 | 39 J= 39, 40 SEC=2 NSEG=1 ANG=180
| 46 X= 1.800 Y= 0.000 Z= -0.325 | 40 J= 40, 41 SEC=2 NSEG=4 ANG=180
| 47 X= 2.350 Y= 0.000 Z= -0.325 | 41 J= 41, 42 SEC=2 NSEG=1 ANG=180
| 48 X= 2.900 Y= 0.000 Z= -0.325 | 42 J= 42, 1 SEC=2 NSEG=1 ANG=180
| 49 X= 3.450 Y= 0.000 Z= -0.325 | 43 J= 32, 11 SEC=2 NSEG=4 ANG=0
50 X= 4.000 Y= 0.000 Z= -0.325
| 51 X= 4.550 Y= 0.000 Z= -0.325 | NLLINK
| 52 X= 5.100 Y= 0.000 Z= -0.325 | 1 J=1,43 NLP=SP1 ANG=0
| 53 X= 5.650 Y= 0.000 Z= -0.325 | 2 J=4,44 NLP=SP2 ANG=0
| 54 X= 6.200 Y= 0.000 Z= -0.325 | 3 J=5,45 NLP=SP2 ANG=0
| 55 X= 6.750 Y= 0.000 Z= -0.325 | 4 J=6,46 NLP=SP2 ANG=0
5 J=7,47 NLP=SP2 ANG=0
| RESTRAINT | 6 J=8,48 NLP=SP2 ANG=0
| ADD=43 DOF=U1, U2, U3, R1, R2, R3 | 7 J=11,49 NLP=SP2 ANG=0
| ADD=44 DOF=U1, U2, U3, R1, R2, R3 | 8 J=14,50 NLP=SP2 ANG=0
| ADD=45 DOF=U1, U2, U3, R1, R2, R3 | 9 J=15,51 NLP=SP2 ANG=0
| ADD=46 DOF=U1, U2, U3, R1, R2, R3 | 10 J=16,52 NLP=SP2 ANG=0
| ADD=47 DOF=U1, U2, U3, R1, R2, R3 | 11 J=17,53 NLP=SP2 ANG=0
| ADD=48 DOF=U1, U2, U3, R1, R2, R3 | 12 J=18,54 NLP=SP2 ANG=0
| ADD=49 DOF=U1, U2, U3, R1, R2, R3 | 13 J=21,55 NLP=SP1 ANG=0
ADD=50 DOF=U1, U2, U3, R1, R2, R3
| ADD=51 DOF=U1, U2, U3, R1, R2, R3 | LOAD
| ADD=52 DOF=U1, U2, U3, R1, R2, R3 | NAME=SELFWGT SW=1
| ADD=53 DOF=U1, U2, U3, R1, R2, R3 | NAME=NWDEAD
| ADD=54 DOF=U1, U2, U3, R1, R2, R3 | TYPE=Distributed Span
| ADD=55 DOF=U1, U2, U3, R1, R2, R3 | ADD=26 RD=0,1 UZ=-38,-38
ADD=27 RD=0,1 UZ=-38,-38
| SPRING | ADD=28 RD=0,1 UZ=-38,-38
| ADD=1 U1=1e+010 | ADD=29 RD=0,1 UZ=-38,-38
ADD=30 RD=0,1 UZ=-38,-38
| MATERIAL | ADD=31 RD=0,1 UZ=-38,-38
| NAME=CONC IDES=C M=0.0001 W=24.5 | ADD=32 RD=0,1 UZ=-38,-38
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | ADD=33 RD=0,1 UZ=-38,-38
ADD=34 RD=0,1 UZ=-38,-38
| NLPROP | ADD=35 RD=0,1 UZ=-38,-38
| ADD=36 RD=0,1 UZ=-38,-38 | LOAD=SELFWGT SF=1 AT=1
| ADD=37 RD=0,1 UZ=-38,-38 | LOAD=NWDEAD SF=1 AT=1
| NAME=LIVEFULL | LOAD=LIVEFULL SF=1 AT=1
| TYPE=Distributed Span | LOAD=HORLIVE SF=1 AT=1
| ADD=26 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=NWSOFULL SF=1 AT=1
| ADD=27 RD=0,1 UZ=-15.4858,-15.4858 | NAME=HIST8 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=28 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=SELFWGT SF=1 AT=1
| ADD=29 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=NWDEAD SF=1 AT=1
| ADD=30 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=HORLIVE SF=1 AT=1
| ADD=31 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=NWSOFULL SF=1 AT=1
| ADD=32 RD=0,1 UZ=-15.4858,-15.4858 | NAME=HIST9 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
| ADD=33 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=SELFWGT SF=1 AT=1
| ADD=34 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=NWDEAD SF=1 AT=1
| ADD=35 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=LIVEFULL SF=1 AT=1
| ADD=36 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=HORLIVE SF=0.5 AT=1
| ADD=37 RD=0,1 UZ=-15.4858,-15.4858 | LOAD=NWSOFULL SF=0.5 AT=1
NAME=HORLIVE
| TYPE=Distributed Span | COMBO
| ADD=21 RD=0,1 UX=-5,-5 | NAME=ULTIMATE TYPE=ENVE
| ADD=22 RD=0,1 UX=-5,-5 | HIST=HIST1 SF=1
| ADD=23 RD=0,1 UX=-5,-5 | HIST=HIST2 SF=1
| ADD=24 RD=0,1 UX=-5,-5 | HIST=HIST3 SF=1
| ADD=25 RD=0,1 UX=-5,-5 | HIST=HIST4 SF=1
| ADD=38 RD=0,1 UX=5,5 | HIST=HIST5 SF=1
| ADD=39 RD=0,1 UX=5,5 | HIST=HIST6 SF=1
| ADD=40 RD=0,1 UX=5,5 | NAME=SERVICE TYPE=ENVE
| ADD=41 RD=0,1 UX=5,5 | HIST=HIST7 SF=1
| ADD=42 RD=0,1 UX=5,5 | HIST=HIST8 SF=1
| NAME=NWSOFULL | HIST=HIST9 SF=1
TYPE=Distributed Span
| ADD=21 RD=0,1 UX=-52.487,-50.824 | OUTPUT
| ADD=22 RD=0,1 UX=-50.824,-48.639 | ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
| ADD=23 RD=0,1 UX=-48.639,-24.509 | ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*
ADD=24 RD=0,1 UX=-24.509,-22.324
ADD=25 RD=0,1 UX=-22.324,-20.662
ADD=38 RD=0,1 UX=20.662,22.324
ADD=39 RD=0,1 UX=22.324,24.509
ADD=40 RD=0,1 UX=24.509,48.639
ADD=41 RD=0,1 UX=48.639,50.824
ADD=42 RD=0,1 UX=50.824,52.487
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=HORLIVE
LOAD=NWSOFULL
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.6 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST3 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.6 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST4 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.6 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST5 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=0.9 AT=1
LOAD=NWDEAD SF=1.6 AT=1
LOAD=HORLIVE SF=1.6 AT=1
LOAD=NWSOFULL SF=1.6 AT=1
NAME=HIST6 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1.2 AT=1
LOAD=NWDEAD SF=1.6 AT=1
LOAD=LIVEFULL SF=1.6 AT=1
LOAD=HORLIVE SF=0.8 AT=1
LOAD=NWSOFULL SF=0.8 AT=1
NAME=HIST7 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y

## INPUT(붕괴방지)
14. INPUT DATA (붕괴방지)
| SYSTEM | 80 X= 7.250 Y= 0.000 Z= 3.525
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | 81 X= 6.750 Y= 0.000 Z= 4.025
82 X= 6.200 Y= 0.000 Z= 4.025
| JOINT | 83 X= 5.650 Y= 0.000 Z= 4.025
| 1 X= 0.150 Y= 0.000 Z= 0.175 | 84 X= 5.100 Y= 0.000 Z= 4.025
| 2 X= 0.300 Y= 0.000 Z= 0.175 | 85 X= 4.550 Y= 0.000 Z= 4.025
| 3 X= 0.580 Y= 0.000 Z= 0.175 | 86 X= 4.000 Y= 0.000 Z= 4.025
| 4 X= 0.700 Y= 0.000 Z= 0.175 | 87 X= 3.450 Y= 0.000 Z= 4.025
| 5 X= 1.250 Y= 0.000 Z= 0.175 | 88 X= 2.900 Y= 0.000 Z= 4.025
| 6 X= 1.800 Y= 0.000 Z= 0.175 | 89 X= 2.350 Y= 0.000 Z= 4.025
| 7 X= 2.350 Y= 0.000 Z= 0.175 | 90 X= 1.800 Y= 0.000 Z= 4.025
| 8 X= 2.900 Y= 0.000 Z= 0.175 | 91 X= 1.250 Y= 0.000 Z= 4.025
| 9 X= 3.020 Y= 0.000 Z= 0.175 | 92 X= 0.700 Y= 0.000 Z= 4.025
| 10 X= 3.300 Y= 0.000 Z= 0.175 | 93 X= 0.150 Y= 0.000 Z= 4.025
| 11 X= 3.450 Y= 0.000 Z= 0.175 | 94 X= -0.350 Y= 0.000 Z= 3.525
| 12 X= 3.600 Y= 0.000 Z= 0.175 | 95 X= -0.350 Y= 0.000 Z= 2.967
| 13 X= 3.880 Y= 0.000 Z= 0.175 | 96 X= -0.350 Y= 0.000 Z= 2.408
| 14 X= 4.000 Y= 0.000 Z= 0.175 | 97 X= -0.350 Y= 0.000 Z= 1.850
| 15 X= 4.550 Y= 0.000 Z= 0.175 | 98 X= -0.350 Y= 0.000 Z= 1.292
| 16 X= 5.100 Y= 0.000 Z= 0.175 | 99 X= -0.350 Y= 0.000 Z= 0.733
| 17 X= 5.650 Y= 0.000 Z= 0.175 | 100 X= -0.350 Y= 0.000 Z= 0.175
18 X= 6.200 Y= 0.000 Z= 0.175
| 19 X= 6.320 Y= 0.000 Z= 0.175 | RESTRAINT
| 20 X= 6.600 Y= 0.000 Z= 0.175 | ADD=61 DOF=U1, U2, U3, R1, R2, R3
| 21 X= 6.750 Y= 0.000 Z= 0.175 | ADD=62 DOF=U1, U2, U3, R1, R2, R3
| 22 X= 6.750 Y= 0.000 Z= 0.350 | ADD=63 DOF=U1, U2, U3, R1, R2, R3
| 23 X= 6.750 Y= 0.000 Z= 0.580 | ADD=64 DOF=U1, U2, U3, R1, R2, R3
| 24 X= 6.750 Y= 0.000 Z= 0.733 | ADD=65 DOF=U1, U2, U3, R1, R2, R3
| 25 X= 6.750 Y= 0.000 Z= 1.292 | ADD=66 DOF=U1, U2, U3, R1, R2, R3
| 26 X= 6.750 Y= 0.000 Z= 1.850 | ADD=67 DOF=U1, U2, U3, R1, R2, R3
| 27 X= 6.750 Y= 0.000 Z= 2.408 | ADD=68 DOF=U1, U2, U3, R1, R2, R3
| 28 X= 6.750 Y= 0.000 Z= 2.967 | ADD=69 DOF=U1, U2, U3, R1, R2, R3
| 29 X= 6.750 Y= 0.000 Z= 3.120 | ADD=70 DOF=U1, U2, U3, R1, R2, R3
| 30 X= 6.750 Y= 0.000 Z= 3.350 | ADD=71 DOF=U1, U2, U3, R1, R2, R3
| 31 X= 6.750 Y= 0.000 Z= 3.525 | ADD=72 DOF=U1, U2, U3, R1, R2, R3
| 32 X= 6.600 Y= 0.000 Z= 3.525 | ADD=73 DOF=U1, U2, U3, R1, R2, R3
| 33 X= 6.320 Y= 0.000 Z= 3.525 | ADD=74 DOF=U1, U2, U3, R1, R2, R3
| 34 X= 6.200 Y= 0.000 Z= 3.525 | ADD=75 DOF=U1, U2, U3, R1, R2, R3
| 35 X= 5.650 Y= 0.000 Z= 3.525 | ADD=76 DOF=U1, U2, U3, R1, R2, R3
| 36 X= 5.100 Y= 0.000 Z= 3.525 | ADD=77 DOF=U1, U2, U3, R1, R2, R3
| 37 X= 4.550 Y= 0.000 Z= 3.525 | ADD=78 DOF=U1, U2, U3, R1, R2, R3
| 38 X= 4.000 Y= 0.000 Z= 3.525 | ADD=79 DOF=U1, U2, U3, R1, R2, R3
| 39 X= 3.880 Y= 0.000 Z= 3.525 | ADD=80 DOF=U1, U2, U3, R1, R2, R3
| 40 X= 3.600 Y= 0.000 Z= 3.525 | ADD=81 DOF=U1, U2, U3, R1, R2, R3
| 41 X= 3.450 Y= 0.000 Z= 3.525 | ADD=82 DOF=U1, U2, U3, R1, R2, R3
| 42 X= 3.300 Y= 0.000 Z= 3.525 | ADD=83 DOF=U1, U2, U3, R1, R2, R3
| 43 X= 3.020 Y= 0.000 Z= 3.525 | ADD=84 DOF=U1, U2, U3, R1, R2, R3
| 44 X= 2.900 Y= 0.000 Z= 3.525 | ADD=85 DOF=U1, U2, U3, R1, R2, R3
| 45 X= 2.350 Y= 0.000 Z= 3.525 | ADD=86 DOF=U1, U2, U3, R1, R2, R3
| 46 X= 1.800 Y= 0.000 Z= 3.525 | ADD=87 DOF=U1, U2, U3, R1, R2, R3
| 47 X= 1.250 Y= 0.000 Z= 3.525 | ADD=88 DOF=U1, U2, U3, R1, R2, R3
| 48 X= 0.700 Y= 0.000 Z= 3.525 | ADD=89 DOF=U1, U2, U3, R1, R2, R3
| 49 X= 0.580 Y= 0.000 Z= 3.525 | ADD=90 DOF=U1, U2, U3, R1, R2, R3
| 50 X= 0.300 Y= 0.000 Z= 3.525 | ADD=91 DOF=U1, U2, U3, R1, R2, R3
| 51 X= 0.150 Y= 0.000 Z= 3.525 | ADD=92 DOF=U1, U2, U3, R1, R2, R3
| 52 X= 0.150 Y= 0.000 Z= 3.350 | ADD=93 DOF=U1, U2, U3, R1, R2, R3
| 53 X= 0.150 Y= 0.000 Z= 3.120 | ADD=94 DOF=U1, U2, U3, R1, R2, R3
| 54 X= 0.150 Y= 0.000 Z= 2.967 | ADD=95 DOF=U1, U2, U3, R1, R2, R3
| 55 X= 0.150 Y= 0.000 Z= 2.408 | ADD=96 DOF=U1, U2, U3, R1, R2, R3
| 56 X= 0.150 Y= 0.000 Z= 1.850 | ADD=97 DOF=U1, U2, U3, R1, R2, R3
| 57 X= 0.150 Y= 0.000 Z= 1.292 | ADD=98 DOF=U1, U2, U3, R1, R2, R3
| 58 X= 0.150 Y= 0.000 Z= 0.733 | ADD=99 DOF=U1, U2, U3, R1, R2, R3
| 59 X= 0.150 Y= 0.000 Z= 0.580 | ADD=100 DOF=U1, U2, U3, R1, R2, R3
60 X= 0.150 Y= 0.000 Z= 0.350
| 61 X= 0.150 Y= 0.000 Z= -0.325 | SPRING
| 62 X= 0.700 Y= 0.000 Z= -0.325 | ADD=1 U1=4750.77 U3=8098.73
| 63 X= 1.250 Y= 0.000 Z= -0.325 | ADD=4 U1=6148.06
| 64 X= 1.800 Y= 0.000 Z= -0.325 | ADD=5 U1=6148.06
| 65 X= 2.350 Y= 0.000 Z= -0.325 | ADD=6 U1=6148.06
| 66 X= 2.900 Y= 0.000 Z= -0.325 | ADD=7 U1=6148.06
| 67 X= 3.450 Y= 0.000 Z= -0.325 | ADD=8 U1=6148.06
| 68 X= 4.000 Y= 0.000 Z= -0.325 | ADD=11 U1=6148.06
| 69 X= 4.550 Y= 0.000 Z= -0.325 | ADD=14 U1=6148.06
| 70 X= 5.100 Y= 0.000 Z= -0.325 | ADD=15 U1=6148.06
| 71 X= 5.650 Y= 0.000 Z= -0.325 | ADD=16 U1=6148.06
| 72 X= 6.200 Y= 0.000 Z= -0.325 | ADD=17 U1=6148.06
| 73 X= 6.750 Y= 0.000 Z= -0.325 | ADD=18 U1=6148.06
| 74 X= 7.250 Y= 0.000 Z= 0.175 | ADD=21 U1=4750.77 U3=8098.73
| 75 X= 7.250 Y= 0.000 Z= 0.733 | ADD=24 U3=9953.94
| 76 X= 7.250 Y= 0.000 Z= 1.292 | ADD=25 U3=9953.94
| 77 X= 7.250 Y= 0.000 Z= 1.850 | ADD=26 U3=9953.94
| 78 X= 7.250 Y= 0.000 Z= 2.408 | ADD=27 U3=9953.94
| 79 X= 7.250 Y= 0.000 Z= 2.967 | ADD=28 U3=9953.94
| ADD=31 U1=4750.77 U3=8098.73 | 49 J= 49, 50 SEC=1 NSEG=1 ANG=0
| ADD=34 U1=6148.06 | 50 J= 50, 51 SEC=1 NSEG=1 ANG=0
| ADD=35 U1=6148.06 | 51 J= 51, 52 SEC=2 NSEG=1 ANG=180
| ADD=36 U1=6148.06 | 52 J= 52, 53 SEC=2 NSEG=1 ANG=180
| ADD=37 U1=6148.06 | 53 J= 53, 54 SEC=2 NSEG=1 ANG=180
| ADD=38 U1=6148.06 | 54 J= 54, 55 SEC=2 NSEG=2 ANG=180
| ADD=41 U1=6148.06 | 55 J= 55, 56 SEC=2 NSEG=2 ANG=180
| ADD=44 U1=6148.06 | 56 J= 56, 57 SEC=2 NSEG=2 ANG=180
| ADD=45 U1=6148.06 | 57 J= 57, 58 SEC=2 NSEG=2 ANG=180
| ADD=46 U1=6148.06 | 58 J= 58, 59 SEC=2 NSEG=1 ANG=180
| ADD=47 U1=6148.06 | 59 J= 59, 60 SEC=2 NSEG=1 ANG=180
| ADD=48 U1=6148.06 | 60 J= 60, 1 SEC=2 NSEG=1 ANG=180
| ADD=51 U1=4750.77 U3=8098.73 | 61 J= 41, 11 SEC=2 NSEG=4 ANG=0
ADD=54 U3=9953.94
| ADD=55 U3=9953.94 | NLLINK
| ADD=56 U3=9953.94 | 1 J=1,61 NLP=SP1 ANG=0
| ADD=57 U3=9953.94 | 2 J=4,62 NLP=SP2 ANG=0
| ADD=58 U3=9953.94 | 3 J=5,63 NLP=SP2 ANG=0
4 J=6,64 NLP=SP2 ANG=0
| MATERIAL | 5 J=7,65 NLP=SP2 ANG=0
| NAME=CONC IDES=C M=0.0001 W=24.5 | 6 J=8,66 NLP=SP2 ANG=0
| T=0 E=2.7e+007 U=0.17 A=9.99e-006 | 7 J=11,67 NLP=SP2 ANG=0
8 J=14,68 NLP=SP2 ANG=0
| NLPROP | 9 J=15,69 NLP=SP2 ANG=0
| NAME=SP1 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 10 J=16,70 NLP=SP2 ANG=0
| DOF=U1 KE=14252.3 CE=0.99999 K=14252.3 OPEN=0 | 11 J=17,71 NLP=SP2 ANG=0
| NAME=SP2 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 12 J=18,72 NLP=SP2 ANG=0
| DOF=U1 KE=18444.2 CE=0.99999 K=18444.2 OPEN=0 | 13 J=21,73 NLP=SP1 ANG=0
| NAME=SP3 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 14 J=21,74 NLP=SP3 ANG=180
| DOF=U1 KE=24296.2 CE=0.99999 K=24296.2 OPEN=0 | 15 J=24,75 NLP=SP4 ANG=180
| NAME=SP4 TYPE=Gap M=1e-005 MR1=1e-005 MR2=1e-005 MR3=1e-005 | 16 J=25,76 NLP=SP4 ANG=180
| DOF=U1 KE=29861.8 CE=0.99999 K=29861.8 OPEN=0 | 17 J=26,77 NLP=SP4 ANG=180
18 J=27,78 NLP=SP4 ANG=180
| FRAME SECTION | 19 J=28,79 NLP=SP4 ANG=180
| NAME=1 MAT=CONC SH=R T=0.35, 1 | 20 J=31,80 NLP=SP3 ANG=180
| NAME=2 MAT=CONC SH=R T=0.3, 1 | 21 J=31,81 NLP=SP1 ANG=0
22 J=34,82 NLP=SP2 ANG=0
| FRAME | 23 J=35,83 NLP=SP2 ANG=0
| 1 J= 1, 2 SEC=1 NSEG=1 ANG=180 | 24 J=36,84 NLP=SP2 ANG=0
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | 25 J=37,85 NLP=SP2 ANG=0
| 3 J= 3, 4 SEC=1 NSEG=1 ANG=180 | 26 J=38,86 NLP=SP2 ANG=0
| 4 J= 4, 5 SEC=1 NSEG=2 ANG=180 | 27 J=41,87 NLP=SP2 ANG=0
| 5 J= 5, 6 SEC=1 NSEG=2 ANG=180 | 28 J=44,88 NLP=SP2 ANG=0
| 6 J= 6, 7 SEC=1 NSEG=2 ANG=180 | 29 J=45,89 NLP=SP2 ANG=0
| 7 J= 7, 8 SEC=1 NSEG=2 ANG=180 | 30 J=46,90 NLP=SP2 ANG=0
| 8 J= 8, 9 SEC=1 NSEG=1 ANG=180 | 31 J=47,91 NLP=SP2 ANG=0
| 9 J= 9, 10 SEC=1 NSEG=1 ANG=180 | 32 J=48,92 NLP=SP2 ANG=0
| 10 J= 10, 11 SEC=1 NSEG=1 ANG=180 | 33 J=51,93 NLP=SP1 ANG=0
| 11 J= 11, 12 SEC=1 NSEG=1 ANG=180 | 34 J=51,94 NLP=SP3 ANG=180
| 12 J= 12, 13 SEC=1 NSEG=1 ANG=180 | 35 J=54,95 NLP=SP4 ANG=180
| 13 J= 13, 14 SEC=1 NSEG=1 ANG=180 | 36 J=55,96 NLP=SP4 ANG=180
| 14 J= 14, 15 SEC=1 NSEG=2 ANG=180 | 37 J=56,97 NLP=SP4 ANG=180
| 15 J= 15, 16 SEC=1 NSEG=2 ANG=180 | 38 J=57,98 NLP=SP4 ANG=180
| 16 J= 16, 17 SEC=1 NSEG=2 ANG=180 | 39 J=58,99 NLP=SP4 ANG=180
| 17 J= 17, 18 SEC=1 NSEG=2 ANG=180 | 40 J=1,100 NLP=SP3 ANG=180
18 J= 18, 19 SEC=1 NSEG=1 ANG=180
| 19 J= 19, 20 SEC=1 NSEG=1 ANG=180 | LOAD
| 20 J= 20, 21 SEC=1 NSEG=1 ANG=180 | NAME=SELFWGT SW=1
| 21 J= 21, 22 SEC=2 NSEG=1 ANG=0 | NAME=NWDEAD
| 22 J= 22, 23 SEC=2 NSEG=1 ANG=0 | TYPE=Distributed Span
| 23 J= 23, 24 SEC=2 NSEG=1 ANG=0 | ADD=31 RD=0,1 UZ=-38,-38
| 24 J= 24, 25 SEC=2 NSEG=2 ANG=0 | ADD=32 RD=0,1 UZ=-38,-38
| 25 J= 25, 26 SEC=2 NSEG=2 ANG=0 | ADD=33 RD=0,1 UZ=-38,-38
| 26 J= 26, 27 SEC=2 NSEG=2 ANG=0 | ADD=34 RD=0,1 UZ=-38,-38
| 27 J= 27, 28 SEC=2 NSEG=2 ANG=0 | ADD=35 RD=0,1 UZ=-38,-38
| 28 J= 28, 29 SEC=2 NSEG=1 ANG=0 | ADD=36 RD=0,1 UZ=-38,-38
| 29 J= 29, 30 SEC=2 NSEG=1 ANG=0 | ADD=37 RD=0,1 UZ=-38,-38
| 30 J= 30, 31 SEC=2 NSEG=1 ANG=0 | ADD=38 RD=0,1 UZ=-38,-38
| 31 J= 31, 32 SEC=1 NSEG=1 ANG=0 | ADD=39 RD=0,1 UZ=-38,-38
| 32 J= 32, 33 SEC=1 NSEG=1 ANG=0 | ADD=40 RD=0,1 UZ=-38,-38
| 33 J= 33, 34 SEC=1 NSEG=1 ANG=0 | ADD=41 RD=0,1 UZ=-38,-38
| 34 J= 34, 35 SEC=1 NSEG=2 ANG=0 | ADD=42 RD=0,1 UZ=-38,-38
| 35 J= 35, 36 SEC=1 NSEG=2 ANG=0 | ADD=43 RD=0,1 UZ=-38,-38
| 36 J= 36, 37 SEC=1 NSEG=2 ANG=0 | ADD=44 RD=0,1 UZ=-38,-38
| 37 J= 37, 38 SEC=1 NSEG=2 ANG=0 | ADD=45 RD=0,1 UZ=-38,-38
| 38 J= 38, 39 SEC=1 NSEG=1 ANG=0 | ADD=46 RD=0,1 UZ=-38,-38
| 39 J= 39, 40 SEC=1 NSEG=1 ANG=0 | ADD=47 RD=0,1 UZ=-38,-38
| 40 J= 40, 41 SEC=1 NSEG=1 ANG=0 | ADD=48 RD=0,1 UZ=-38,-38
| 41 J= 41, 42 SEC=1 NSEG=1 ANG=0 | ADD=49 RD=0,1 UZ=-38,-38
| 42 J= 42, 43 SEC=1 NSEG=1 ANG=0 | ADD=50 RD=0,1 UZ=-38,-38
| 43 J= 43, 44 SEC=1 NSEG=1 ANG=0 | NAME=LIVEFULL
| 44 J= 44, 45 SEC=1 NSEG=2 ANG=0 | TYPE=Distributed Span
| 45 J= 45, 46 SEC=1 NSEG=2 ANG=0 | ADD=31 RD=0,1 UZ=-15.4858,-15.4858
| 46 J= 46, 47 SEC=1 NSEG=2 ANG=0 | ADD=32 RD=0,1 UZ=-15.4858,-15.4858
| 47 J= 47, 48 SEC=1 NSEG=2 ANG=0 | ADD=33 RD=0,1 UZ=-15.4858,-15.4858
| 48 J= 48, 49 SEC=1 NSEG=1 ANG=0 | ADD=34 RD=0,1 UZ=-15.4858,-15.4858
| ADD=35 RD=0,1 UZ=-15.4858,-15.4858 | ADD=25 RD=0,1 UZ=0.3,0.3
| ADD=36 RD=0,1 UZ=-15.4858,-15.4858 | ADD=26 RD=0,1 UZ=0.3,0.3
| ADD=37 RD=0,1 UZ=-15.4858,-15.4858 | ADD=27 RD=0,1 UZ=0.3,0.3
| ADD=38 RD=0,1 UZ=-15.4858,-15.4858 | ADD=28 RD=0,1 UZ=0.3,0.3
| ADD=39 RD=0,1 UZ=-15.4858,-15.4858 | ADD=29 RD=0,1 UZ=0.3,0.3
| ADD=40 RD=0,1 UZ=-15.4858,-15.4858 | ADD=30 RD=0,1 UZ=0.3,0.3
| ADD=41 RD=0,1 UZ=-15.4858,-15.4858 | ADD=31 RD=0,1 UX=0.17,0.17
| ADD=42 RD=0,1 UZ=-15.4858,-15.4858 | ADD=32 RD=0,1 UX=0.17,0.17
| ADD=43 RD=0,1 UZ=-15.4858,-15.4858 | ADD=33 RD=0,1 UX=0.17,0.17
| ADD=44 RD=0,1 UZ=-15.4858,-15.4858 | ADD=34 RD=0,1 UX=0.17,0.17
| ADD=45 RD=0,1 UZ=-15.4858,-15.4858 | ADD=35 RD=0,1 UX=0.17,0.17
| ADD=46 RD=0,1 UZ=-15.4858,-15.4858 | ADD=36 RD=0,1 UX=0.17,0.17
| ADD=47 RD=0,1 UZ=-15.4858,-15.4858 | ADD=37 RD=0,1 UX=0.17,0.17
| ADD=48 RD=0,1 UZ=-15.4858,-15.4858 | ADD=38 RD=0,1 UX=0.17,0.17
| ADD=49 RD=0,1 UZ=-15.4858,-15.4858 | ADD=39 RD=0,1 UX=0.17,0.17
| ADD=50 RD=0,1 UZ=-15.4858,-15.4858 | ADD=40 RD=0,1 UX=0.17,0.17
| NAME=SEUPSLAB | ADD=41 RD=0,1 UX=0.17,0.17
| TYPE=Distributed Span | ADD=42 RD=0,1 UX=0.17,0.17
| ADD=31 RD=0,1 UX=0.6036,0.6036 | ADD=43 RD=0,1 UX=0.17,0.17
| ADD=32 RD=0,1 UX=0.6036,0.6036 | ADD=44 RD=0,1 UX=0.17,0.17
| ADD=33 RD=0,1 UX=0.6036,0.6036 | ADD=45 RD=0,1 UX=0.17,0.17
| ADD=34 RD=0,1 UX=0.6036,0.6036 | ADD=46 RD=0,1 UX=0.17,0.17
| ADD=35 RD=0,1 UX=0.6036,0.6036 | ADD=47 RD=0,1 UX=0.17,0.17
| ADD=36 RD=0,1 UX=0.6036,0.6036 | ADD=48 RD=0,1 UX=0.17,0.17
| ADD=37 RD=0,1 UX=0.6036,0.6036 | ADD=49 RD=0,1 UX=0.17,0.17
| ADD=38 RD=0,1 UX=0.6036,0.6036 | ADD=50 RD=0,1 UX=0.17,0.17
| ADD=39 RD=0,1 UX=0.6036,0.6036 | ADD=51 RD=0,1 UZ=-0.3,-0.3
| ADD=40 RD=0,1 UX=0.6036,0.6036 | ADD=52 RD=0,1 UZ=-0.3,-0.3
| ADD=41 RD=0,1 UX=0.6036,0.6036 | ADD=53 RD=0,1 UZ=-0.3,-0.3
| ADD=42 RD=0,1 UX=0.6036,0.6036 | ADD=54 RD=0,1 UZ=-0.3,-0.3
| ADD=43 RD=0,1 UX=0.6036,0.6036 | ADD=55 RD=0,1 UZ=-0.3,-0.3
| ADD=44 RD=0,1 UX=0.6036,0.6036 | ADD=56 RD=0,1 UZ=-0.3,-0.3
| ADD=45 RD=0,1 UX=0.6036,0.6036 | ADD=57 RD=0,1 UZ=-0.3,-0.3
| ADD=46 RD=0,1 UX=0.6036,0.6036 | ADD=58 RD=0,1 UZ=-0.3,-0.3
| ADD=47 RD=0,1 UX=0.6036,0.6036 | ADD=59 RD=0,1 UZ=-0.3,-0.3
| ADD=48 RD=0,1 UX=0.6036,0.6036 | ADD=60 RD=0,1 UZ=-0.3,-0.3
| ADD=49 RD=0,1 UX=0.6036,0.6036 | NAME=SEINER
| ADD=50 RD=0,1 UX=0.6036,0.6036 | TYPE=Distributed Span
| NAME=SEWALL | ADD=1 RD=0,1 UX=1.2583,1.2583
| TYPE=Distributed Span | ADD=2 RD=0,1 UX=1.2583,1.2583
| ADD=21 RD=0,1 UX=0,0.2141 | ADD=3 RD=0,1 UX=1.2583,1.2583
| ADD=22 RD=0,1 UX=0.2141,0.4816 | ADD=4 RD=0,1 UX=1.2583,1.2583
| ADD=23 RD=0,1 UX=0.4816,0.6422 | ADD=5 RD=0,1 UX=1.2583,1.2583
| ADD=24 RD=0,1 UX=0.6422,1.2309 | ADD=6 RD=0,1 UX=1.2583,1.2583
| ADD=25 RD=0,1 UX=1.2309,1.766 | ADD=7 RD=0,1 UX=1.2583,1.2583
| ADD=26 RD=0,1 UX=1.766,2.1941 | ADD=8 RD=0,1 UX=1.2583,1.2583
| ADD=27 RD=0,1 UX=2.1941,2.5688 | ADD=9 RD=0,1 UX=1.2583,1.2583
| ADD=28 RD=0,1 UX=2.5688,2.6758 | ADD=10 RD=0,1 UX=1.2583,1.2583
| ADD=29 RD=0,1 UX=2.6758,2.7828 | ADD=11 RD=0,1 UX=1.2583,1.2583
| ADD=30 RD=0,1 UX=2.7828,2.8899 | ADD=12 RD=0,1 UX=1.2583,1.2583
| ADD=51 RD=0,1 UX=2.8899,2.7828 | ADD=13 RD=0,1 UX=1.2583,1.2583
| ADD=52 RD=0,1 UX=2.7828,2.6758 | ADD=14 RD=0,1 UX=1.2583,1.2583
| ADD=53 RD=0,1 UX=2.6758,2.5688 | ADD=15 RD=0,1 UX=1.2583,1.2583
| ADD=54 RD=0,1 UX=2.5688,2.1941 | ADD=16 RD=0,1 UX=1.2583,1.2583
| ADD=55 RD=0,1 UX=2.1941,1.766 | ADD=17 RD=0,1 UX=1.2583,1.2583
| ADD=56 RD=0,1 UX=1.766,1.2309 | ADD=18 RD=0,1 UX=1.2583,1.2583
| ADD=57 RD=0,1 UX=1.2309,0.6422 | ADD=19 RD=0,1 UX=1.2583,1.2583
| ADD=58 RD=0,1 UX=0.6422,0.4816 | ADD=20 RD=0,1 UX=1.2583,1.2583
| ADD=59 RD=0,1 UX=0.4816,0.2141 | ADD=21 RD=0,1 UX=1.07854,1.08163
| ADD=60 RD=0,1 UX=0.2141,0 | ADD=22 RD=0,1 UX=1.08163,1.08568
| NAME=SEPRINSH | ADD=23 RD=0,1 UX=1.08568,1.08838
| TYPE=Distributed Span | ADD=24 RD=0,1 UX=1.08838,1.09824
| ADD=1 RD=0,1 UX=-0.43,-0.43 | ADD=25 RD=0,1 UX=1.09824,1.10809
| ADD=2 RD=0,1 UX=-0.43,-0.43 | ADD=26 RD=0,1 UX=1.10809,1.11793
| ADD=3 RD=0,1 UX=-0.43,-0.43 | ADD=27 RD=0,1 UX=1.11793,1.12779
| ADD=4 RD=0,1 UX=-0.43,-0.43 | ADD=28 RD=0,1 UX=1.12779,1.13049
| ADD=5 RD=0,1 UX=-0.43,-0.43 | ADD=29 RD=0,1 UX=1.13049,1.13455
| ADD=6 RD=0,1 UX=-0.43,-0.43 | ADD=30 RD=0,1 UX=1.13455,1.13763
| ADD=7 RD=0,1 UX=-0.43,-0.43 | ADD=31 RD=0,1 UX=1.32724,1.32724
| ADD=8 RD=0,1 UX=-0.43,-0.43 | ADD=32 RD=0,1 UX=1.32724,1.32724
| ADD=9 RD=0,1 UX=-0.43,-0.43 | ADD=33 RD=0,1 UX=1.32724,1.32724
| ADD=10 RD=0,1 UX=-0.43,-0.43 | ADD=34 RD=0,1 UX=1.32724,1.32724
| ADD=11 RD=0,1 UX=-0.43,-0.43 | ADD=35 RD=0,1 UX=1.32724,1.32724
| ADD=12 RD=0,1 UX=-0.43,-0.43 | ADD=36 RD=0,1 UX=1.32724,1.32724
| ADD=13 RD=0,1 UX=-0.43,-0.43 | ADD=37 RD=0,1 UX=1.32724,1.32724
| ADD=14 RD=0,1 UX=-0.43,-0.43 | ADD=38 RD=0,1 UX=1.32724,1.32724
| ADD=15 RD=0,1 UX=-0.43,-0.43 | ADD=39 RD=0,1 UX=1.32724,1.32724
| ADD=16 RD=0,1 UX=-0.43,-0.43 | ADD=40 RD=0,1 UX=1.32724,1.32724
| ADD=17 RD=0,1 UX=-0.43,-0.43 | ADD=41 RD=0,1 UX=1.32724,1.32724
| ADD=18 RD=0,1 UX=-0.43,-0.43 | ADD=42 RD=0,1 UX=1.32724,1.32724
| ADD=19 RD=0,1 UX=-0.43,-0.43 | ADD=43 RD=0,1 UX=1.32724,1.32724
| ADD=20 RD=0,1 UX=-0.43,-0.43 | ADD=44 RD=0,1 UX=1.32724,1.32724
| ADD=21 RD=0,1 UZ=0.3,0.3 | ADD=45 RD=0,1 UX=1.32724,1.32724
| ADD=22 RD=0,1 UZ=0.3,0.3 | ADD=46 RD=0,1 UX=1.32724,1.32724
| ADD=23 RD=0,1 UZ=0.3,0.3 | ADD=47 RD=0,1 UX=1.32724,1.32724
| ADD=24 RD=0,1 UZ=0.3,0.3 | ADD=48 RD=0,1 UX=1.32724,1.32724
ADD=49 RD=0,1 UX=1.32724,1.32724
ADD=50 RD=0,1 UX=1.32724,1.32724
ADD=51 RD=0,1 UX=1.13763,1.13455
ADD=52 RD=0,1 UX=1.13455,1.13049
ADD=53 RD=0,1 UX=1.13049,1.12779
ADD=54 RD=0,1 UX=1.12779,1.11793
ADD=55 RD=0,1 UX=1.11793,1.10809
ADD=56 RD=0,1 UX=1.10809,1.09824
ADD=57 RD=0,1 UX=1.09824,1.08838
ADD=58 RD=0,1 UX=1.08838,1.08568
ADD=59 RD=0,1 UX=1.08568,1.08163
ADD=60 RD=0,1 UX=1.08163,1.07854
ADD=61 RD=0,1 UX=1.13763,1.07854
MODE
TYPE=RITZ N=50
LOAD=SELFWGT
LOAD=NWDEAD
LOAD=LIVEFULL
LOAD=SEUPSLAB
LOAD=SEWALL
LOAD=SEPRINSH
LOAD=SEINER
NLLINK=*
HISTORY
NAME=HIST1 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=1 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=1 AT=1
LOAD=SEWALL SF=1 AT=1
LOAD=SEPRINSH SF=1 AT=1
LOAD=SEINER SF=1 AT=1
NAME=HIST2 TYPE=NON NSTEP=50 DT=1 DAMP=.99 DTMAX=1 ENVE=Y
LOAD=SELFWGT SF=1 AT=1
LOAD=NWDEAD SF=1 AT=1
LOAD=LIVEFULL SF=1 AT=1
LOAD=SEUPSLAB SF=-1 AT=1
LOAD=SEWALL SF=-1 AT=1
LOAD=SEPRINSH SF=-1 AT=1
LOAD=SEINER SF=-1 AT=1
COMBO
NAME=ULTIMATE TYPE=ENVE
HIST=HIST1 SF=1
HIST=HIST2 SF=1
OUTPUT
ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*

## OUTPUT(상시)
15. OUTPUT DATA (상시)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 17 | ULTIMATE MAX | 0 | 0 | 77.9292 | 55.7424
| 1 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 17 | ULTIMATE MAX | 0.5 | 0 | 75.0995 | 37.6812
| 1 | ULTIMATE MIN | 0 | -126.6485 | -129.8167 | -70.6527 | 17 | ULTIMATE MAX | 1 | 0 | 72.2697 | 20.3983
| 1 | ULTIMATE MIN | 1 | -126.6485 | -131.3602 | -51.0644 | 17 | ULTIMATE MIN | 0 | -126.6485 | 0 | 0
| 2 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 17 | ULTIMATE MIN | 0.5 | -126.6485 | 0 | 0
| 2 | ULTIMATE MAX | 1 | 0 | 0 | 5.5282 | 17 | ULTIMATE MIN | 1 | -126.6485 | 0 | -8.6347
| 2 | ULTIMATE MIN | 0 | -126.6485 | -131.3602 | -51.0644 | 18 | ULTIMATE MAX | 0 | 0 | 135.4762 | 20.3983
| 2 | ULTIMATE MIN | 1 | -126.6485 | -134.2414 | -21.0335 | 18 | ULTIMATE MAX | 1 | 0 | 134.2414 | 5.5282
| 3 | ULTIMATE MAX | 0 | 0 | 0 | 5.5282 | 18 | ULTIMATE MIN | 0 | -126.6485 | 0 | -8.6347
| 3 | ULTIMATE MAX | 1 | 0 | 0 | 20.3983 | 18 | ULTIMATE MIN | 1 | -126.6485 | 0 | -21.0333
| 3 | ULTIMATE MIN | 0 | -126.6485 | -134.2414 | -21.0335 | 19 | ULTIMATE MAX | 0 | 0 | 134.2414 | 5.5282
| 3 | ULTIMATE MIN | 1 | -126.6485 | -135.4762 | -8.6349 | 19 | ULTIMATE MAX | 1 | 0 | 131.3602 | 0
| 4 | ULTIMATE MAX | 0 | 0 | 0 | 20.3983 | 19 | ULTIMATE MIN | 0 | -126.6485 | 0 | -21.0333
| 4 | ULTIMATE MAX | 0.5 | 0 | 0 | 37.6812 | 19 | ULTIMATE MIN | 1 | -126.6485 | 0 | -51.0644
| 4 | ULTIMATE MAX | 1 | 0 | 0 | 55.7424 | 20 | ULTIMATE MAX | 0 | 0 | 131.3602 | 0
| 4 | ULTIMATE MIN | 0 | -126.6485 | -72.2697 | -8.6349 | 20 | ULTIMATE MAX | 1 | 0 | 129.8167 | 0
| 4 | ULTIMATE MIN | 0.5 | -126.6485 | -75.0995 | 0 | 20 | ULTIMATE MIN | 0 | -126.6485 | 0 | -51.0644
| 4 | ULTIMATE MIN | 1 | -126.6485 | -77.9292 | 0 | 20 | ULTIMATE MIN | 1 | -126.6485 | 0 | -70.6527
| 5 | ULTIMATE MAX | 0 | 0 | 0 | 55.7424 | 21 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 0.5 | 0 | 0 | 57.6617 | 21 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 1 | 0 | 0 | 60.3593 | 21 | ULTIMATE MIN | 0 | -179.704 | -126.6485 | -70.6527
| 5 | ULTIMATE MIN | 0 | -126.6485 | -17.522 | 0 | 21 | ULTIMATE MIN | 1 | -178.1605 | -110.785 | -49.896
| 5 | ULTIMATE MIN | 0.5 | -126.6485 | -19.6443 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 5 | ULTIMATE MIN | 1 | -126.6485 | -21.7666 | 0 | 22 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 6 | ULTIMATE MAX | 0 | 0 | 49.9531 | 60.3593 | 22 | ULTIMATE MIN | 0 | -178.1605 | -110.785 | -49.896
| 6 | ULTIMATE MAX | 0.5 | 0 | 47.1233 | 47.0113 | 22 | ULTIMATE MIN | 1 | -176.1319 | -90.6438 | -26.7627
| 6 | ULTIMATE MAX | 1 | 0 | 44.2936 | 34.4414 | 23 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 6 | ULTIMATE MIN | 0 | -126.6485 | 0 | 0 | 23 | ULTIMATE MAX | 0.25 | 0 | 0 | 20.27
| 6 | ULTIMATE MIN | 0.5 | -126.6485 | 0 | 0 | 23 | ULTIMATE MAX | 0.5 | 0 | 6.1627 | 30.4599
| 6 | ULTIMATE MIN | 1 | -126.6485 | 0 | 0 | 23 | ULTIMATE MAX | 0.75 | 0 | 45.3374 | 13.8279
| 7 | ULTIMATE MAX | 0 | 0 | 106.4518 | 34.4414 | 23 | ULTIMATE MAX | 1 | 0 | 78.3831 | 0
| 7 | ULTIMATE MAX | 0.5 | 0 | 103.622 | 7.6565 | 23 | ULTIMATE MIN | 0 | -176.1319 | -90.6438 | -26.7627
| 7 | ULTIMATE MAX | 1 | 0 | 100.7923 | 0 | 23 | ULTIMATE MIN | 0.25 | -170.5312 | -39.2111 | -4.0123
| 7 | ULTIMATE MIN | 0 | -126.6485 | 0 | 0 | 23 | ULTIMATE MIN | 0.5 | -164.9305 | 0 | 0
| 7 | ULTIMATE MIN | 0.5 | -126.6485 | 0 | 0 | 23 | ULTIMATE MIN | 0.75 | -159.3298 | 0 | -7.091
| 7 | ULTIMATE MIN | 1 | -126.6485 | 0 | -22.5507 | 23 | ULTIMATE MIN | 1 | -153.7291 | 0 | -32.0331
| 8 | ULTIMATE MAX | 0 | 0 | 164.666 | 0 | 24 | ULTIMATE MAX | 0 | 0 | 78.3814 | 0
| 8 | ULTIMATE MAX | 1 | 0 | 163.4312 | 0 | 24 | ULTIMATE MAX | 1 | 0 | 88.8387 | 0
| 8 | ULTIMATE MIN | 0 | -126.6485 | 0 | -22.5507 | 24 | ULTIMATE MIN | 0 | -153.7291 | 0 | -32.033
| 8 | ULTIMATE MIN | 1 | -126.6485 | 0 | -42.2365 | 24 | ULTIMATE MIN | 1 | -151.7005 | 0 | -51.2788
| 9 | ULTIMATE MAX | 0 | 0 | 163.4312 | 0 | 25 | ULTIMATE MAX | 0 | 0 | 88.8387 | 0
| 9 | ULTIMATE MAX | 1 | 0 | 160.55 | 0 | 25 | ULTIMATE MAX | 1 | 0 | 96.2567 | 0
| 9 | ULTIMATE MIN | 0 | -126.6485 | 0 | -42.2365 | 25 | ULTIMATE MIN | 0 | -151.7005 | 0 | -51.2788
| 9 | ULTIMATE MIN | 1 | -126.6485 | 0 | -87.5939 | 25 | ULTIMATE MIN | 1 | -150.157 | 0 | -67.4814
| 10 | ULTIMATE MAX | 0 | 0 | 160.55 | 0 | 26 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 10 | ULTIMATE MAX | 1 | 0 | 159.0065 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 10 | ULTIMATE MIN | 0 | -126.6485 | 0 | -87.5939 | 26 | ULTIMATE MIN | 0 | -96.2567 | -150.157 | -67.4814
| 10 | ULTIMATE MIN | 1 | -126.6485 | 0 | -111.5606 | 26 | ULTIMATE MIN | 1 | -96.2567 | -135.7769 | -46.0375
| 11 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 11 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 27 | ULTIMATE MAX | 1 | 0 | 0 | 6.7091
| 11 | ULTIMATE MIN | 0 | -126.6485 | -159.0065 | -111.5606 | 27 | ULTIMATE MIN | 0 | -96.2567 | -135.7769 | -46.0375
| 11 | ULTIMATE MIN | 1 | -126.6485 | -160.55 | -87.5939 | 27 | ULTIMATE MIN | 1 | -96.2567 | -108.9341 | -18.8219
| 12 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 28 | ULTIMATE MAX | 0 | 0 | 0 | 6.7091
| 12 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 28 | ULTIMATE MAX | 0.25 | 0 | 0 | 32.2621
| 12 | ULTIMATE MIN | 0 | -126.6485 | -160.55 | -87.5939 | 28 | ULTIMATE MAX | 0.5 | 0 | 0 | 48.8971
| 12 | ULTIMATE MIN | 1 | -126.6485 | -163.4312 | -42.2365 | 28 | ULTIMATE MAX | 0.75 | 0 | 0 | 56.614
| 13 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 28 | ULTIMATE MAX | 1 | 0 | 18.5592 | 55.4128
| 13 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 0 | -96.2566 | -108.9341 | -18.8219
| 13 | ULTIMATE MIN | 0 | -126.6485 | -163.4312 | -42.2365 | 28 | ULTIMATE MIN | 0.25 | -96.2566 | -79.6946 | 0
| 13 | ULTIMATE MIN | 1 | -126.6485 | -164.666 | -22.5507 | 28 | ULTIMATE MIN | 0.5 | -96.2566 | -50.455 | 0
| 14 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 28 | ULTIMATE MIN | 0.75 | -96.2566 | -21.2155 | 0
| 14 | ULTIMATE MAX | 0.5 | 0 | 0 | 7.6565 | 28 | ULTIMATE MIN | 1 | -96.2566 | -0.13003 | 0
| 14 | ULTIMATE MAX | 1 | 0 | 0 | 34.4414 | 29 | ULTIMATE MAX | 0 | 0 | 18.5579 | 55.4128
| 14 | ULTIMATE MIN | 0 | -126.6485 | -100.7923 | -22.5507 | 29 | ULTIMATE MAX | 0.25 | 0 | 47.7975 | 45.2936
| 14 | ULTIMATE MIN | 0.5 | -126.6485 | -103.622 | 0 | 29 | ULTIMATE MAX | 0.5 | 0 | 77.037 | 27.0481
| 14 | ULTIMATE MIN | 1 | -126.6485 | -106.4518 | 0 | 29 | ULTIMATE MAX | 0.75 | 0 | 106.2765 | 3.7683
| 15 | ULTIMATE MAX | 0 | 0 | 0 | 34.4414 | 29 | ULTIMATE MAX | 1 | 0 | 135.516 | 0
| 15 | ULTIMATE MAX | 0.5 | 0 | 0 | 47.0113 | 29 | ULTIMATE MIN | 0 | -96.2565 | -0.13594 | 0
| 15 | ULTIMATE MAX | 1 | 0 | 0 | 60.3593 | 29 | ULTIMATE MIN | 0.25 | -96.2565 | 0 | 0
| 15 | ULTIMATE MIN | 0 | -126.6485 | -44.2936 | 0 | 29 | ULTIMATE MIN | 0.5 | -96.2565 | 0 | 0
| 15 | ULTIMATE MIN | 0.5 | -126.6485 | -47.1233 | 0 | 29 | ULTIMATE MIN | 0.75 | -96.2565 | 0 | -1.6989
| 15 | ULTIMATE MIN | 1 | -126.6485 | -49.9531 | 0 | 29 | ULTIMATE MIN | 1 | -96.2565 | 0 | -38.5723
| 16 | ULTIMATE MAX | 0 | 0 | 21.7666 | 60.3593 | 30 | ULTIMATE MAX | 0 | 0 | 135.516 | 0
| 16 | ULTIMATE MAX | 0.5 | 0 | 19.6443 | 57.6617 | 30 | ULTIMATE MAX | 1 | 0 | 162.3589 | 0
| 16 | ULTIMATE MAX | 1 | 0 | 17.522 | 55.7424 | 30 | ULTIMATE MIN | 0 | -96.2565 | 0 | -38.5723
| 16 | ULTIMATE MIN | 0 | -126.6485 | 0 | 0 | 30 | ULTIMATE MIN | 1 | -96.2565 | 0 | -80.2748
| 16 | ULTIMATE MIN | 0.5 | -126.6485 | 0 | 0 | 31 | ULTIMATE MAX | 0 | 0 | 162.3589 | 0
| 16 | ULTIMATE MIN | 1 | -126.6485 | 0 | 0 | 31 | ULTIMATE MAX | 1 | 0 | 176.7389 | 0
| FRAME | LOAD | DIST | P | V2 | M3
| 31 | ULTIMATE MIN | 0 | -96.2565 | 0 | -80.2748
| 31 | ULTIMATE MIN | 1 | -96.2565 | 0 | -105.7071
| 32 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 32 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 32 | ULTIMATE MIN | 0 | -96.2566 | -176.7389 | -105.7071
| 32 | ULTIMATE MIN | 1 | -96.2566 | -162.3589 | -80.2748
| 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 33 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 33 | ULTIMATE MIN | 0 | -96.2566 | -162.3589 | -80.2748
| 33 | ULTIMATE MIN | 1 | -96.2566 | -135.516 | -38.5723
| 34 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 34 | ULTIMATE MAX | 0.25 | 0 | 0 | 3.7682
| 34 | ULTIMATE MAX | 0.5 | 0 | 0 | 27.0481
| 34 | ULTIMATE MAX | 0.75 | 0 | 0 | 45.2936
| 34 | ULTIMATE MAX | 1 | 0 | 0.13581 | 55.4128
| 34 | ULTIMATE MIN | 0 | -96.2566 | -135.516 | -38.5723
| 34 | ULTIMATE MIN | 0.25 | -96.2566 | -106.2765 | -1.6989
| 34 | ULTIMATE MIN | 0.5 | -96.2566 | -77.037 | 0
| 34 | ULTIMATE MIN | 0.75 | -96.2566 | -47.7975 | 0
| 34 | ULTIMATE MIN | 1 | -96.2566 | -18.5579 | 0
| 35 | ULTIMATE MAX | 0 | 0 | 0.13003 | 55.4128
| 35 | ULTIMATE MAX | 0.25 | 0 | 21.2155 | 56.614
| 35 | ULTIMATE MAX | 0.5 | 0 | 50.455 | 48.8971
| 35 | ULTIMATE MAX | 0.75 | 0 | 79.6946 | 32.2621
| 35 | ULTIMATE MAX | 1 | 0 | 108.9341 | 6.7091
| 35 | ULTIMATE MIN | 0 | -96.2566 | -18.5593 | 0
| 35 | ULTIMATE MIN | 0.25 | -96.2566 | 0 | 0
| 35 | ULTIMATE MIN | 0.5 | -96.2566 | 0 | 0
| 35 | ULTIMATE MIN | 0.75 | -96.2566 | 0 | 0
| 35 | ULTIMATE MIN | 1 | -96.2566 | 0 | -18.8217
| 36 | ULTIMATE MAX | 0 | 0 | 108.9341 | 6.7091
| 36 | ULTIMATE MAX | 1 | 0 | 135.7769 | 0
| 36 | ULTIMATE MIN | 0 | -96.2566 | 0 | -18.8217
| 36 | ULTIMATE MIN | 1 | -96.2566 | 0 | -46.0373
| 37 | ULTIMATE MAX | 0 | 0 | 135.7769 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 150.157 | 0
| 37 | ULTIMATE MIN | 0 | -96.2566 | 0 | -46.0373
| 37 | ULTIMATE MIN | 1 | -96.2566 | 0 | -67.4812
| 38 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 38 | ULTIMATE MIN | 0 | -150.157 | -96.2566 | -67.4812
| 38 | ULTIMATE MIN | 1 | -151.7005 | -88.8386 | -51.2786
| 39 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 39 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 39 | ULTIMATE MIN | 0 | -151.7005 | -88.8387 | -51.2786
| 39 | ULTIMATE MIN | 1 | -153.7291 | -78.3814 | -32.0329
| 40 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 40 | ULTIMATE MAX | 0.25 | 0 | 0 | 13.828
| 40 | ULTIMATE MAX | 0.5 | 0 | 0 | 30.4599
| 40 | ULTIMATE MAX | 0.75 | 0 | 39.2111 | 20.2699
| 40 | ULTIMATE MAX | 1 | 0 | 90.6438 | 0
| 40 | ULTIMATE MIN | 0 | -153.7291 | -78.3829 | -32.0329
| 40 | ULTIMATE MIN | 0.25 | -159.3298 | -45.3373 | -7.091
| 40 | ULTIMATE MIN | 0.5 | -164.9305 | -6.1626 | 0
| 40 | ULTIMATE MIN | 0.75 | -170.5312 | 0 | -4.0123
| 40 | ULTIMATE MIN | 1 | -176.1319 | 0 | -26.7627
| 41 | ULTIMATE MAX | 0 | 0 | 90.6438 | 0
| 41 | ULTIMATE MAX | 1 | 0 | 110.785 | 0
| 41 | ULTIMATE MIN | 0 | -176.1319 | 0 | -26.7627
| 41 | ULTIMATE MIN | 1 | -178.1605 | 0 | -49.896
| 42 | ULTIMATE MAX | 0 | 0 | 110.785 | 0
| 42 | ULTIMATE MAX | 1 | 0 | 126.6485 | 0
| 42 | ULTIMATE MIN | 0 | -178.1605 | 0 | -49.896
| 42 | ULTIMATE MIN | 1 | -179.704 | 0 | -70.6527
| 43 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 43 | ULTIMATE MAX | 0.25 | 0 | 0 | 0
| 43 | ULTIMATE MAX | 0.5 | 0 | 0 | 7e-06
| 43 | ULTIMATE MAX | 0.75 | 0 | 0 | 0.000101
| 43 | ULTIMATE MAX | 1 | 0 | 0 | 0.000195
| 43 | ULTIMATE MIN | 0 | -353.4779 | -0.000112 | -0.000181
| 43 | ULTIMATE MIN | 0.25 | -360.8646 | -0.000112 | -8.7e-05
| 43 | ULTIMATE MIN | 0.5 | -368.2514 | -0.000112 | 0
| 43 | ULTIMATE MIN | 0.75 | -375.6381 | -0.000112 | 0
| 43 | ULTIMATE MIN | 1 | -383.0249 | -0.000112 | 0
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0 | 0 | 0 | 0 | 17 | SERVICE MIN | 0 | -80.561 | 0 | 0
| 1 | SERVICE MAX | 1 | 0 | 0 | 0 | 17 | SERVICE MIN | 0.5 | -80.561 | 0 | 0
| 1 | SERVICE MIN | 0 | -80.561 | -86.3358 | -46.2379 | 17 | SERVICE MIN | 1 | -80.561 | 0 | -3.4643
| 1 | SERVICE MIN | 1 | -80.561 | -87.622 | -33.1918 | 18 | SERVICE MAX | 0 | 0 | 91.052 | 13.8533
| 2 | SERVICE MAX | 0 | 0 | 0 | 0 | 18 | SERVICE MAX | 1 | 0 | 90.023 | 3.8094
| 2 | SERVICE MAX | 1 | 0 | 0 | 3.8094 | 18 | SERVICE MIN | 0 | -80.561 | 0 | -3.4643
| 2 | SERVICE MIN | 0 | -80.561 | -87.622 | -33.1918 | 18 | SERVICE MIN | 1 | -80.561 | 0 | -12.5259
| 2 | SERVICE MIN | 1 | -80.561 | -90.023 | -12.526 | 19 | SERVICE MAX | 0 | 0 | 90.023 | 3.8094
| 3 | SERVICE MAX | 0 | 0 | 0 | 3.8094 | 19 | SERVICE MAX | 1 | 0 | 87.622 | 0
| 3 | SERVICE MAX | 1 | 0 | 0 | 13.8533 | 19 | SERVICE MIN | 0 | -80.561 | 0 | -12.5259
| 3 | SERVICE MIN | 0 | -80.561 | -90.023 | -12.526 | 19 | SERVICE MIN | 1 | -80.561 | 0 | -33.1918
| 3 | SERVICE MIN | 1 | -80.561 | -91.052 | -3.4645 | 20 | SERVICE MAX | 0 | 0 | 87.622 | 0
| 4 | SERVICE MAX | 0 | 0 | 0 | 13.8533 | 20 | SERVICE MAX | 1 | 0 | 86.3358 | 0
| 4 | SERVICE MAX | 0.5 | 0 | 0 | 25.4381 | 20 | SERVICE MIN | 0 | -80.561 | 0 | -33.1918
| 4 | SERVICE MAX | 1 | 0 | 0 | 37.6715 | 20 | SERVICE MIN | 1 | -80.561 | 0 | -46.2379
| 4 | SERVICE MIN | 0 | -80.561 | -47.721 | -3.4645 | 21 | SERVICE MAX | 0 | 0 | 0 | 0
| 4 | SERVICE MIN | 0.5 | -80.561 | -50.0792 | 0 | 21 | SERVICE MAX | 1 | 0 | 0 | 0
| 4 | SERVICE MIN | 1 | -80.561 | -52.4373 | 0 | 21 | SERVICE MIN | 0 | -120.5904 | -80.561 | -46.2379
| 5 | SERVICE MAX | 0 | 0 | 0 | 37.6715 | 21 | SERVICE MIN | 1 | -119.3041 | -70.6463 | -33.1244
| 5 | SERVICE MAX | 0.5 | 0 | 0 | 38.9619 | 22 | SERVICE MAX | 0 | 0 | 0 | 0
| 5 | SERVICE MAX | 1 | 0 | 0 | 40.9008 | 22 | SERVICE MAX | 1 | 0 | 0 | 0
| 5 | SERVICE MIN | 0 | -80.561 | -11.0134 | 0 | 22 | SERVICE MIN | 0 | -119.3041 | -70.6463 | -33.1244
| 5 | SERVICE MIN | 0.5 | -80.561 | -13.3715 | 0 | 22 | SERVICE MIN | 1 | -117.6136 | -58.0581 | -18.4814
| 5 | SERVICE MIN | 1 | -80.561 | -15.7296 | 0 | 23 | SERVICE MAX | 0 | 0 | 0 | 0
| 6 | SERVICE MAX | 0 | 0 | 33.6329 | 40.9008 | 23 | SERVICE MAX | 0.25 | 0 | 0 | 10.491
| 6 | SERVICE MAX | 0.5 | 0 | 31.2747 | 31.976 | 23 | SERVICE MAX | 0.5 | 0 | 3.0486 | 17.7522
| 6 | SERVICE MAX | 1 | 0 | 28.9166 | 23.6997 | 23 | SERVICE MAX | 0.75 | 0 | 27.5328 | 8.2496
| 6 | SERVICE MIN | 0 | -80.561 | 0 | 0 | 23 | SERVICE MAX | 1 | 0 | 48.1863 | 0
| 6 | SERVICE MIN | 0.5 | -80.561 | 0 | 0 | 23 | SERVICE MIN | 0 | -117.6136 | -58.0581 | -18.4814
| 6 | SERVICE MIN | 1 | -80.561 | 0 | 0 | 23 | SERVICE MIN | 0.25 | -112.9464 | -25.9126 | -3.7524
| 7 | SERVICE MAX | 0 | 0 | 71.3925 | 23.6997 | 23 | SERVICE MIN | 0.5 | -108.2791 | 0 | -0.013437
| 7 | SERVICE MAX | 0.5 | 0 | 69.0344 | 5.8759 | 23 | SERVICE MIN | 0.75 | -103.6119 | 0 | -4.6564
| 7 | SERVICE MAX | 1 | 0 | 66.6763 | 0 | 23 | SERVICE MIN | 1 | -98.9446 | 0 | -19.7352
| 7 | SERVICE MIN | 0 | -80.561 | 0 | 0 | 24 | SERVICE MAX | 0 | 0 | 48.1853 | 0
| 7 | SERVICE MIN | 0.5 | -80.561 | 0 | 0 | 24 | SERVICE MAX | 1 | 0 | 54.7211 | 0
| 7 | SERVICE MIN | 1 | -80.561 | 0 | -14.2692 | 24 | SERVICE MIN | 0 | -98.9446 | 0 | -19.7352
| 8 | SERVICE MAX | 0 | 0 | 110.2712 | 0 | 24 | SERVICE MIN | 1 | -97.2541 | 0 | -31.579
| 8 | SERVICE MAX | 1 | 0 | 109.2422 | 0 | 25 | SERVICE MAX | 0 | 0 | 54.7211 | 0
| 8 | SERVICE MIN | 0 | -80.561 | 0 | -14.2692 | 25 | SERVICE MAX | 1 | 0 | 59.3574 | 0
| 8 | SERVICE MIN | 1 | -80.561 | 0 | -27.44 | 25 | SERVICE MIN | 0 | -97.2541 | 0 | -31.579
| 9 | SERVICE MAX | 0 | 0 | 109.2422 | 0 | 25 | SERVICE MIN | 1 | -95.9679 | 0 | -41.5651
| 9 | SERVICE MAX | 1 | 0 | 106.8412 | 0 | 26 | SERVICE MAX | 0 | 0 | 0 | 0
| 9 | SERVICE MIN | 0 | -80.561 | 0 | -27.44 | 26 | SERVICE MAX | 1 | 0 | 0 | 0
| 9 | SERVICE MIN | 1 | -80.561 | 0 | -57.6917 | 26 | SERVICE MIN | 0 | -59.3573 | -95.9679 | -41.5651
| 10 | SERVICE MAX | 0 | 0 | 106.8412 | 0 | 26 | SERVICE MIN | 1 | -59.3573 | -86.6587 | -27.8689
| 10 | SERVICE MAX | 1 | 0 | 105.555 | 0 | 27 | SERVICE MAX | 0 | 0 | 0 | 0
| 10 | SERVICE MIN | 0 | -80.561 | 0 | -57.6917 | 27 | SERVICE MAX | 1 | 0 | 0 | 5.5174
| 10 | SERVICE MIN | 1 | -80.561 | 0 | -73.6214 | 27 | SERVICE MIN | 0 | -59.3573 | -86.6587 | -27.8689
| 11 | SERVICE MAX | 0 | 0 | 0 | 0 | 27 | SERVICE MIN | 1 | -59.3573 | -69.2817 | -9.4468
| 11 | SERVICE MAX | 1 | 0 | 0 | 0 | 28 | SERVICE MAX | 0 | 0 | 0 | 5.5174
| 11 | SERVICE MIN | 0 | -80.561 | -105.555 | -73.6214 | 28 | SERVICE MAX | 0.25 | 0 | 0 | 21.7537
| 11 | SERVICE MIN | 1 | -80.561 | -106.8412 | -57.6917 | 28 | SERVICE MAX | 0.5 | 0 | 0 | 32.2167
| 12 | SERVICE MAX | 0 | 0 | 0 | 0 | 28 | SERVICE MAX | 0.75 | 0 | 0 | 36.9066
| 12 | SERVICE MAX | 1 | 0 | 0 | 0 | 28 | SERVICE MAX | 1 | 0 | 13.0169 | 35.8233
| 12 | SERVICE MIN | 0 | -80.561 | -106.8412 | -57.6917 | 28 | SERVICE MIN | 0 | -59.3573 | -69.2817 | -9.4468
| 12 | SERVICE MIN | 1 | -80.561 | -109.2422 | -27.44 | 28 | SERVICE MIN | 0.25 | -59.3573 | -50.3532 | 0
| 13 | SERVICE MAX | 0 | 0 | 0 | 0 | 28 | SERVICE MIN | 0.5 | -59.3573 | -31.4246 | 0
| 13 | SERVICE MAX | 1 | 0 | 0 | 0 | 28 | SERVICE MIN | 0.75 | -59.3573 | -12.4961 | 0
| 13 | SERVICE MIN | 0 | -80.561 | -109.2422 | -27.44 | 28 | SERVICE MIN | 1 | -59.3573 | 0 | 0
| 13 | SERVICE MIN | 1 | -80.561 | -110.2712 | -14.2692 | 29 | SERVICE MAX | 0 | 0 | 13.0162 | 35.8233
| 14 | SERVICE MAX | 0 | 0 | 0 | 0 | 29 | SERVICE MAX | 0.25 | 0 | 31.9447 | 28.9668
| 14 | SERVICE MAX | 0.5 | 0 | 0 | 5.8759 | 29 | SERVICE MAX | 0.5 | 0 | 50.8732 | 16.8319
| 14 | SERVICE MAX | 1 | 0 | 0 | 23.6997 | 29 | SERVICE MAX | 0.75 | 0 | 69.8018 | 0.59843
| 14 | SERVICE MIN | 0 | -80.561 | -66.6763 | -14.2692 | 29 | SERVICE MAX | 1 | 0 | 88.7303 | 0
| 14 | SERVICE MIN | 0.5 | -80.561 | -69.0344 | 0 | 29 | SERVICE MIN | 0 | -59.3572 | 0 | 0
| 14 | SERVICE MIN | 1 | -80.561 | -71.3925 | 0 | 29 | SERVICE MIN | 0.25 | -59.3572 | 0 | 0
| 15 | SERVICE MAX | 0 | 0 | 0 | 23.6997 | 29 | SERVICE MIN | 0.5 | -59.3572 | 0 | 0
| 15 | SERVICE MAX | 0.5 | 0 | 0 | 31.976 | 29 | SERVICE MIN | 0.75 | -59.3572 | 0 | -2.0659
| 15 | SERVICE MAX | 1 | 0 | 0 | 40.9008 | 29 | SERVICE MIN | 1 | -59.3572 | 0 | -26.2421
| 15 | SERVICE MIN | 0 | -80.561 | -28.9166 | 0 | 30 | SERVICE MAX | 0 | 0 | 88.7303 | 0
| 15 | SERVICE MIN | 0.5 | -80.561 | -31.2747 | 0 | 30 | SERVICE MAX | 1 | 0 | 106.1074 | 0
| 15 | SERVICE MIN | 1 | -80.561 | -33.6329 | 0 | 30 | SERVICE MIN | 0 | -59.3572 | 0 | -26.2421
| 16 | SERVICE MAX | 0 | 0 | 15.7296 | 40.9008 | 30 | SERVICE MIN | 1 | -59.3572 | 0 | -53.5194
| 16 | SERVICE MAX | 0.5 | 0 | 13.3715 | 38.9619 | 31 | SERVICE MAX | 0 | 0 | 106.1074 | 0
| 16 | SERVICE MAX | 1 | 0 | 11.0134 | 37.6715 | 31 | SERVICE MAX | 1 | 0 | 115.4165 | 0
| 16 | SERVICE MIN | 0 | -80.561 | 0 | 0 | 31 | SERVICE MIN | 0 | -59.3572 | 0 | -53.5194
| 16 | SERVICE MIN | 0.5 | -80.561 | 0 | 0 | 31 | SERVICE MIN | 1 | -59.3572 | 0 | -70.1336
| 16 | SERVICE MIN | 1 | -80.561 | 0 | 0 | 32 | SERVICE MAX | 0 | 0 | 0 | 0
| 17 | SERVICE MAX | 0 | 0 | 52.4373 | 37.6715 | 32 | SERVICE MAX | 1 | 0 | 0 | 0
| 17 | SERVICE MAX | 0.5 | 0 | 50.0792 | 25.4381 | 32 | SERVICE MIN | 0 | -59.3573 | -115.4165 | -70.1336
| 17 | SERVICE MAX | 1 | 0 | 47.721 | 13.8533 | 32 | SERVICE MIN | 1 | -59.3573 | -106.1074 | -53.5194
| FRAME | LOAD | DIST | P | V2 | M3
| 33 | SERVICE MAX | 0 | 0 | 0 | 0
| 33 | SERVICE MAX | 1 | 0 | 0 | 0
| 33 | SERVICE MIN | 0 | -59.3573 | -106.1074 | -53.5194
| 33 | SERVICE MIN | 1 | -59.3573 | -88.7303 | -26.2421
| 34 | SERVICE MAX | 0 | 0 | 0 | 0
| 34 | SERVICE MAX | 0.25 | 0 | 0 | 0.59837
| 34 | SERVICE MAX | 0.5 | 0 | 0 | 16.8319
| 34 | SERVICE MAX | 0.75 | 0 | 0 | 28.9668
| 34 | SERVICE MAX | 1 | 0 | 0 | 35.8233
| 34 | SERVICE MIN | 0 | -59.3573 | -88.7303 | -26.2421
| 34 | SERVICE MIN | 0.25 | -59.3573 | -69.8018 | -2.0659
| 34 | SERVICE MIN | 0.5 | -59.3573 | -50.8732 | 0
| 34 | SERVICE MIN | 0.75 | -59.3573 | -31.9447 | 0
| 34 | SERVICE MIN | 1 | -59.3573 | -13.0162 | 0
| 35 | SERVICE MAX | 0 | 0 | 0 | 35.8233
| 35 | SERVICE MAX | 0.25 | 0 | 12.4961 | 36.9066
| 35 | SERVICE MAX | 0.5 | 0 | 31.4246 | 32.2167
| 35 | SERVICE MAX | 0.75 | 0 | 50.3532 | 21.7537
| 35 | SERVICE MAX | 1 | 0 | 69.2817 | 5.5174
| 35 | SERVICE MIN | 0 | -59.3573 | -13.017 | 0
| 35 | SERVICE MIN | 0.25 | -59.3573 | 0 | 0
| 35 | SERVICE MIN | 0.5 | -59.3573 | 0 | 0
| 35 | SERVICE MIN | 0.75 | -59.3573 | 0 | 0
| 35 | SERVICE MIN | 1 | -59.3573 | 0 | -9.4467
| 36 | SERVICE MAX | 0 | 0 | 69.2817 | 5.5174
| 36 | SERVICE MAX | 1 | 0 | 86.6587 | 0
| 36 | SERVICE MIN | 0 | -59.3573 | 0 | -9.4467
| 36 | SERVICE MIN | 1 | -59.3573 | 0 | -27.8688
| 37 | SERVICE MAX | 0 | 0 | 86.6587 | 0
| 37 | SERVICE MAX | 1 | 0 | 95.9679 | 0
| 37 | SERVICE MIN | 0 | -59.3573 | 0 | -27.8688
| 37 | SERVICE MIN | 1 | -59.3573 | 0 | -41.565
| 38 | SERVICE MAX | 0 | 0 | 0 | 0
| 38 | SERVICE MAX | 1 | 0 | 0 | 0
| 38 | SERVICE MIN | 0 | -95.9679 | -59.3573 | -41.565
| 38 | SERVICE MIN | 1 | -97.2541 | -54.721 | -31.5789
| 39 | SERVICE MAX | 0 | 0 | 0 | 0
| 39 | SERVICE MAX | 1 | 0 | 0 | 0
| 39 | SERVICE MIN | 0 | -97.2541 | -54.7211 | -31.5789
| 39 | SERVICE MIN | 1 | -98.9446 | -48.1853 | -19.7351
| 40 | SERVICE MAX | 0 | 0 | 0 | 0
| 40 | SERVICE MAX | 0.25 | 0 | 0 | 8.2497
| 40 | SERVICE MAX | 0.5 | 0 | 0 | 17.7522
| 40 | SERVICE MAX | 0.75 | 0 | 25.9126 | 10.491
| 40 | SERVICE MAX | 1 | 0 | 58.0581 | 0
| 40 | SERVICE MIN | 0 | -98.9446 | -48.1862 | -19.7351
| 40 | SERVICE MIN | 0.25 | -103.6119 | -27.5327 | -4.6564
| 40 | SERVICE MIN | 0.5 | -108.2791 | -3.0485 | -0.013437
| 40 | SERVICE MIN | 0.75 | -112.9464 | 0 | -3.7524
| 40 | SERVICE MIN | 1 | -117.6136 | 0 | -18.4814
| 41 | SERVICE MAX | 0 | 0 | 58.0581 | 0
| 41 | SERVICE MAX | 1 | 0 | 70.6463 | 0
| 41 | SERVICE MIN | 0 | -117.6136 | 0 | -18.4814
| 41 | SERVICE MIN | 1 | -119.3041 | 0 | -33.1244
| 42 | SERVICE MAX | 0 | 0 | 70.6463 | 0
| 42 | SERVICE MAX | 1 | 0 | 80.561 | 0
| 42 | SERVICE MIN | 0 | -119.3041 | 0 | -33.1244
| 42 | SERVICE MIN | 1 | -120.5904 | 0 | -46.2379
| 43 | SERVICE MAX | 0 | 0 | 0 | 0
| 43 | SERVICE MAX | 0.25 | 0 | 0 | 0
| 43 | SERVICE MAX | 0.5 | 0 | 0 | 4e-06
| 43 | SERVICE MAX | 0.75 | 0 | 0 | 6.4e-05
| 43 | SERVICE MAX | 1 | 0 | 0 | 0.000123
| 43 | SERVICE MIN | 0 | -230.833 | -7.1e-05 | -0.000115
| 43 | SERVICE MIN | 0.25 | -236.9886 | -7.1e-05 | -5.5e-05
| 43 | SERVICE MIN | 0.5 | -243.1442 | -7.1e-05 | 0
| 43 | SERVICE MIN | 0.75 | -249.2998 | -7.1e-05 | 0
| 43 | SERVICE MIN | 1 | -255.4555 | -7.1e-05 | 0

## OUTPUT(붕괴방지)
16. OUTPUT DATA (붕괴방지)
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0 | 8.09 | 0 | 9.8446 | 17 | ULTIMATE MAX | 0 | 7.5672 | 10.5138 | 28.9087
| 1 | ULTIMATE MAX | 1 | 7.9658 | 0 | 13.584 | 17 | ULTIMATE MAX | 0.5 | 7.795 | 8.1557 | 26.3416
| 1 | ULTIMATE MIN | 0 | 0 | -24.8396 | 0 | 17 | ULTIMATE MAX | 1 | 8.0228 | 5.7976 | 24.4991
| 1 | ULTIMATE MIN | 1 | 0 | -26.1258 | 0 | 17 | ULTIMATE MIN | 0 | 0 | 0 | 0
| 2 | ULTIMATE MAX | 0 | 7.9658 | 0 | 13.584 | 17 | ULTIMATE MIN | 0.5 | 0 | 0 | 0
| 2 | ULTIMATE MAX | 1 | 7.7338 | 0 | 21.0805 | 17 | ULTIMATE MIN | 1 | 0 | 0 | 0
| 2 | ULTIMATE MIN | 0 | 0 | -26.1258 | 0 | 18 | ULTIMATE MAX | 0 | 7.6344 | 29.5558 | 24.4991
| 2 | ULTIMATE MIN | 1 | 0 | -28.5268 | 0 | 18 | ULTIMATE MAX | 1 | 7.7338 | 28.5268 | 21.0805
| 3 | ULTIMATE MAX | 0 | 7.7338 | 0 | 21.0805 | 18 | ULTIMATE MIN | 0 | 0 | 0 | 0
| 3 | ULTIMATE MAX | 1 | 7.6344 | 0 | 24.4991 | 18 | ULTIMATE MIN | 1 | 0 | 0 | 0
| 3 | ULTIMATE MIN | 0 | 0 | -28.5268 | 0 | 19 | ULTIMATE MAX | 0 | 7.7338 | 28.5268 | 21.0805
| 3 | ULTIMATE MIN | 1 | 0 | -29.5558 | 0 | 19 | ULTIMATE MAX | 1 | 7.9658 | 26.1258 | 13.584
| 4 | ULTIMATE MAX | 0 | 8.0228 | 0 | 24.4991 | 19 | ULTIMATE MIN | 0 | 0 | 0 | 0
| 4 | ULTIMATE MAX | 0.5 | 7.795 | 0 | 26.3416 | 19 | ULTIMATE MIN | 1 | 0 | 0 | 0
| 4 | ULTIMATE MAX | 1 | 7.5672 | 0 | 28.9087 | 20 | ULTIMATE MAX | 0 | 7.9658 | 26.1258 | 13.584
| 4 | ULTIMATE MIN | 0 | 0 | -5.7976 | 0 | 20 | ULTIMATE MAX | 1 | 8.09 | 24.8396 | 9.8446
| 4 | ULTIMATE MIN | 0.5 | 0 | -8.1557 | 0 | 20 | ULTIMATE MIN | 0 | 0 | 0 | 0
| 4 | ULTIMATE MIN | 1 | 0 | -10.5138 | 0 | 20 | ULTIMATE MIN | 1 | 0 | 0 | 0
| 5 | ULTIMATE MAX | 0 | 7.9583 | 15.3313 | 28.9087 | 21 | ULTIMATE MAX | 0 | 0 | 7.7921 | 9.8446
| 5 | ULTIMATE MAX | 0.5 | 7.7305 | 12.9732 | 25.2018 | 21 | ULTIMATE MAX | 1 | 0 | 7.9999 | 8.7683
| 5 | ULTIMATE MAX | 1 | 7.5027 | 10.6151 | 22.1434 | 21 | ULTIMATE MIN | 0 | -53.5604 | 0 | 0
| 5 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 21 | ULTIMATE MIN | 1 | -52.2216 | 0 | 0
| 5 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 22 | ULTIMATE MAX | 0 | 0 | 7.9999 | 8.7683
| 5 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 22 | ULTIMATE MAX | 1 | 0 | 8.3291 | 7.4151
| 6 | ULTIMATE MAX | 0 | 7.8966 | 38.9672 | 22.1434 | 22 | ULTIMATE MIN | 0 | -52.2216 | 0 | 0
| 6 | ULTIMATE MAX | 0.5 | 7.6688 | 36.6091 | 11.9787 | 22 | ULTIMATE MIN | 1 | -50.4621 | 0 | 0
| 6 | ULTIMATE MAX | 1 | 7.4411 | 34.251 | 2.4627 | 23 | ULTIMATE MAX | 0 | 0 | 8.3291 | 7.4151
| 6 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 23 | ULTIMATE MAX | 1 | 0 | 8.5814 | 6.5598
| 6 | ULTIMATE MIN | 0.5 | 0 | 0 | 0 | 23 | ULTIMATE MIN | 0 | -50.4621 | 0 | 0
| 6 | ULTIMATE MIN | 1 | 0 | 0 | 0 | 23 | ULTIMATE MIN | 1 | -49.2917 | 0 | 0
| 7 | ULTIMATE MAX | 0 | 7.8377 | 66.8661 | 2.4628 | 24 | ULTIMATE MAX | 0 | 0 | 8.5814 | 6.5598
| 7 | ULTIMATE MAX | 0.5 | 7.6099 | 64.508 | 0 | 24 | ULTIMATE MAX | 0.5 | 0 | 9.1069 | 4.2511
| 7 | ULTIMATE MAX | 1 | 7.3821 | 62.1498 | 0 | 24 | ULTIMATE MAX | 1 | 0 | 9.7161 | 2.101
| 7 | ULTIMATE MIN | 0 | 0 | 0 | 0 | 24 | ULTIMATE MIN | 0 | -62.1176 | 0 | 0
| 7 | ULTIMATE MIN | 0.5 | 0 | 0 | -16.667 | 24 | ULTIMATE MIN | 0.5 | -59.9795 | 0 | 0
| 7 | ULTIMATE MIN | 1 | 0 | 0 | -34.0824 | 24 | ULTIMATE MIN | 1 | -57.8822 | 0 | -0.18557
| 8 | ULTIMATE MAX | 0 | 7.7814 | 99.0324 | 0 | 25 | ULTIMATE MAX | 0 | 0 | 12.4724 | 2.101
| 8 | ULTIMATE MAX | 1 | 7.6821 | 98.0034 | 0 | 25 | ULTIMATE MAX | 0.5 | 0 | 11.7845 | 0
| 8 | ULTIMATE MIN | 0 | 0 | 0 | -34.0824 | 25 | ULTIMATE MAX | 1 | 0 | 12.259 | 0
| 8 | ULTIMATE MIN | 1 | 0 | 0 | -45.9046 | 25 | ULTIMATE MIN | 0 | -70.7256 | 0 | -0.18553
| 9 | ULTIMATE MAX | 0 | 7.6821 | 98.0034 | 0 | 25 | ULTIMATE MIN | 0.5 | -68.7587 | 0 | -3.2949
| 9 | ULTIMATE MAX | 1 | 7.4501 | 95.6024 | 0 | 25 | ULTIMATE MIN | 1 | -66.7917 | 0 | -6.6068
| 9 | ULTIMATE MIN | 0 | 0 | 0 | -45.9046 | 26 | ULTIMATE MAX | 0 | 0 | 18.4257 | 0
| 9 | ULTIMATE MIN | 1 | 0 | 0 | -73.0094 | 26 | ULTIMATE MAX | 0.5 | 0 | 17.5933 | 0
| 10 | ULTIMATE MAX | 0 | 7.4501 | 95.6024 | 0 | 26 | ULTIMATE MAX | 1 | 0 | 16.8929 | 0
| 10 | ULTIMATE MAX | 1 | 7.3259 | 94.3162 | 0 | 26 | ULTIMATE MIN | 0 | -79.6823 | 0 | -6.6068
| 10 | ULTIMATE MIN | 0 | 0 | 0 | -73.0094 | 26 | ULTIMATE MIN | 0.5 | -77.7153 | 0 | -10.9531
| 10 | ULTIMATE MIN | 1 | 0 | 0 | -87.2533 | 26 | ULTIMATE MIN | 1 | -75.7484 | 0 | -15.5402
| 11 | ULTIMATE MAX | 0 | 7.3259 | 0 | 0 | 27 | ULTIMATE MAX | 0 | 0 | 25.6746 | 0
| 11 | ULTIMATE MAX | 1 | 7.4501 | 0 | 0 | 27 | ULTIMATE MAX | 0.5 | 0 | 24.722 | 0
| 11 | ULTIMATE MIN | 0 | 0 | -94.3162 | -87.2533 | 27 | ULTIMATE MAX | 1 | 0 | 23.7157 | 0
| 11 | ULTIMATE MIN | 1 | 0 | -95.6024 | -73.0094 | 27 | ULTIMATE MIN | 0 | -88.6923 | 0 | -15.5402
| 12 | ULTIMATE MAX | 0 | 7.4501 | 0 | 0 | 27 | ULTIMATE MIN | 0.5 | -86.7218 | 0 | -21.4241
| 12 | ULTIMATE MAX | 1 | 7.6821 | 0 | 0 | 27 | ULTIMATE MIN | 1 | -84.7513 | 0 | -28.0937
| 12 | ULTIMATE MIN | 0 | 0 | -95.6024 | -73.0094 | 28 | ULTIMATE MAX | 0 | 0 | 31.9969 | 0
| 12 | ULTIMATE MIN | 1 | 0 | -98.0034 | -45.9046 | 28 | ULTIMATE MAX | 1 | 0 | 31.4229 | 0
| 13 | ULTIMATE MAX | 0 | 7.6821 | 0 | 0 | 28 | ULTIMATE MIN | 0 | -97.7548 | 0 | -28.0937
| 13 | ULTIMATE MAX | 1 | 7.7814 | 0 | 0 | 28 | ULTIMATE MIN | 1 | -96.6761 | 0 | -32.9456
| 13 | ULTIMATE MIN | 0 | 0 | -98.0034 | -45.9046 | 29 | ULTIMATE MAX | 0 | 0 | 31.4229 | 0
| 13 | ULTIMATE MIN | 1 | 0 | -99.0324 | -34.0824 | 29 | ULTIMATE MAX | 1 | 0 | 30.5347 | 0
| 14 | ULTIMATE MAX | 0 | 7.3821 | 0 | 0 | 29 | ULTIMATE MIN | 0 | -96.6761 | 0 | -32.9456
| 14 | ULTIMATE MAX | 0.5 | 7.6099 | 0 | 0 | 29 | ULTIMATE MIN | 1 | -95.0546 | 0 | -40.0712
| 14 | ULTIMATE MAX | 1 | 7.8377 | 0 | 2.4628 | 30 | ULTIMATE MAX | 0 | 0 | 30.5347 | 0
| 14 | ULTIMATE MIN | 0 | 0 | -62.1498 | -34.0824 | 30 | ULTIMATE MAX | 1 | 0 | 29.8395 | 0
| 14 | ULTIMATE MIN | 0.5 | 0 | -64.508 | -16.667 | 30 | ULTIMATE MIN | 0 | -95.0546 | 0 | -40.0712
| 14 | ULTIMATE MIN | 1 | 0 | -66.8661 | 0 | 30 | ULTIMATE MIN | 1 | -93.8209 | 0 | -45.3542
| 15 | ULTIMATE MAX | 0 | 7.4411 | 0 | 2.4627 | 31 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MAX | 0.5 | 7.6688 | 0 | 11.9787 | 31 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 15 | ULTIMATE MAX | 1 | 7.8966 | 0 | 22.1434 | 31 | ULTIMATE MIN | 0 | -32.9709 | -104.454 | -45.3542
| 15 | ULTIMATE MIN | 0 | 0 | -34.251 | 0 | 31 | ULTIMATE MIN | 1 | -32.6557 | -95.1448 | -30.3843
| 15 | ULTIMATE MIN | 0.5 | 0 | -36.6091 | 0 | 32 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 15 | ULTIMATE MIN | 1 | 0 | -38.9672 | 0 | 32 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 16 | ULTIMATE MAX | 0 | 7.5027 | 0 | 22.1434 | 32 | ULTIMATE MIN | 0 | -32.6557 | -95.1448 | -30.3843
| 16 | ULTIMATE MAX | 0.5 | 7.7305 | 0 | 25.2018 | 32 | ULTIMATE MIN | 1 | -32.0675 | -77.7678 | -6.1765
| 16 | ULTIMATE MAX | 1 | 7.9583 | 0 | 28.9087 | 33 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 16 | ULTIMATE MIN | 0 | 0 | -10.6151 | 0 | 33 | ULTIMATE MAX | 1 | 0 | 0 | 5.4705
| 16 | ULTIMATE MIN | 0.5 | 0 | -12.9732 | 0 | 33 | ULTIMATE MIN | 0 | -32.0675 | -77.7678 | -6.1765
| 16 | ULTIMATE MIN | 1 | 0 | -15.3313 | 0 | 33 | ULTIMATE MIN | 1 | -31.8154 | -70.3205 | 0
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 34 | ULTIMATE MAX | 0 | 0 | 0 | 5.4703 | 51 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 34 | ULTIMATE MAX | 0.5 | 0 | 0 | 22.1126 | 51 | ULTIMATE MIN | 0 | -93.8209 | -29.8395 | -45.3542
| 34 | ULTIMATE MAX | 1 | 0 | 0 | 34.0615 | 51 | ULTIMATE MIN | 1 | -95.0546 | -30.5347 | -40.0712
| 34 | ULTIMATE MIN | 0 | -32.4898 | -70.3201 | 0 | 52 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 34 | ULTIMATE MIN | 0.5 | -31.912 | -53.2534 | 0 | 52 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 34 | ULTIMATE MIN | 1 | -31.3343 | -36.1867 | 0 | 52 | ULTIMATE MIN | 0 | -95.0546 | -30.5347 | -40.0712
| 35 | ULTIMATE MAX | 0 | 0 | 0 | 34.0615 | 52 | ULTIMATE MIN | 1 | -96.6761 | -31.4229 | -32.9456
| 35 | ULTIMATE MAX | 0.5 | 0 | 0 | 41.3169 | 53 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 35 | ULTIMATE MAX | 1 | 0 | 0 | 43.879 | 53 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 35 | ULTIMATE MIN | 0 | -32.0201 | -36.1862 | 0 | 53 | ULTIMATE MIN | 0 | -96.6761 | -31.4229 | -32.9456
| 35 | ULTIMATE MIN | 0.5 | -31.4423 | -19.1195 | 0 | 53 | ULTIMATE MIN | 1 | -97.7548 | -31.9969 | -28.0937
| 35 | ULTIMATE MIN | 1 | -30.8646 | -2.0528 | 0 | 54 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 36 | ULTIMATE MAX | 0 | 0 | 0 | 43.879 | 54 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 36 | ULTIMATE MAX | 0.5 | 0 | 16.284 | 41.7475 | 54 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 36 | ULTIMATE MAX | 1 | 0 | 33.3507 | 34.9228 | 54 | ULTIMATE MIN | 0 | -84.7513 | -23.7157 | -28.0937
| 36 | ULTIMATE MIN | 0 | -31.5616 | -2.0531 | 0 | 54 | ULTIMATE MIN | 0.5 | -86.7218 | -24.722 | -21.4241
| 36 | ULTIMATE MIN | 0.5 | -30.9839 | 0 | 0 | 54 | ULTIMATE MIN | 1 | -88.6923 | -25.6746 | -15.5402
| 36 | ULTIMATE MIN | 1 | -30.4062 | 0 | 0 | 55 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0 | 0 | 33.3513 | 34.9228 | 55 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 0.5 | 0 | 50.418 | 23.4045 | 55 | ULTIMATE MAX | 1 | 0 | 0 | 0
| 37 | ULTIMATE MAX | 1 | 0 | 67.4847 | 7.2243 | 55 | ULTIMATE MIN | 0 | -75.7484 | -16.8929 | -15.5402
| 37 | ULTIMATE MIN | 0 | -31.1143 | 0 | 0 | 55 | ULTIMATE MIN | 0.5 | -77.7153 | -17.5933 | -10.9531
| 37 | ULTIMATE MIN | 0.5 | -30.5366 | 0 | 0 | 55 | ULTIMATE MIN | 1 | -79.6823 | -18.4257 | -6.6068
| 37 | ULTIMATE MIN | 1 | -29.9588 | 0 | 0 | 56 | ULTIMATE MAX | 0 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 0 | 0 | 67.4853 | 7.2243 | 56 | ULTIMATE MAX | 0.5 | 0 | 0 | 0
| 38 | ULTIMATE MAX | 1 | 0 | 74.9326 | 0 | 56 | ULTIMATE MAX | 1 | 0 | 0 | 2.101
| 38 | ULTIMATE MIN | 0 | -30.6779 | 0 | 0 | 56 | ULTIMATE MIN | 0 | -66.7917 | -12.259 | -6.6068
| 38 | ULTIMATE MIN | 1 | -30.4258 | 0 | -1.3535 | 56 | ULTIMATE MIN | 0.5 | -68.7587 | -11.7845 | -3.2949
| 39 | ULTIMATE MAX | 0 | 0 | 74.9326 | 0 | 56 | ULTIMATE MIN | 1 | -70.7256 | -12.4724 | -0.18553
| 39 | ULTIMATE MAX | 1 | 0 | 92.3096 | 0 | 57 | ULTIMATE MAX | 0 | 0 | 0 | 2.101
| 39 | ULTIMATE MIN | 0 | -30.4258 | 0 | -1.3535 | 57 | ULTIMATE MAX | 0.5 | 0 | 0 | 4.2511
| 39 | ULTIMATE MIN | 1 | -29.8376 | 0 | -24.7661 | 57 | ULTIMATE MAX | 1 | 0 | 0 | 6.5598
| 40 | ULTIMATE MAX | 0 | 0 | 92.3096 | 0 | 57 | ULTIMATE MIN | 0 | -57.8822 | -9.7161 | -0.18557
| 40 | ULTIMATE MAX | 1 | 0 | 101.6187 | 0 | 57 | ULTIMATE MIN | 0.5 | -59.9795 | -9.1069 | 0
| 40 | ULTIMATE MIN | 0 | -29.8376 | 0 | -24.7661 | 57 | ULTIMATE MIN | 1 | -62.1176 | -8.5814 | 0
| 40 | ULTIMATE MIN | 1 | -29.5224 | 0 | -39.3107 | 58 | ULTIMATE MAX | 0 | 0 | 0 | 6.5598
| 41 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 58 | ULTIMATE MAX | 1 | 0 | 0 | 7.4151
| 41 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 58 | ULTIMATE MIN | 0 | -49.2917 | -8.5814 | 0
| 41 | ULTIMATE MIN | 0 | -29.5224 | -101.6187 | -39.3107 | 58 | ULTIMATE MIN | 1 | -50.4621 | -8.3291 | 0
| 41 | ULTIMATE MIN | 1 | -29.8376 | -92.3096 | -24.7661 | 59 | ULTIMATE MAX | 0 | 0 | 0 | 7.4151
| 42 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 59 | ULTIMATE MAX | 1 | 0 | 0 | 8.7683
| 42 | ULTIMATE MAX | 1 | 0 | 0 | 0 | 59 | ULTIMATE MIN | 0 | -50.4621 | -8.3291 | 0
| 42 | ULTIMATE MIN | 0 | -29.8376 | -92.3096 | -24.7661 | 59 | ULTIMATE MIN | 1 | -52.2216 | -7.9999 | 0
| 42 | ULTIMATE MIN | 1 | -30.4258 | -74.9326 | -1.3535 | 60 | ULTIMATE MAX | 0 | 0 | 0 | 8.7683
| 43 | ULTIMATE MAX | 0 | 0 | 0 | 0 | 60 | ULTIMATE MAX | 1 | 0 | 0 | 9.8446
| 43 | ULTIMATE MAX | 1 | 0 | 0 | 7.2243 | 60 | ULTIMATE MIN | 0 | -52.2216 | -7.9999 | 0
| 43 | ULTIMATE MIN | 0 | -30.4258 | -74.9326 | -1.3535 | 60 | ULTIMATE MIN | 1 | -53.5604 | -7.7921 | 0
| 43 | ULTIMATE MIN | 1 | -30.6779 | -67.4853 | 0 | 61 | ULTIMATE MAX | 0 | 0 | 0.98638 | 0.72967
| 44 | ULTIMATE MAX | 0 | 0 | 0 | 7.2243 | 61 | ULTIMATE MAX | 0.25 | 0 | 0.039797 | 1.1584
| 44 | ULTIMATE MAX | 0.5 | 0 | 0 | 23.4045 | 61 | ULTIMATE MAX | 0.5 | 0 | 0.8945 | 0.79963
| 44 | ULTIMATE MAX | 1 | 0 | 0 | 34.9228 | 61 | ULTIMATE MAX | 0.75 | 0 | 1.8163 | 0.33639
| 44 | ULTIMATE MIN | 0 | -29.9588 | -67.4847 | 0 | 61 | ULTIMATE MAX | 1 | 0 | 2.7258 | 2.2393
| 44 | ULTIMATE MIN | 0.5 | -30.5366 | -50.418 | 0 | 61 | ULTIMATE MIN | 0 | -201.9684 | -0.98638 | -0.72967
| 44 | ULTIMATE MIN | 1 | -31.1143 | -33.3513 | 0 | 61 | ULTIMATE MIN | 0.25 | -208.124 | -0.039797 | -1.1584
| 45 | ULTIMATE MAX | 0 | 0 | 0 | 34.9228 | 61 | ULTIMATE MIN | 0.5 | -214.2797 | -0.8945 | -0.79963
| 45 | ULTIMATE MAX | 0.5 | 0 | 0 | 41.7475 | 61 | ULTIMATE MIN | 0.75 | -220.4353 | -1.8163 | -0.33639
| 45 | ULTIMATE MAX | 1 | 0 | 2.0531 | 43.879 | 61 | ULTIMATE MIN | 1 | -226.5909 | -2.7258 | -2.2393
| 45 | ULTIMATE MIN | 0 | -30.4062 | -33.3507 | 0
| 45 | ULTIMATE MIN | 0.5 | -30.9839 | -16.284 | 0
| 45 | ULTIMATE MIN | 1 | -31.5616 | 0 | 0
| 46 | ULTIMATE MAX | 0 | 0 | 2.0528 | 43.879
| 46 | ULTIMATE MAX | 0.5 | 0 | 19.1195 | 41.3169
| 46 | ULTIMATE MAX | 1 | 0 | 36.1862 | 34.0615
| 46 | ULTIMATE MIN | 0 | -30.8646 | 0 | 0
| 46 | ULTIMATE MIN | 0.5 | -31.4423 | 0 | 0
| 46 | ULTIMATE MIN | 1 | -32.0201 | 0 | 0
| 47 | ULTIMATE MAX | 0 | 0 | 36.1867 | 34.0615
| 47 | ULTIMATE MAX | 0.5 | 0 | 53.2534 | 22.1126
| 47 | ULTIMATE MAX | 1 | 0 | 70.3201 | 5.4703
| 47 | ULTIMATE MIN | 0 | -31.3343 | 0 | 0
| 47 | ULTIMATE MIN | 0.5 | -31.912 | 0 | 0
| 47 | ULTIMATE MIN | 1 | -32.4898 | 0 | 0
| 48 | ULTIMATE MAX | 0 | 0 | 70.3205 | 5.4705
| 48 | ULTIMATE MAX | 1 | 0 | 77.7678 | 0
| 48 | ULTIMATE MIN | 0 | -31.8154 | 0 | 0
| 48 | ULTIMATE MIN | 1 | -32.0675 | 0 | -6.1765
| 49 | ULTIMATE MAX | 0 | 0 | 77.7678 | 0
| 49 | ULTIMATE MAX | 1 | 0 | 95.1448 | 0
| 49 | ULTIMATE MIN | 0 | -32.0675 | 0 | -6.1765
| 49 | ULTIMATE MIN | 1 | -32.6557 | 0 | -30.3843
| 50 | ULTIMATE MAX | 0 | 0 | 95.1448 | 0
| 50 | ULTIMATE MAX | 1 | 0 | 104.454 | 0
| 50 | ULTIMATE MIN | 0 | -32.6557 | 0 | -30.3843
| 50 | ULTIMATE MIN | 1 | -32.9709 | 0 | -45.3542
| 51 | ULTIMATE MAX | 0 | 0 | 0 | 0

## 단면력정리(상시)
17. 단면력정리 (상시)
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 67.481 | 108.934 | 96.257 | 41.565 | 1000 | 416.667
|  | 제 1경간 중앙부 | 56.614 | - | 96.257 | 36.907 | 1000 | 350
|  | 제 1경간 지점부 | 105.707 | 135.516 | 96.257 | 70.134 | 1000 | 416.667
|  | 제 2경간 중앙부 | 56.614 | - | 96.257 | 36.907 | 1000 | 350
|  | 단지점부(우측) | 67.481 | 108.934 | 96.257 | 41.565 | 1000 | 416.667
| 하부슬래브 | 단지점부(좌측) | 70.653 | 134.241 | 126.649 | 46.238 | 1000 | 350
|  | 제 1경간 중앙부 | 60.359 | - | 126.649 | 40.901 | 1000 | 350
|  | 제 1경간 지점부 | 111.561 | 163.431 | 126.649 | 73.621 | 1000 | 350
|  | 제 2경간 중앙부 | 60.359 | - | 126.649 | 40.901 | 1000 | 350
|  | 단지점부(우측) | 70.653 | 134.241 | 126.649 | 46.238 | 1000 | 350
| 좌측벽체 | 상부 | 67.481 | 78.383 | 150.157 | 41.565 | 1000 | 366.667
|  | 중앙부 | 30.46 | - | 164.931 | 17.752 | 1000 | 300
|  | 중앙부(부모멘트) | -32.033 | - | 164.931 | -19.735 | 1000 | 300 | 부모멘트
|  | 하부 | 70.653 | 90.644 | 179.704 | 46.238 | 1000 | 300
| 우측벽체 | 상부 | 67.481 | 78.383 | 150.157 | 41.565 | 1000 | 366.667
|  | 중앙부 | 30.46 | - | 164.931 | 17.752 | 1000 | 300
|  | 중앙부(부모멘트) | -32.033 | - | 164.931 | -19.735 | 1000 | 300 | 부모멘트
|  | 하부 | 70.653 | 90.644 | 179.704 | 46.238 | 1000 | 300

## 단면력정리(붕괴방지)
18. 단면력정리 (붕괴방지)
1) 지진하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 지진하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 지진하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | mm | mm
| 상부슬래브 | 단지점부(좌측) | 45.354 | 77.768 | 32.971 | 1000 | 416.667
|  | 제 1경간 중앙부 | 43.879 | - | 30.865 | 1000 | 350
|  | 제 1경간 지점부 | 39.311 | 74.933 | 29.522 | 1000 | 416.667
|  | 제 2경간 중앙부 | 43.879 | - | 31.562 | 1000 | 350
|  | 단지점부(우측) | 45.354 | 77.768 | 32.971 | 1000 | 416.667
| 하부슬래브 | 단지점부(좌측) | 0 | 28.527 | 8.09 | 1000 | 350
|  | 제 1경간 중앙부 | 28.909 | - | 7.567 | 1000 | 350
|  | 제 1경간 지점부 | 87.253 | 98.003 | 7.326 | 1000 | 350
|  | 제 2경간 중앙부 | 28.909 | - | 7.958 | 1000 | 350
|  | 단지점부(우측) | 0 | 28.527 | 8.09 | 1000 | 350
| 좌측벽체 | 상부 | 45.354 | 31.423 | 93.821 | 1000 | 366.667
|  | 중앙부 | 7.415 | - | 50.462 | 1000 | 300
|  | 중앙부(부모멘트) | -32.946 | - | 50.462 | 1000 | 300 | 부모멘트
|  | 하부 | 0 | 8.329 | 53.56 | 1000 | 300
| 우측벽체 | 상부 | 45.354 | 31.423 | 93.821 | 1000 | 366.667
|  | 중앙부 | 7.415 | - | 50.462 | 1000 | 300
|  | 중앙부(부모멘트) | -32.946 | - | 50.462 | 1000 | 300 | 부모멘트
|  | 하부 | 0 | 8.329 | 53.56 | 1000 | 300

## 단면검토 및 철근량 산정
19. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 346.667 | 67.481 | 123.887 |  | 582.104 | H16 - 3.3EA + H13 - 3.3EA |  |  | 1084.333 | 1.836
상부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 300 | 56.614 | 83.778 |  | 565.489 | H13 - 6.7EA |  |  | 844.667 | 1.48
상부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 346.667 | 105.707 | 150.212 |  | 920.815 | H16 - 6.7EA |  |  | 1324 | 1.421
상부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 300 | 56.614 | 83.778 |  | 565.489 | H13 - 6.7EA |  |  | 844.667 | 1.48
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 346.667 | 67.481 | 123.887 |  | 582.106 | H16 - 3.3EA + H13 - 3.3EA |  |  | 1084.333 | 1.836
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 280 | 70.653 | 99.309 |  | 762.508 | H16 - 3.3EA + H13 - 3.3EA |  |  | 1084.333 | 1.406
하부슬래브 : 제 1경간 중앙부 |  |  |  | 1000 |  | 300 | 60.359 | 83.778 |  | 603.666 | H13 - 6.7EA |  |  | 844.667 | 1.388
하부슬래브 : 제 2경간 지점부 |  |  |  | 1000 |  | 280 | 111.561 | 145.223 |  | 1224.341 | H19 - 3.3EA + H16 - 3.3EA |  |  | 1617 | 1.302
하부슬래브 : 제 2경간 중앙부 |  |  |  | 1000 |  | 300 | 60.359 | 83.778 |  | 603.666 | H13 - 6.7EA |  |  | 844.667 | 1.388
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 280 | 70.653 | 99.309 |  | 762.508 | H16 - 3.3EA + H13 - 3.3EA |  |  | 1084.333 | 1.406
좌측벽체 : 상부 |  |  |  | 1000 |  | 296.667 | 67.481 | 141.908 |  | - | H16 - 3.3EA + H13 - 3.3EA |  |  | - | 2.103
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 250 | 30.46 | 130.2 |  | - | H16 - 3.3EA |  |  | - | 4.274
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 230 | 32.946 | 113.744 |  | - | H16 - 3.3EA |  |  | - | 3.452
좌측벽체 : 하부 |  |  |  | 1000 |  | 230 | 70.653 | 106.794 |  | - | H16 - 3.3EA + H13 - 3.3EA |  |  | - | 1.512
우측벽체 : 상부 |  |  |  | 1000 |  | 296.667 | 67.481 | 141.908 |  | - | H16 - 3.3EA + H13 - 3.3EA |  |  | - | 2.103
우측벽체 : 중앙부 |  |  |  | 1000 |  | 250 | 30.46 | 130.2 |  | - | H16 - 3.3EA |  |  | - | 4.274
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 230 | 32.946 | 113.744 |  | - | H16 - 3.3EA |  |  | - | 3.452
우측벽체 : 하부 |  |  |  | 1000 |  | 230 | 70.653 | 106.794 |  | - | H16 - 3.3EA + H13 - 3.3EA |  |  | - | 1.512
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s |  | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 171.464 |  | 108.934 | 171.464 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 1경간 중앙부 |  |  |  | 183.712 |  | - | 183.712 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 지점부 |  |  |  | 171.464 |  | 135.516 | 171.464 | - |  | - | - | - |  | - | O.K
상부슬래브 : 제 2경간 중앙부 |  |  |  | 183.712 |  | - | 183.712 | - |  | - | - | - |  | - | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 171.464 |  | 108.934 | 171.464 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 171.464 |  | 134.241 | 171.464 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 1경간 중앙부 |  |  |  | 183.712 |  | - | 183.712 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 지점부 |  |  |  | 171.464 |  | 163.431 | 171.464 | - |  | - | - | - |  | - | O.K
하부슬래브 : 제 2경간 중앙부 |  |  |  | 183.712 |  | - | 183.712 | - |  | - | - | - |  | - | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 171.464 |  | 134.241 | 171.464 | - |  | - | - | - |  | - | O.K
좌측벽체 : 상부 |  |  |  | 145.881 |  | 78.383 | 145.881 | - |  | - | - | - |  | - | O.K
좌측벽체 : 중앙부 |  |  |  | 159.105 |  | - | 159.105 | - |  | - | - | - |  | - | O.K
좌측벽체 : 하부 |  |  |  | 146.872 |  | 90.644 | 146.872 | - |  | - | - | - |  | - | O.K
우측벽체 : 상부 |  |  |  | 145.881 |  | 78.383 | 145.881 | - |  | - | - | - |  | - | O.K
우측벽체 : 중앙부 |  |  |  | 159.105 |  | - | 159.105 | - |  | - | - | - |  | - | O.K
우측벽체 : 하부 |  |  |  | 146.872 |  | 90.644 | 146.872 | - |  | - | - | - |  | - | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 416.667 |  | 346.667 |  | 70 |  | 67.481 |  | 108.934
＊ 강도감소계수(Φ) 산정
T = As x fy = 1084.333 x 400.00 = 433733.333
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 21.261 mm, c = 21.261 / β1 = 21.261 / 0.85 = 25.013 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (346.67 - 25.013) / 25.013 = 0.0386
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 582.104 mm²
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00313
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1084.333 x 400 x (346.67 - a/2) = 123.887 kN.m
; a = As x fy / (0.85 x fck x b) = 21.261 mm
≥ Mu (= 67.481 kN.m) ∴ O.K [안전률 1.836]
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 280.00 = 171.464 kN
≥ Vu (= 108.934 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 300 |  | 50 |  | 56.614 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 844.667 x 400.00 = 337866.667
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 16.562 mm, c = 16.562 / β1 = 16.562 / 0.85 = 19.485 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (300.00 - 19.485) / 19.485 = 0.0432
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 565.489 mm²
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00282
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 844.667 x 400 x (300.00 - a/2) = 83.778 kN.m
; a = As x fy / (0.85 x fck x b) = 16.562 mm
≥ Mu (= 56.614 kN.m) ∴ O.K [안전률 1.480]
＊ 전단에 대한 검토 (d = 300.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 300.00 = 183.712 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 416.667 |  | 346.667 |  | 70 |  | 105.707 |  | 135.516
＊ 강도감소계수(Φ) 산정
T = As x fy = 1324.000 x 400.00 = 529600.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 25.961 mm, c = 25.961 / β1 = 25.961 / 0.85 = 30.542 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (346.67 - 30.542) / 30.542 = 0.0311
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 920.815 mm²
Use As = 1324.000 mm² (철근도심 : 70.000 mm)
1단 : H16 - 6.7 EA (= 1324.000 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00382
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1324.000 x 400 x (346.67 - a/2) = 150.212 kN.m
; a = As x fy / (0.85 x fck x b) = 25.961 mm
≥ Mu (= 105.707 kN.m) ∴ O.K [안전률 1.421]
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 280.00 = 171.464 kN
≥ Vu (= 135.516 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 300 |  | 50 |  | 56.614 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 844.667 x 400.00 = 337866.667
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 16.562 mm, c = 16.562 / β1 = 16.562 / 0.85 = 19.485 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (300.00 - 19.485) / 19.485 = 0.0432
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 565.489 mm²
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00282
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 844.667 x 400 x (300.00 - a/2) = 83.778 kN.m
; a = As x fy / (0.85 x fck x b) = 16.562 mm
≥ Mu (= 56.614 kN.m) ∴ O.K [안전률 1.480]
＊ 전단에 대한 검토 (d = 300.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 300.00 = 183.712 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 416.667 |  | 346.667 |  | 70 |  | 67.481 |  | 108.934
＊ 강도감소계수(Φ) 산정
T = As x fy = 1084.333 x 400.00 = 433733.333
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 21.261 mm, c = 21.261 / β1 = 21.261 / 0.85 = 25.013 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (346.67 - 25.013) / 25.013 = 0.0386
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 582.106 mm²
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00313
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1084.333 x 400 x (346.67 - a/2) = 123.887 kN.m
; a = As x fy / (0.85 x fck x b) = 21.261 mm
≥ Mu (= 67.481 kN.m) ∴ O.K [안전률 1.836]
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 280.00 = 171.464 kN
≥ Vu (= 108.934 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 280 |  | 70 |  | 70.653 |  | 134.241
＊ 강도감소계수(Φ) 산정
T = As x fy = 1084.333 x 400.00 = 433733.333
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 21.261 mm, c = 21.261 / β1 = 21.261 / 0.85 = 25.013 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (280.00 - 25.013) / 25.013 = 0.0306
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 762.508 mm²
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00387
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1084.333 x 400 x (280.00 - a/2) = 99.309 kN.m
; a = As x fy / (0.85 x fck x b) = 21.261 mm
≥ Mu (= 70.653 kN.m) ∴ O.K [안전률 1.406]
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 280.00 = 171.464 kN
≥ Vu (= 134.241 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 300 |  | 50 |  | 60.359 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 844.667 x 400.00 = 337866.667
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 16.562 mm, c = 16.562 / β1 = 16.562 / 0.85 = 19.485 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (300.00 - 19.485) / 19.485 = 0.0432
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 603.666 mm²
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00282
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 844.667 x 400 x (300.00 - a/2) = 83.778 kN.m
; a = As x fy / (0.85 x fck x b) = 16.562 mm
≥ Mu (= 60.359 kN.m) ∴ O.K [안전률 1.388]
＊ 전단에 대한 검토 (d = 300.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 300.00 = 183.712 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 지점부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 280 |  | 70 |  | 111.561 |  | 163.431
＊ 강도감소계수(Φ) 산정
T = As x fy = 1617.000 x 400.00 = 646800.000
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 31.706 mm, c = 31.706 / β1 = 31.706 / 0.85 = 37.301 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (280.00 - 37.301) / 37.301 = 0.0195
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 1224.341 mm²
Use As = 1617.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 3.3 EA + H16 - 3.3 EA (= 1617.000 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00578
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1617.000 x 400 x (280.00 - a/2) = 145.223 kN.m
; a = As x fy / (0.85 x fck x b) = 31.706 mm
≥ Mu (= 111.561 kN.m) ∴ O.K [안전률 1.302]
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 280.00 = 171.464 kN
≥ Vu (= 163.431 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 300 |  | 50 |  | 60.359 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 844.667 x 400.00 = 337866.667
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 16.562 mm, c = 16.562 / β1 = 16.562 / 0.85 = 19.485 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (300.00 - 19.485) / 19.485 = 0.0432
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 603.666 mm²
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00282
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 844.667 x 400 x (300.00 - a/2) = 83.778 kN.m
; a = As x fy / (0.85 x fck x b) = 16.562 mm
≥ Mu (= 60.359 kN.m) ∴ O.K [안전률 1.388]
＊ 전단에 대한 검토 (d = 300.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 300.00 = 183.712 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 350 |  | 280 |  | 70 |  | 70.653 |  | 134.241
＊ 강도감소계수(Φ) 산정
T = As x fy = 1084.333 x 400.00 = 433733.333
C = 0.85 x fck x a x b = 0.85 x 24.00 x a x 1000.000 = 20400.000 x a
T = C 이므로, a = 21.261 mm, c = 21.261 / β1 = 21.261 / 0.85 = 25.013 mm
εy = fy / Es = 400.00 / 200000.00 = 0.0020
εt = 0.0030 x (dt - c) / c = 0.0030 x (280.00 - 25.013) / 25.013 = 0.0306
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 762.508 mm²
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00350
0.25 √fck / fy = 0.00306 , ρmin = 0.00350 적용
수축온도철근비 = 0.00200
ρmax = 0.71 x ρb = 0.71 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.01857
ρuse = As / bd = 0.00387
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1084.333 x 400 x (280.00 - a/2) = 99.309 kN.m
; a = As x fy / (0.85 x fck x b) = 21.261 mm
≥ Mu (= 70.653 kN.m) ∴ O.K [안전률 1.406]
＊ 전단에 대한 검토 (d = 280.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √24 x 1000.00 x 280.00 = 171.464 kN
≥ Vu (= 134.241 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 366.667 |  | 296.667 |  | 150.157 |  | 67.481 |  | 78.383 |  | 449.404
＊ 철근비 검토
As = 1084.333 mm² (인장중심 = 70.00 mm) , 1단 : H16- 3.3EA + H13- 3.3EA , d1 = 70.00 mm
Asf = 662.000 mm² (압축중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0048) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 366.7 x 1000.0 = 7480000.0 N
Cs = As x fy = 433733.3 N, Cs' = Asf x fy = 264800.0 N
Xp = (7480000.0 x 183.33 + 433733.3 x 70.000 + 264800.0 x 316.667) / 8178533.3
= 181.640 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 178.000 mm, ab = k1 x cb = 151.300 mm
fs' = 600 x (178.000 - 50.000) / 178.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 151.300 x 1000.000 = 3086.520 kN
Cs = As' x (fs' - 0.85 x fck) = 251.295 kN
Ts = As x fs = 433.733 kN
Pb = 3086.520 + 251.295 - 433.733 = 2904.082 kN
Mb = 3086.520 x (296.667 - 151.300/2) + 251.295 x (296.667 - 50.00)
- 2904.082 x (181.640 - 70.000)
= 419.947 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 144.606 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 47.694 mm, a = k1 x c = 40.540 mm 를 사용.
fs = 600 x (296.667 - 47.694) / 47.694 (≤fy) = 400.000 MPa
fs' = 600 x ( 47.694 - 50.000) / 47.694 (≤fy) = 5.557 MPa
Cc = 0.85 x 24.0 x 40.540 x 1000.000 = 827.016 kN
Cs = As' x (fs' - 0.85 x fck) = -9.826 kN
Ts = As x fs = 433.733 kN
Pn = 827.016 + -9.826 - 433.733 = 403.108 kN
Mn' = 827.016 x (296.667 - 40.540/2) + -9.826 x (296.667 - 50.00)
= 226.161 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0024 ＜ 0.0100 (e' = e + Xp - dc = 561.044 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6514.327 kN ≥ Pn = 403.108 kN
ΦPn = 0.78 x 403.108 = 315.768 kN ≥ Pu = 150.157 kN ∴ O.K
ΦMn = ΦPn x 0.449 = 141.908 kN.m ≥ Mu = 67.481 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.881 kN
≥ Vu (= 78.383 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 250 |  | 164.931 |  | 30.46 |  | 0 |  | 184.683
＊ 철근비 검토
As = 662.000 mm² (인장중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Asf = 662.000 mm² (압축중심 = 70.00 mm) , 1단 : H16- 3.3EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0044) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 264800.0 N, Cs' = Asf x fy = 264800.0 N
Xp = (6120000.0 x 150.00 + 264800.0 x 50.000 + 264800.0 x 230.000) / 6649600.0
= 149.204 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 150.000 mm, ab = k1 x cb = 127.500 mm
fs' = 600 x (150.000 - 70.000) / 150.000 (≤fy) = 320.000 MPa
Cc = 0.85 x 24.0 x 127.500 x 1000.000 = 2601.000 kN
Cs = As' x (fs' - 0.85 x fck) = 198.335 kN
Ts = As x fs = 264.800 kN
Pb = 2601.000 + 198.335 - 264.800 = 2534.535 kN
Mb = 2601.000 x (250.000 - 127.500/2) + 198.335 x (250.000 - 70.00)
- 2534.535 x (149.204 - 50.000)
= 268.702 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 106.016 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 66.795 mm, a = k1 x c = 56.776 mm 를 사용.
fs = 600 x (250.000 - 66.795) / 66.795 (≤fy) = 400.000 MPa
fs' = 600 x ( 66.795 - 70.000) / 66.795 (≤fy) = 10.495 MPa
Cc = 0.85 x 24.0 x 56.776 x 1000.000 = 1158.231 kN
Cs = As' x (fs' - 0.85 x fck) = -6.557 kN
Ts = As x fs = 264.800 kN
Pn = 1158.231 + -6.557 - 264.800 = 899.988 kN
Mn' = 1158.231 x (250.000 - 56.776/2) + -6.557 x (250.000 - 70.00)
= 255.498 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0031 ＜ 0.0100 (e' = e + Xp - dc = 283.887 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 50.00 = 250.000 mm
c = 600.00 / (600.00+400.00) x 250.000 = 150.000 mm, a = k1 x c = 127.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (250.00-150.00) / 150.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5298.072 kN ≥ Pn = 899.988 kN
ΦPn = 0.78 x 899.988 = 704.991 kN ≥ Pu = 164.931 kN ∴ O.K
ΦMn = ΦPn x 0.185 = 130.200 kN.m ≥ Mu = 30.460 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 250.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 250.00 = 159.105 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 164.931 |  | 32.946 |  | 0 |  | 199.754
＊ 철근비 검토
As = 662.000 mm² (인장중심 = 70.00 mm) , 1단 : H16- 3.3EA , d1 = 70.00 mm
Asf = 662.000 mm² (압축중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0044) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 264800.0 N, Cs' = Asf x fy = 264800.0 N
Xp = (6120000.0 x 150.00 + 264800.0 x 70.000 + 264800.0 x 250.000) / 6649600.0
= 150.796 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 50.000) / 138.000 (≤fy) = 382.609 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 239.782 kN
Ts = As x fs = 264.800 kN
Pb = 2392.920 + 239.782 - 264.800 = 2367.902 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 239.782 x (230.000 - 50.00)
- 2367.902 x (150.796 - 70.000)
= 261.870 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 110.591 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 55.647 mm, a = k1 x c = 47.300 mm 를 사용.
fs = 600 x (230.000 - 55.647) / 55.647 (≤fy) = 400.000 MPa
fs' = 600 x ( 55.647 - 50.000) / 55.647 (≤fy) = 60.887 MPa
Cc = 0.85 x 24.0 x 47.300 x 1000.000 = 964.919 kN
Cs = As' x (fs' - 0.85 x fck) = 26.802 kN
Ts = As x fs = 264.800 kN
Pn = 964.919 + 26.802 - 264.800 = 726.921 kN
Mn' = 964.919 x (230.000 - 47.300/2) + 26.802 x (230.000 - 50.00)
= 203.935 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0038 ＜ 0.0100 (e' = e + Xp - dc = 280.551 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5298.072 kN ≥ Pn = 726.921 kN
ΦPn = 0.78 x 726.921 = 569.421 kN ≥ Pu = 164.931 kN ∴ O.K
ΦMn = ΦPn x 0.200 = 113.744 kN.m ≥ Mu = 32.946 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 146.377 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 179.704 |  | 70.653 |  | 90.644 |  | 393.161
＊ 철근비 검토
As = 1084.333 mm² (인장중심 = 70.00 mm) , 1단 : H16- 3.3EA + H13- 3.3EA , d1 = 70.00 mm
Asf = 662.000 mm² (압축중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0058) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 433733.3 N, Cs' = Asf x fy = 264800.0 N
Xp = (6120000.0 x 150.00 + 433733.3 x 70.000 + 264800.0 x 250.000) / 6818533.3
= 148.795 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 50.000) / 138.000 (≤fy) = 382.609 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 239.782 kN
Ts = As x fs = 433.733 kN
Pb = 2392.920 + 239.782 - 433.733 = 2198.969 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 239.782 x (230.000 - 50.00)
- 2198.969 x (148.795 - 70.000)
= 279.921 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 127.296 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 44.867 mm, a = k1 x c = 38.137 mm 를 사용.
fs = 600 x (230.000 - 44.867) / 44.867 (≤fy) = 400.000 MPa
fs' = 600 x ( 44.867 - 50.000) / 44.867 (≤fy) = 16.634 MPa
Cc = 0.85 x 24.0 x 38.137 x 1000.000 = 778.002 kN
Cs = As' x (fs' - 0.85 x fck) = -2.493 kN
Ts = As x fs = 433.733 kN
Pn = 778.002 + -2.493 - 433.733 = 346.762 kN
Mn' = 778.002 x (230.000 - 38.137/2) + -2.493 x (230.000 - 50.00)
= 163.656 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0001 ＜ 0.0100 (e' = e + Xp - dc = 471.956 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5426.327 kN ≥ Pn = 346.762 kN
ΦPn = 0.78 x 346.762 = 271.630 kN ≥ Pu = 179.704 kN ∴ O.K
ΦMn = ΦPn x 0.393 = 106.794 kN.m ≥ Mu = 70.653 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 146.872 kN
≥ Vu (= 90.644 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 366.667 |  | 296.667 |  | 150.157 |  | 67.481 |  | 78.383 |  | 449.406
＊ 철근비 검토
As = 1084.333 mm² (인장중심 = 70.00 mm) , 1단 : H16- 3.3EA + H13- 3.3EA , d1 = 70.00 mm
Asf = 662.000 mm² (압축중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0048) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 366.7 x 1000.0 = 7480000.0 N
Cs = As x fy = 433733.3 N, Cs' = Asf x fy = 264800.0 N
Xp = (7480000.0 x 183.33 + 433733.3 x 70.000 + 264800.0 x 316.667) / 8178533.3
= 181.640 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 178.000 mm, ab = k1 x cb = 151.300 mm
fs' = 600 x (178.000 - 50.000) / 178.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 151.300 x 1000.000 = 3086.520 kN
Cs = As' x (fs' - 0.85 x fck) = 251.295 kN
Ts = As x fs = 433.733 kN
Pb = 3086.520 + 251.295 - 433.733 = 2904.082 kN
Mb = 3086.520 x (296.667 - 151.300/2) + 251.295 x (296.667 - 50.00)
- 2904.082 x (181.640 - 70.000)
= 419.947 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 144.606 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 47.694 mm, a = k1 x c = 40.540 mm 를 사용.
fs = 600 x (296.667 - 47.694) / 47.694 (≤fy) = 400.000 MPa
fs' = 600 x ( 47.694 - 50.000) / 47.694 (≤fy) = 5.557 MPa
Cc = 0.85 x 24.0 x 40.540 x 1000.000 = 827.016 kN
Cs = As' x (fs' - 0.85 x fck) = -9.826 kN
Ts = As x fs = 433.733 kN
Pn = 827.016 + -9.826 - 433.733 = 403.108 kN
Mn' = 827.016 x (296.667 - 40.540/2) + -9.826 x (296.667 - 50.00)
= 226.161 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0037 ＜ 0.0100 (e' = e + Xp - dc = 561.046 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 6514.327 kN ≥ Pn = 403.108 kN
ΦPn = 0.78 x 403.108 = 315.768 kN ≥ Pu = 150.157 kN ∴ O.K
ΦMn = ΦPn x 0.449 = 141.908 kN.m ≥ Mu = 67.481 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 145.881 kN
≥ Vu (= 78.383 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 250 |  | 164.931 |  | 30.46 |  | 0 |  | 184.683
＊ 철근비 검토
As = 662.000 mm² (인장중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Asf = 662.000 mm² (압축중심 = 70.00 mm) , 1단 : H16- 3.3EA , d1 = 70.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0044) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 264800.0 N, Cs' = Asf x fy = 264800.0 N
Xp = (6120000.0 x 150.00 + 264800.0 x 50.000 + 264800.0 x 230.000) / 6649600.0
= 149.204 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 150.000 mm, ab = k1 x cb = 127.500 mm
fs' = 600 x (150.000 - 70.000) / 150.000 (≤fy) = 320.000 MPa
Cc = 0.85 x 24.0 x 127.500 x 1000.000 = 2601.000 kN
Cs = As' x (fs' - 0.85 x fck) = 198.335 kN
Ts = As x fs = 264.800 kN
Pb = 2601.000 + 198.335 - 264.800 = 2534.535 kN
Mb = 2601.000 x (250.000 - 127.500/2) + 198.335 x (250.000 - 70.00)
- 2534.535 x (149.204 - 50.000)
= 268.702 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 106.016 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 66.795 mm, a = k1 x c = 56.776 mm 를 사용.
fs = 600 x (250.000 - 66.795) / 66.795 (≤fy) = 400.000 MPa
fs' = 600 x ( 66.795 - 70.000) / 66.795 (≤fy) = 10.495 MPa
Cc = 0.85 x 24.0 x 56.776 x 1000.000 = 1158.231 kN
Cs = As' x (fs' - 0.85 x fck) = -6.557 kN
Ts = As x fs = 264.800 kN
Pn = 1158.231 + -6.557 - 264.800 = 899.988 kN
Mn' = 1158.231 x (250.000 - 56.776/2) + -6.557 x (250.000 - 70.00)
= 255.498 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0033 ＜ 0.0100 (e' = e + Xp - dc = 283.887 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 50.00 = 250.000 mm
c = 600.00 / (600.00+400.00) x 250.000 = 150.000 mm, a = k1 x c = 127.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (250.00-150.00) / 150.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5298.072 kN ≥ Pn = 899.988 kN
ΦPn = 0.78 x 899.988 = 704.991 kN ≥ Pu = 164.931 kN ∴ O.K
ΦMn = ΦPn x 0.185 = 130.200 kN.m ≥ Mu = 30.460 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 250.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 250.00 = 159.105 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 164.931 |  | 32.946 |  | 0 |  | 199.754
＊ 철근비 검토
As = 662.000 mm² (인장중심 = 70.00 mm) , 1단 : H16- 3.3EA , d1 = 70.00 mm
Asf = 662.000 mm² (압축중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0044) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 264800.0 N, Cs' = Asf x fy = 264800.0 N
Xp = (6120000.0 x 150.00 + 264800.0 x 70.000 + 264800.0 x 250.000) / 6649600.0
= 150.796 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 50.000) / 138.000 (≤fy) = 382.609 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 239.782 kN
Ts = As x fs = 264.800 kN
Pb = 2392.920 + 239.782 - 264.800 = 2367.902 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 239.782 x (230.000 - 50.00)
- 2367.902 x (150.796 - 70.000)
= 261.870 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 110.591 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 55.647 mm, a = k1 x c = 47.300 mm 를 사용.
fs = 600 x (230.000 - 55.647) / 55.647 (≤fy) = 400.000 MPa
fs' = 600 x ( 55.647 - 50.000) / 55.647 (≤fy) = 60.887 MPa
Cc = 0.85 x 24.0 x 47.300 x 1000.000 = 964.919 kN
Cs = As' x (fs' - 0.85 x fck) = 26.802 kN
Ts = As x fs = 264.800 kN
Pn = 964.919 + 26.802 - 264.800 = 726.921 kN
Mn' = 964.919 x (230.000 - 47.300/2) + 26.802 x (230.000 - 50.00)
= 203.935 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0038 ＜ 0.0100 (e' = e + Xp - dc = 280.551 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5298.072 kN ≥ Pn = 726.921 kN
ΦPn = 0.78 x 726.921 = 569.421 kN ≥ Pu = 164.931 kN ∴ O.K
ΦMn = ΦPn x 0.200 = 113.744 kN.m ≥ Mu = 32.946 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 146.377 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  | B(mm) | H(mm) |  | d(mm) |  | Pu(kN) |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  | 1000 | 300 |  | 230 |  | 179.704 |  | 70.653 |  | 90.644 |  | 393.161
＊ 철근비 검토
As = 1084.333 mm² (인장중심 = 70.00 mm) , 1단 : H16- 3.3EA + H13- 3.3EA , d1 = 70.00 mm
Asf = 662.000 mm² (압축중심 = 50.00 mm) , 1단 : H16- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0058) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 433733.3 N, Cs' = Asf x fy = 264800.0 N
Xp = (6120000.0 x 150.00 + 433733.3 x 70.000 + 264800.0 x 250.000) / 6818533.3
= 148.795 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 138.000 mm, ab = k1 x cb = 117.300 mm
fs' = 600 x (138.000 - 50.000) / 138.000 (≤fy) = 382.609 MPa
Cc = 0.85 x 24.0 x 117.300 x 1000.000 = 2392.920 kN
Cs = As' x (fs' - 0.85 x fck) = 239.782 kN
Ts = As x fs = 433.733 kN
Pb = 2392.920 + 239.782 - 433.733 = 2198.969 kN
Mb = 2392.920 x (230.000 - 117.300/2) + 239.782 x (230.000 - 50.00)
- 2198.969 x (148.795 - 70.000)
= 279.921 kN.m
eb ＜ e → 인장 파괴 (eb = Mb/Pb = 127.296 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 44.867 mm, a = k1 x c = 38.137 mm 를 사용.
fs = 600 x (230.000 - 44.867) / 44.867 (≤fy) = 400.000 MPa
fs' = 600 x ( 44.867 - 50.000) / 44.867 (≤fy) = 16.634 MPa
Cc = 0.85 x 24.0 x 38.137 x 1000.000 = 778.002 kN
Cs = As' x (fs' - 0.85 x fck) = -2.493 kN
Ts = As x fs = 433.733 kN
Pn = 778.002 + -2.493 - 433.733 = 346.762 kN
Mn' = 778.002 x (230.000 - 38.137/2) + -2.493 x (230.000 - 50.00)
= 163.656 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0001 ＜ 0.0100 (e' = e + Xp - dc = 471.956 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 70.00 = 230.000 mm
c = 600.00 / (600.00+400.00) x 230.000 = 138.000 mm, a = k1 x c = 117.300 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (230.00-138.00) / 138.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5426.327 kN ≥ Pn = 346.762 kN
ΦPn = 0.78 x 346.762 = 271.630 kN ≥ Pu = 179.704 kN ∴ O.K
ΦMn = ΦPn x 0.393 = 106.794 kN.m ≥ Mu = 70.653 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 230.00 = 146.872 kN
≥ Vu (= 90.644 kN) , 전단보강 불필요.

## 수평철근검토
20. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
2) 상부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 844.667 |  | × | 0.2 |  | = | 168.933 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 168.933 ----------> O.K !!!
3) 상부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1324 |  | × | 0.2 |  | = | 264.8 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 264.800 ----------> O.K !!!
4) 상부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 844.667 |  | × | 0.2 |  | = | 168.933 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 168.933 ----------> O.K !!!
5) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
6) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
7) 하부슬래브 : 제 1경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 844.667 |  | × | 0.2 |  | = | 168.933 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 168.933 ----------> O.K !!!
8) 하부슬래브 : 제 2경간 지점부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1617 |  | × | 0.2 |  | = | 323.4 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 323.400 ----------> O.K !!!
9) 하부슬래브 : 제 2경간 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 844.667 |  | × | 0.2 |  | = | 168.933 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 168.933 ----------> O.K !!!
10) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 350 |  | × | 0.002 |  | = | 700 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 700.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
11) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
12) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 662 |  | × | 0.2 |  | = | 132.4 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 132.400 ----------> O.K !!!
13) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 662 |  | × | 0.2 |  | = | 132.4 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 132.400 ----------> O.K !!!
14) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
15) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!
16) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 662 |  | × | 0.2 |  | = | 132.4 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 132.400 ----------> O.K !!!
17) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 662 |  | × | 0.2 |  | = | 132.4 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 132.400 ----------> O.K !!!
18) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | H13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 사용 주철근량 |  |  | × | 20%
|  |  | = | 1084.333 |  | × | 0.2 |  | = | 216.867 |  | mm²
|  | ∴ Used As | = | H13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 216.867 ----------> O.K !!!

## 거더,기둥검토,내측벽체
21. 거더,기둥,내측벽체 검토
(1) 내측벽체 검토
(단위 : kN,m)
|  | 기둥부재 |  | 폭 | 두께 | 높이 |  | 길이 | 축력 |  | 모멘트 |  | 축력×길이 | 모멘트×길이 | Load Case
|  | P1 |  | 1 | 0.3 | 2.8 |  | 1 | 383.02 |  | 0 |  | 383.02 | 0 | 3
[9 empty] | 226.59 |  | 2.24 |  | 226.59 | 2.24 | 1
* 벽체와 기둥의 판별 (P1)
0.4Agfck = 0.4 × 1000 × 300 × 24
|  |  | = 2880000 N = 2880.00 kN | [6 empty] | ≥ 383.02 kN
∴ 벽체로 검토한다
1)벽체 1
① 축력 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 300 |  | 250 |  | 383.025 |  |  | 0 |  | 0 |  | 0
＊ 철근비 검토
As = 422.333 mm² (인장중심 = 50.00 mm) , 1단 : H13- 3.3EA , d1 = 50.00 mm
Asf = 422.333 mm² (압축중심 = 50.00 mm) , 1단 : H13- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0028) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 168933.3 N, Cs' = Asf x fy = 168933.3 N
Xp = (6120000.0 x 150.00 + 168933.3 x 50.000 + 168933.3 x 250.000) / 6457866.7
= 150.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 150.000 mm, ab = k1 x cb = 127.500 mm
fs' = 600 x (150.000 - 50.000) / 150.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 127.500 x 1000.000 = 2601.000 kN
Cs = As' x (fs' - 0.85 x fck) = 160.318 kN
Ts = As x fs = 168.933 kN
Pb = 2601.000 + 160.318 - 168.933 = 2592.384 kN
Mb = 2601.000 x (250.000 - 127.500/2) + 160.318 x (250.000 - 50.00)
- 2592.384 x (150.000 - 50.000)
= 257.261 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 99.237 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 356.191 mm, a = k1 x c = 302.762 mm 를 사용.
fs = 600 x (250.000 - 356.191) / 356.191 (≤fy) = 178.878 MPa
fs' = 600 x (356.191 - 50.000) / 356.191 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 302.762 x 1000.000 = 6176.352 kN
Cs = As' x (fs' - 0.85 x fck) = 160.318 kN
Ts = As x fs = 75.546 kN
Pn = 6176.352 + 160.318 - 75.546 = 6412.216 kN
Mn' = 6176.352 x (250.000 - 302.762/2) + 160.318 x (250.000 - 50.00)
= 641.168 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0086 ＜ 0.0100 (e' = e + Xp - dc = 100.000 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 50.00 = 250.000 mm
c = 600.00 / (600.00+400.00) x 250.000 = 150.000 mm, a = k1 x c = 127.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (250.00-150.00) / 150.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5152.508 kN ＜ Pn = 6412.216 kN
ΦPn = 0.78 x 5152.508 = 4036.132 kN ≥ Pu = 383.025 kN ∴ O.K
ΦMn = ΦPn x 0.000 = 0.001 kN.m ≥ Mu = 0.000 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 250.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 250.00 = 167.055 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
② 모멘트 최대
＊ 단면제원 및 설계가정
fck=24MPa, fy=400MPa, k1=0.85, Φc=0.65, Φf=0.85, Φv=0.75
|  |  | B(mm) |  | H(mm) |  | d(mm) |  | Pu(kN) |  |  | Mu(kN.m) |  | Vu(kN) |  | e(mm)
|  |  | 1000 |  | 300 |  | 250 |  | 226.591 |  |  | 2.239 |  | 0 |  | 9.882
＊ 철근비 검토
As = 422.333 mm² (인장중심 = 50.00 mm) , 1단 : H13- 3.3EA , d1 = 50.00 mm
Asf = 422.333 mm² (압축중심 = 50.00 mm) , 1단 : H13- 3.3EA , d1 = 50.00 mm
Pmin (= 0.0012) ≤ Puse (= 0.0028) ≤ Pmax (= 0.0800) ∴ O.K
＊ 평형하중 산정
- 소성중심 계산
Cc = 0.85 x 24.0 x 300.0 x 1000.0 = 6120000.0 N
Cs = As x fy = 168933.3 N, Cs' = Asf x fy = 168933.3 N
Xp = (6120000.0 x 150.00 + 168933.3 x 50.000 + 168933.3 x 250.000) / 6457866.7
= 150.000 mm
- 평형상태 계산
cb = 600 / (600 + fy) x d = 150.000 mm, ab = k1 x cb = 127.500 mm
fs' = 600 x (150.000 - 50.000) / 150.000 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 127.500 x 1000.000 = 2601.000 kN
Cs = As' x (fs' - 0.85 x fck) = 160.318 kN
Ts = As x fs = 168.933 kN
Pb = 2601.000 + 160.318 - 168.933 = 2592.384 kN
Mb = 2601.000 x (250.000 - 127.500/2) + 160.318 x (250.000 - 50.00)
- 2592.384 x (150.000 - 50.000)
= 257.261 kN.m
eb ＞ e → 압축 파괴 (eb = Mb/Pb = 99.237 mm)
＊ 공칭강도 산정
- 반복계산을 통해, c = 332.751 mm, a = k1 x c = 282.838 mm 를 사용.
fs = 600 x (250.000 - 332.751) / 332.751 (≤fy) = 149.213 MPa
fs' = 600 x (332.751 - 50.000) / 332.751 (≤fy) = 400.000 MPa
Cc = 0.85 x 24.0 x 282.838 x 1000.000 = 5769.905 kN
Cs = As' x (fs' - 0.85 x fck) = 160.318 kN
Ts = As x fs = 63.017 kN
Pn = 5769.905 + 160.318 - 63.017 = 5993.240 kN
Mn' = 5769.905 x (250.000 - 282.838/2) + 160.318 x (250.000 - 50.00)
= 658.564 kN.m
- 편심오차 = │e' - Mn'/Pn│ = 0.0021 ＜ 0.0100 (e' = e + Xp - dc = 109.882 mm)
＊ 강도감소계수(Φ) 산정
dt = 300.00 - 50.00 = 250.000 mm
c = 600.00 / (600.00+400.00) x 250.000 = 150.000 mm, a = k1 x c = 127.500 mm
εy = fy / Es = 400.00 / 600.00 = 0.0020
εt = 0.0030 x (dt-c) / c = 0.0030 x (250.00-150.00) / 150.00 = 0.0020
→ 계수축력이 0.10*fck*Ag보다 작고, fy가 400 MPa 이하이므로 εt = 0.0040를 적용한다.
εy ＜εt ＜ 0.0050 이므로 변화구간단면이며, Φ = 0.78 를 적용한다.
Φ = Φc + (εt-εy) x (Φf-Φc) / (0.6500-εy) = 0.0040
＊ 축방향력 및 휨에대한 검토
(max)Pn = 0.80 x {0.85 fck*(Ag-Ast) + fy*Ast} = 5152.508 kN ＜ Pn = 5993.240 kN
ΦPn = 0.78 x 5152.508 = 4036.132 kN ≥ Pu = 226.591 kN ∴ O.K
ΦMn = ΦPn x 0.010 = 39.887 kN.m ≥ Mu = 2.239 kN.m ∴ O.K
＊ 전단에 대한 검토 (d = 250.00 mm)
ΦVc = 0.75 x 1/6 x (1 + 1/14 Pu/Ag) x √24.0 x 1000.00 x 250.00 = 161.353 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.

## 절점부 검토
22. 절점부 검토
1) 절점 38
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 41.565 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 41.565 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 601.041 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @300 - 3.3EA |  |  |  |  | = | 422.333 | mm²
∴ Total Asb = 422.333 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 41.57 × 10^6 |  |  | = | 0.575 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 601.041²× 1000
∴ 절점부 보강철근 필요없음 !!!
2) 절점 1
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 46.238 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 46.238 kN.m
R = √(T1² + T2²) = 460.977 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @300 - 3.3EA |  |  |  |  | = | 422.333 | mm²
∴ Total Asb = 422.333 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 46.24 × 10^6 |  |  | = | 1.088 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 460.977²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 46.24 × 10^6 |  |  | = | 1114.491 mm²
|  |  |  | R × fsa |  |  | 460.977 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1114.491 mm² - 422.333 mm²
[5 empty] | = | 692.158 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @300 - 3.3EA
∴ Total As = 955.000 mm² > Req'd As (= 692.158 mm²) -------------> O.K !!!
3) 절점 26
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 41.565 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 41.565 kN.m
[12 empty] | R = | (T1×B + T2×A + A×B) |  |  |  | √2
(A + B)
[12 empty] | = | 601.041 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @300 - 3.3EA |  |  |  |  | = | 422.333 | mm²
∴ Total Asb = 422.333 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 41.57 × 10^6 |  |  | = | 0.575 MPa < 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 601.041²× 1000
∴ 절점부 보강철근 필요없음 !!!
4) 절점 21
[11 empty] | - CON'C 설계기준강도 |  |  |  |  | : fck = 24 MPa
[11 empty] | - 철근 항복강도 |  |  |  |  | : fy = 400 MPa
[11 empty] | - 사용 모멘트 |  |  |  |  | : Mu = 46.238 kN.m
[11 empty] | - 절점부 휨모멘트 |  |  |  |  | : Mo = 46.238 kN.m
R = √(T1² + T2²) = 460.977 mm
▣ 절점부 보강철근으로 볼 수 있는 주 철근량
|  |  | H13 @300 - 3.3EA |  |  |  |  | = | 422.333 | mm²
∴ Total Asb = 422.333 mm²
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = |  | 5 × Mo |  | = | 5 × 46.24 × 10^6 |  |  | = | 1.088 MPa > 0.13√fck (=0.637)
|  |  |  | R²×W |  |  | 460.977²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = |  | 2 × Mo |  | = | 2 × 46.24 × 10^6 |  |  | = | 1114.491 mm²
|  |  |  | R × fsa |  |  | 460.977 × 180
|  | Req'd As |  |  | = | As - Asb
[5 empty] | = | 1114.491 mm² - 422.333 mm²
[5 empty] | = | 692.158 mm²
☞ 사용보강철근
|  | Use'd As = |  |  | H19 @300 - 3.3EA
∴ Total As = 955.000 mm² > Req'd As (= 692.158 mm²) -------------> O.K !!!

## 사용성 검토
23. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 150 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 철근간격 (mm) | 최대간격 (mm) | 검토 결과 |  | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 346.667 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 512.441 | O.K |  | 3.416
2 | 상부슬래브 : 제 1경간 중앙부 |  | 300 |  | H13 - 6.7EA |  |  | 150 | 399.539 | O.K |  | 2.664
3 | 상부슬래브 : 제 2경간 지점부 |  | 346.667 |  | H16 - 6.7EA |  |  | 150 | 324.98 | O.K |  | 2.167
4 | 상부슬래브 : 제 2경간 중앙부 |  | 300 |  | H13 - 6.7EA |  |  | 150 | 399.539 | O.K |  | 2.664
5 | 상부슬래브 : 단지점부(우측) |  | 346.667 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 512.439 | O.K |  | 3.416
6 | 하부슬래브 : 단지점부(좌측) |  | 280 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 326.365 | O.K |  | 2.176
7 | 하부슬래브 : 제 1경간 중앙부 |  | 300 |  | H13 - 6.7EA |  |  | 150 | 349.902 | O.K |  | 2.333
8 | 하부슬래브 : 제 2경간 지점부 |  | 280 |  | H19 - 3.3EA + H16 - 3.3EA |  |  | 150 | 293.212 | O.K |  | 1.955
9 | 하부슬래브 : 제 2경간 중앙부 |  | 300 |  | H13 - 6.7EA |  |  | 150 | 349.902 | O.K |  | 2.333
10 | 하부슬래브 : 단지점부(우측) |  | 280 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 326.365 | O.K |  | 2.176
11 | 좌측벽체 : 상부 |  | 296.667 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 413.421 | O.K |  | 2.756
12 | 좌측벽체 : 중앙부 |  | 250 |  | H16 - 3.3EA |  |  | 300 | 553.095 | O.K |  | 1.844
13 | 좌측벽체 : 중앙부(부모멘트) |  | 230 |  | H16 - 3.3EA |  |  | 300 | 415.794 | O.K |  | 1.386
14 | 좌측벽체 : 하부 |  | 230 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 237.758 | O.K |  | 1.585
15 | 우측벽체 : 상부 |  | 296.667 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 413.42 | O.K |  | 2.756
16 | 우측벽체 : 중앙부 |  | 250 |  | H16 - 3.3EA |  |  | 300 | 553.096 | O.K |  | 1.844
17 | 우측벽체 : 중앙부(부모멘트) |  | 230 |  | H16 - 3.3EA |  |  | 300 | 415.791 | O.K |  | 1.386
18 | 우측벽체 : 하부 |  | 230 |  | H16 - 3.3EA + H13 - 3.3EA |  |  | 150 | 237.758 | O.K |  | 1.585
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 41.565 x 1000000 / [1084.333 x (346.667 - 65.350/3)]
= 117.988 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x346.7/(7x1084.333)]
= 65.350 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 117.99) - 2.5 x 62.00 = 512.44 mm
300 x (210 / fs) = 300 x (210 / 117.99) = 533.95 mm
Sa는 작은 값인 512.44 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 512.44 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 36.907 x 1000000 / [844.667 x (300.000 - 53.942/3)]
= 154.932 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x844.667/1000.0 + 7x844.667/1000.0 x √[(1 + 2x1000.0x300.0/(7x844.667)]
= 53.942 mm
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 13/2 = 43.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.93) - 2.5 x 43.50 = 399.54 mm
300 x (210 / fs) = 300 x (210 / 154.93) = 406.63 mm
Sa는 작은 값인 399.54 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 399.54 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 70.134 x 1000000 / [1324.000 x (346.667 - 71.427/3)]
= 164.069 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1324.000/1000.0 + 7x1324.000/1000.0 x √[(1 + 2x1000.0x346.7/(7x1324.000)]
= 71.427 mm
Use As = 1324.000 mm² (철근도심 : 70.000 mm)
1단 : H16 - 6.7 EA (= 1324.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 164.07) - 2.5 x 62.00 = 324.98 mm
300 x (210 / fs) = 300 x (210 / 164.07) = 383.98 mm
Sa는 작은 값인 324.98 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 324.98 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 36.907 x 1000000 / [844.667 x (300.000 - 53.942/3)]
= 154.932 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x844.667/1000.0 + 7x844.667/1000.0 x √[(1 + 2x1000.0x300.0/(7x844.667)]
= 53.942 mm
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 13/2 = 43.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 154.93) - 2.5 x 43.50 = 399.54 mm
300 x (210 / fs) = 300 x (210 / 154.93) = 406.63 mm
Sa는 작은 값인 399.54 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 399.54 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 41.565 x 1000000 / [1084.333 x (346.667 - 65.350/3)]
= 117.988 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x346.7/(7x1084.333)]
= 65.350 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 117.99) - 2.5 x 62.00 = 512.44 mm
300 x (210 / fs) = 300 x (210 / 117.99) = 533.95 mm
Sa는 작은 값인 512.44 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 512.44 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 46.238 x 1000000 / [1084.333 x (280.000 - 58.047/3)]
= 163.597 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x280.0/(7x1084.333)]
= 58.047 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 163.60) - 2.5 x 62.00 = 326.36 mm
300 x (210 / fs) = 300 x (210 / 163.60) = 385.09 mm
Sa는 작은 값인 326.36 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 326.36 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 1경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 40.901 x 1000000 / [844.667 x (300.000 - 53.942/3)]
= 171.699 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x844.667/1000.0 + 7x844.667/1000.0 x √[(1 + 2x1000.0x300.0/(7x844.667)]
= 53.942 mm
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 13/2 = 43.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 171.70) - 2.5 x 43.50 = 349.90 mm
300 x (210 / fs) = 300 x (210 / 171.70) = 366.92 mm
Sa는 작은 값인 349.90 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 349.90 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 73.621 x 1000000 / [1617.000 x (280.000 - 69.097/3)]
= 177.180 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1617.000/1000.0 + 7x1617.000/1000.0 x √[(1 + 2x1000.0x280.0/(7x1617.000)]
= 69.097 mm
Use As = 1617.000 mm² (철근도심 : 70.000 mm)
1단 : H19 - 3.3 EA + H16 - 3.3 EA (= 1617.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 19/2 = 60.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 177.18) - 2.5 x 60.50 = 293.21 mm
300 x (210 / fs) = 300 x (210 / 177.18) = 355.57 mm
Sa는 작은 값인 293.21 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 293.21 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 제 2경간 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 40.901 x 1000000 / [844.667 x (300.000 - 53.942/3)]
= 171.699 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x844.667/1000.0 + 7x844.667/1000.0 x √[(1 + 2x1000.0x300.0/(7x844.667)]
= 53.942 mm
Use As = 844.667 mm² (철근도심 : 50.000 mm)
1단 : H13 - 6.7 EA (= 844.667 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 13/2 = 43.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 171.70) - 2.5 x 43.50 = 349.90 mm
300 x (210 / fs) = 300 x (210 / 171.70) = 366.92 mm
Sa는 작은 값인 349.90 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 349.90 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 46.238 x 1000000 / [1084.333 x (280.000 - 58.047/3)]
= 163.597 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x280.0/(7x1084.333)]
= 58.047 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 163.60) - 2.5 x 62.00 = 326.36 mm
300 x (210 / fs) = 300 x (210 / 163.60) = 385.09 mm
Sa는 작은 값인 326.36 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 326.36 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 41.565 x 1000000 / [1084.333 x (296.667 - 59.946/3)]
= 138.542 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x296.7/(7x1084.333)]
= 59.946 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 138.54) - 2.5 x 62.00 = 413.42 mm
300 x (210 / fs) = 300 x (210 / 138.54) = 454.74 mm
Sa는 작은 값인 413.42 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 413.42 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 17.752 x 1000000 / [662.000 x (250.000 - 43.724/3)]
= 113.904 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x662.000/1000.0 + 7x662.000/1000.0 x √[(1 + 2x1000.0x250.0/(7x662.000)]
= 43.724 mm
Use As = 662.000 mm² (철근도심 : 50.000 mm)
1단 : H16 - 3.3 EA (= 662.000 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 113.90) - 2.5 x 42.00 = 586.37 mm
300 x (210 / fs) = 300 x (210 / 113.90) = 553.10 mm
Sa는 작은 값인 553.10 mm 를 적용
S = 1000.00 / 3.33 Ea = 300.00 ≤ Sa (= 553.10 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 19.735 x 1000000 / [662.000 x (230.000 - 41.768/3)]
= 137.966 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x662.000/1000.0 + 7x662.000/1000.0 x √[(1 + 2x1000.0x230.0/(7x662.000)]
= 41.768 mm
Use As = 662.000 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA (= 662.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 137.97) - 2.5 x 62.00 = 415.79 mm
300 x (210 / fs) = 300 x (210 / 137.97) = 456.64 mm
Sa는 작은 값인 415.79 mm 를 적용
S = 1000.00 / 3.33 Ea = 300.00 ≤ Sa (= 415.79 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 46.238 x 1000000 / [1084.333 x (230.000 - 51.985/3)]
= 200.505 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x230.0/(7x1084.333)]
= 51.985 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 200.51) - 2.5 x 62.00 = 237.76 mm
300 x (210 / fs) = 300 x (210 / 200.51) = 314.21 mm
Sa는 작은 값인 237.76 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 237.76 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 41.565 x 1000000 / [1084.333 x (296.667 - 59.946/3)]
= 138.542 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x296.7/(7x1084.333)]
= 59.946 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 138.54) - 2.5 x 62.00 = 413.42 mm
300 x (210 / fs) = 300 x (210 / 138.54) = 454.74 mm
Sa는 작은 값인 413.42 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 413.42 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 17.752 x 1000000 / [662.000 x (250.000 - 43.724/3)]
= 113.904 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x662.000/1000.0 + 7x662.000/1000.0 x √[(1 + 2x1000.0x250.0/(7x662.000)]
= 43.724 mm
Use As = 662.000 mm² (철근도심 : 50.000 mm)
1단 : H16 - 3.3 EA (= 662.000 mm²) , d1 = 50.00 mm
* 철근의 최대 중심간격
Cc = 50.00 - 16/2 = 42.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 113.90) - 2.5 x 42.00 = 586.37 mm
300 x (210 / fs) = 300 x (210 / 113.90) = 553.10 mm
Sa는 작은 값인 553.10 mm 를 적용
S = 1000.00 / 3.33 Ea = 300.00 ≤ Sa (= 553.10 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 19.735 x 1000000 / [662.000 x (230.000 - 41.768/3)]
= 137.966 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x662.000/1000.0 + 7x662.000/1000.0 x √[(1 + 2x1000.0x230.0/(7x662.000)]
= 41.768 mm
Use As = 662.000 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA (= 662.000 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 137.97) - 2.5 x 62.00 = 415.79 mm
300 x (210 / fs) = 300 x (210 / 137.97) = 456.63 mm
Sa는 작은 값인 415.79 mm 를 적용
S = 1000.00 / 3.33 Ea = 300.00 ≤ Sa (= 415.79 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 46.238 x 1000000 / [1084.333 x (230.000 - 51.985/3)]
= 200.505 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -7x1084.333/1000.0 + 7x1084.333/1000.0 x √[(1 + 2x1000.0x230.0/(7x1084.333)]
= 51.985 mm
Use As = 1084.333 mm² (철근도심 : 70.000 mm)
1단 : H16 - 3.3 EA + H13 - 3.3 EA (= 1084.333 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 16/2 = 62.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 200.51) - 2.5 x 62.00 = 237.76 mm
300 x (210 / fs) = 300 x (210 / 200.51) = 314.21 mm
Sa는 작은 값인 237.76 mm 를 적용
S = 1000.00 / 6.67 Ea = 150.00 ≤ Sa (= 237.76 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 3.300 m
- fy = 400 MPa
- 부재두께(T) = 0.35 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28
T = 3.300 / 28
T = 0.118 m < 0.350 m -----------> O.K

## 기초 지지력 검토
24. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 |  |  |  | = | 186.445 |  | / | 6.9 |  | = | 27.021 |  | kN/m²
|  |  | - 상부연직하중 |  |  |  | = | 38 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = |  |  |  |  | 15.486 |  | kN/m²
- 암거 내부 활하중
t = 0 mm (암거내부 포장두께)
T = 350 mm (하부 슬래브 두께)
b' = 0.500 + 2 × ( 0.350 + 0.000 ) × cot 45°
= 1.200 m
a' = 0.200 + 2 × ( 0.350 + 0.000 ) × cot 45°
= 0.900 m
|  |  |  | Qz = 96.0 / ( 1.200 × 0.900 ) = | [7 empty] | 88.889 |  | kN/m²
3) 최대 지반 반력
|  |  | Qmax |  | = | 27.021 |  | + | 38 |  | + | 15.486 |  | + | 88.889
[5 empty] | = | 169.396 |  | kN/m²

## 주철근 조립도
25. 주철근 조립도