## 표지
유량계실 구조계산서
▣ STA. 0K+020.000 ~ STA. 0K+021.000 (L = 1.00 m)
| ▣ 토 피(FH) | = | 0.25 m |  |  | ▣ 선 형 | = | ∞
| ▣ 지반 조건 | : | 토사
| ▣ 구조형식 | : | 폭 : 2.0M, 길이 : 2.5M, 높이 : 1.2M
|  |  |  | 1. | 설계요약표
|  |  |  | 2. | 설계조건
|  |  |  | 3. | 단면가정
|  |  |  | 4. | 부력검토
|  |  |  | 5. | 해석모델 및 단면제원
|  |  |  | 6. | 지반반력계수
|  |  |  | 7. | 하중계산
|  |  |  | 8. | 하중재하도
|  |  |  | 9. | 하중계수 및 하중조합
|  |  |  | 10. | INPUT DATA
|  |  |  | 11. | OUTPUT DATA
|  |  |  | 12. | 단면력정리
|  |  |  | 13. | 단면검토 및 철근량 산정
|  |  |  | 14. | 수평철근 검토
|  |  |  | 15. | 절점부 검토
|  |  |  | 16. | 사용성 검토
|  |  |  | 17. | 기초 지지력 검토
|  |  |  | 18. | 주철근 조립도

## 설계요약표
1. 설계 요약표
적용하중 | 내구성검토 : 사용하중, 단면검토 : 계수하중
설계조건 | 기초형식 : 직접기초, 토피고 : 0.3m, 지하수위 : GL -1.0m
안정(지지력)검토 | Qa = 150.000 kN/m² > Qmax = 64.304 kN/m² ======> O.K ! |  |  |  |  | 부력검토 |  | 시공후 안전율 = 3.08
단면 위치 | 내구성검토 |  | 단 면 검 토 | [8 empty] | 절 점 부 보 강
| 균열검토 |  | 휨 검 토 |  |  |  | 전 단 검 토
| 철근간격 mm | 최대간격 mm | 사용철근 | Mu kN.m | ΦMn kN.m | S.F | 사용철근 |  | Vu kN | ΦVn kN | 비고 | ftmax MPa | fta MPa | 사용철근
상부슬래브 : 단지점부(좌측) | 125 | 757.365 | D13 - 8.0EA | 26.77 | 54.661 | 2.04 | ∴ 전단보강 불필요 |  | - | - | O.K | 0.554 | 0.367 | D13 @125 - 8EA
상부슬래브 : 중앙부 | 125 | 643.42 | D16 - 8.0EA | 53.09 | 91.825 | 1.73 | ∴ 전단보강 불필요 |  | - | - | O.K
상부슬래브 : 단지점부(우측) | 125 | 757.427 | D13 - 8.0EA | 26.768 | 54.661 | 2.04 | ∴ 전단보강 불필요 |  | - | - | O.K | 0.554 | 0.367 | D13 @125 - 8EA
하부슬래브 : 단지점부(좌측) | 125 | 831.027 | D13 - 8.0EA | 24.897 | 57.246 | 2.3 | ∴ 전단보강 불필요 |  | - | - | O.K | 0.453 | 0.367 | D13 @125 - 8EA
하부슬래브 : 중앙부 | 125 | 744.742 | D13 - 8.0EA | 28.626 | 59.831 | 2.09 | ∴ 전단보강 불필요 |  | - | - | O.K
하부슬래브 : 단지점부(우측) | 125 | 830.941 | D13 - 8.0EA | 24.9 | 57.246 | 2.3 | ∴ 전단보강 불필요 |  | - | - | O.K | 0.453 | 0.367 | D13 @125 - 8EA
좌측벽체 : 상부 | 125 | 626.914 | D13 - 8.0EA | 31.097 | 54.661 | 1.76 | ∴ 전단보강 불필요 |  | - | - | O.K
좌측벽체 : 중앙부 | - | - | D13 - 8.0EA | 0 | 59.831 | 0 | ∴ 전단보강 불필요 |  | - | - | O.K
좌측벽체 : 중앙부(부모멘트) | 125 | 772.257 | D13 - 8.0EA | 25.924 | 54.661 | 2.11 | ∴ 전단보강 불필요 |  | - | - | O.K
좌측벽체 : 하부 | 125 | 895.968 | D13 - 8.0EA | 22.014 | 54.661 | 2.48 | ∴ 전단보강 불필요 |  | - | - | O.K
우측벽체 : 상부 | 125 | 626.974 | D13 - 8.0EA | 31.094 | 54.661 | 1.76 | ∴ 전단보강 불필요 |  | - | - | O.K
우측벽체 : 중앙부 | - | - | D13 - 8.0EA | 0 | 59.831 | 0 | ∴ 전단보강 불필요 |  | - | - | O.K
우측벽체 : 중앙부(부모멘트) | 125 | 772.286 | D13 - 8.0EA | 25.923 | 54.661 | 2.11 | ∴ 전단보강 불필요 |  | - | - | O.K
우측벽체 : 하부 | 125 | 895.854 | D13 - 8.0EA | 22.017 | 54.661 | 2.48 | ∴ 전단보강 불필요 |  | - | - | O.K
부상방지턱 : 내측 지점부 | 125 | 2210.311 | D13 - 8.0EA | 7.394 | 57.246 | 7.74 | ∴ 전단보강 불필요 |  | - | - | O.K

## 설계조건
2. 설계조건
1) 구조형식
- 지중 1 련 암거 ( 내공 : 2M ⅹ 1.2M, 사각 : 90°)
2) 지하수위
| - GL 에서 | -1 | m
3) 재료 중량
| - 철근콘크리트 |  |  | = | 24.5 |  | kN/m³
| - Mortar |  |  | = | 21.5 |  | kN/m³
| - 포 장 |  |  | = | 22.5 |  | kN/m³
| - 지 하 수 |  |  | = | 10 |  | kN/m³
4) 사용재료의 강도
| - 콘크리트 강도 |  | (fck) |  | = | 21 |  |  | MPa
| - 콘크리트 탄성계수 |  | (Ec) |  | = | 26114.7 |  |  | MPa
| - 철근(SD300) |  | (fy) |  | = | 300 |  |  | MPa
| - 철근의 탄성계수 |  | (Es) |  | = | 200000 |  |  | MPa
5) 토압계산에 사용되는 흙의 단위중량
: 입도배합이 양호한 모래, 자갈, 경암 및 일반적인 모래
| - 일 반 |  |  |  | = | 19 |  | kN/m³
| - 수 중 |  |  |  | = | 10 |  | kN/m³
| 6) 노면활하중 (DB-24 적용) |  |  |  |  | = | 연행하중 재하 (∵ 토피 : |  |  |  |  | 0.25 | m | )
7) 토 사
| - 흙의 습윤 단위중량 | [5 empty] | = | 19 |  | kN/m³
| - 흙의 수중 단위중량 | [5 empty] | = | 10 |  | kN/m³
| - 흙의 내부마찰각 | [5 empty] | = | 30.0°
| - 정지토압계수 |  |  |  | (Ko) |  | = | 1-sinΦ |  | = | 0.5
8) 설계방법
- 강도설계법 : 부재의 단면검토 (슬래브, 벽체, 보, 기둥)
- 허용응력 설계법 : 사용성 검토 (처짐, 균열, 절점부보강 등)
| 9) 사용프로그램 : |  | SAP2000
10) 참고문헌
| - 콘크리트 구조설계기준.해설 |  |  |  |  | : 건설교통부(2007)
| - 도로교 설계기준 |  |  |  |  | : 건설교통부(2005)
| - 철도설계기준 (철도교편) |  |  |  |  | : 건설교통부(2004)
| - 철도설계기준 (노반편) |  |  |  |  | : 건설교통부(2004)

## 단면가정
3. 단면 가정

## 부력검토
4. 부력 검토
: 부력에 대한 안전률 Fs = R/B
| 공사중 Fs |  |  | = | 1.1
| 완공후 Fs |  |  | = | 1.2
부력에 대한 안정계산시 구체자중과 측면마찰력, 상재하중만을 고려 (최소토피 H = 0.250 m 에 대하여
검토)
1) 구체자중
|  | - 2.600 × 0.300 × 24.5 | [14 empty] | = |  | 19.11 |  | kN/m
|  | - 3.000 × 0.300 × 24.5 | [14 empty] | = |  | 22.05 |  | kN/m
|  | - 0.300 × 1.200 × 24.5 | [14 empty] | = |  | 8.82 |  | kN/m
|  | - 0.300 × 1.200 × 24.5 | [14 empty] | = |  | 8.82 |  | kN/m
[14 empty] | ∴ Total |  |  | = | 58.8 |  |  | kN/m
2) 상재 하중
|  | - ASPHALT 포장하중 | [6 empty] | : | 0.25 × 22.50 × 2.60 | [6 empty] | = |  | 14.625 |  | kN/m
[14 empty] | ∴ Total |  |  | = | 14.625 |  |  | kN/m
3) 부상방지턱
|  | - ASPHALT 포장하중 | [6 empty] | : | 0.25 × 22.50 × 0.20 × 2 | [6 empty] | = |  | 2.25 |  | kN/m
|  | - 흙의 자중(지하수위 이상) | [6 empty] | : | 0.75 × 19.00 × 0.20 × 2 | [6 empty] | = |  | 5.7 |  | kN/m
|  | - 흙의 자중(지하수위 이하) | [6 empty] | : | 0.75 × 10.00 × 0.20 × 2 | [6 empty] | = |  | 3 |  | kN/m
|  | - 지하수 자중 | [6 empty] | : | 0.75 × 10.00 × 0.20 × 2 | [6 empty] | = |  | 3 |  | kN/m
[15 empty] | ∴ Total = |  |  |  | 13.95 |  | kN/m
4) 측면 마찰력
※ 파괴면이 비교적 구조물 벽면에 인접하여 있으므로 구조물과 지반의 상대마찰각으로
생각하여 δ=2/3×φ로 적용
|  | - | [7 empty] | (지하수위 이상)
|  |  |  | = | 0.5 |  | × | 19 |  | × | 1 |  | ² | × | tan( 30.0 × 2 / 3 )
|  |  |  | = | 3.4577 |  | kN/m
|  | - | [12 empty] | (지하수위 이하)
|  |  |  | = | 0.5 |  | × ( | 2× | 1 |  | × | 0.75 |  | × | 19 |  | + | 0.75 |  | ²× | 10 | ) | ×
tan( 30.0 × 2 / 3 )
|  |  |  | = | 6.2102 |  | kN/m
|  | ∴ Total = |  |  | 3.4577 |  | + | 6.2102 |  | = | 9.668 |  | kN/m
※ 구조물 벽체와 주변 뒷채움 흙과의 측면 마찰력은 재질간의 접촉 불확실성을 고려하여 무시한다.
[ 철도설계기준2004(노반편,p.170) ]
5) 부 력
|  | - |  |  |  |  | = | ( | 2.05 |  | - | 1 |  | ) | × | 3 |  | × | 10
|  |  |  | = | 31.5 |  |  | kN/m
6) 완공후 안정검토
|  | - | S.F | = | ( | 58.8 |  |  | + | 14.625 |  | + | 13.95 |  | + | 9.668 |  | ) | / | 31.5
|  |  |  | = | 3.081 |  | > | 1.2 | [10 empty] | ‥‥‥‥‥‥> |  |  | O.K

## 해석모델 및 단면제원
5. 해석모델 및 단면제원
1) Modeling
본 구조물과 같은 지하 박스는 종방향으로 동일한 패턴이 반복·지속되므로 평면 해석이 가능하다.
따라서 구조해석용 프로그램인 SAP2000을 이용하여 2차원 보요소를 사용하여 구조해석을 수행하도록
한다. 해석 모델에서 하부슬래브와 지반이 접하는 부분은 NLLink요소로 모델링을 하였는데, 지반반력
스프링의 특성이 압축에만 저항하고 인장에는 저항하지 못하기 때문에 이를 해석에서 반영하기 위하여
압축에만 저항하는 GAP 특성을 이용하여 모형화 하였다.
이와같은 모형화 기법은 하부슬래브의 지지지반을 탄성체로 보고 해석하기 위한 것으로, 그 이론적
근거는 BEF(Beams on Elastic Foundation) Analogy에 바탕을 두고 있다.
2) 단면제원
| NO | A (m²) |  |  |  | I (m⁴) |  | 부 재
| 1 | 0.300 × 1.000 = 0.300 |  |  |  | 0.00225 |  | 1~18
3) 단면좌표
(단위 : m)
| 절점번호 |  | X | Z | 절점번호 |  | X |  | Z
| 1 |  | 0.15 | 0.15 | 10 |  | 2.45 |  | 1.65
| 2 |  | 0.53 | 0.15 | 11 |  | 2.08 |  | 1.65
| 3 |  | 0.725 | 0.15 | 12 |  | 1.3 |  | 1.65
| 4 |  | 1.3 | 0.15 | 13 |  | 0.52 |  | 1.65
| 5 |  | 1.875 | 0.15 | 14 |  | 0.15 |  | 1.65
| 6 |  | 2.07 | 0.15 | 15 |  | 0.15 |  | 1.28
| 7 |  | 2.45 | 0.15 | 16 |  | 0.15 |  | 0.52
| 8 |  | 2.45 | 0.52 | 17 |  | -0.2 |  | 0.15
| 9 |  | 2.45 | 1.28 | 18 |  | 2.8 |  | 0.15
4) 강역설정
∴ B = 헌치폭 (mm), H = 헌치높이 (mm)
(1) 14 지점 - 슬래브 상면
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(2) 14 지점 - 슬래브 벽체 연결부
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(3) 10 지점 - 슬래브 상면
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(4) 10 지점 - 슬래브 상면과 벽체 연결부
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(5) 1 지점 - 슬래브 하면
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(6) 1 지점 - 슬래브 하면과 벽체 연결부
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(7) 7 지점 - 슬래브 하면
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm
(8) 7 지점 - 슬래브 하면과 벽체 연결부
- D2 / 2 - 0.25 × D1 = 300 / 2 - 0.25 × 300 = 75 mm

## 지반반력계수
6. 지반반력계수
< 연직방향 지반반력계수 >
- 사질토층이 우세한 경우
- 사질토와 점성토의 혼합층인 경우
- 점성토층이 우세한 경우
α = Eo 의 산정방법에 대한 보정계수
Eo = 지반의 탄성계수
- 연직방향 지반반력계수 (Kv)
여기서,
Eo : 지반탄성계수 (kN/m²)
|  | α | = | 1 | (표준관입시험치 N값을 이용하여 Eo= 2800N(kN/m²)으로 추정한 변형계수)
|  | N | = | 20
|  | Eo | = | 2800 × N |  | = | 56000 | kN/m²
|  | Bv | = | √( B × L ) |  | = | √( 2.600 × 1.000 ) |  |  | = | 1.612 | m (L < B)
|  | Kvo | = | 1 / 0.3 × 1 × 56000 |  | = | 186670 | kN/m³
|  | Kv | = | 186670.000 × ( 1.612 / 0.3 )^( -3 / 4 ) | [5 empty] | = | 52881.098 | kN/m³
| 지반반력계수 |  |  | 계 산 식 |  |  |  |  | 해당 절점
| Kv1 |  |  | Kvⅹ(0.350/2 + 0.575/2) = 24457 kN/m |  |  |  |  | 1,7
| Kv2 |  |  | Kvⅹ(0.575/2 + 0.575/2) = 30406 kN/m |  |  |  |  | 3~5
| Kv3 |  |  | Kvⅹ(0.000/2 + 0.350/2) = 9254 kN/m |  |  |  |  | 17,18
| Kh |  |  | 1E10 kN/m (무한강성) |  |  |  |  | 17

## 하중계산
7. 하 중 계 산
1) 구체자중 - 프로그램내에서 내에서 자동계산
2) 고정하중 ( 지하수가 없을 경우, α = 1.019 ≤ 1.15)
|  | - ASPHALT 포장하중 | [5 empty] | : | 0.25 × 22.50 | [5 empty] | = | 5.625 |  | kN/m²
[14 empty] | ∴ Total Wd1 | = | 5.623 |  | kN/m²
[12 empty] | ∴ Total Wd1 × α |  |  | = | 5.73 |  | kN/m²
3) 부상방지턱에 작용하는 고정하중 ( 지하수가 없을경우, α = 1.019 ≤ 1.15)
|  | - ASPHALT 포장하중 | [5 empty] | : | 0.25 × 22.50 | [5 empty] | = | 5.625 |  | kN/m²
|  | - 토 사 | [5 empty] | : | 1.50 × 19.00 | [5 empty] | = | 28.5 |  | kN/m²
[14 empty] | ∴ Total We1 | = | 34.122 |  | kN/m²
[12 empty] | ∴ Total We1 × α |  |  | = | 34.77 |  | kN/m²
4) 고정하중 ( 지하수가 있을 경우 : GL = -1.0 m, α = 1.019 ≤ 1.15 )
|  | - ASPHALT 포장하중 | [5 empty] | : | 0.25 × 22.50 | [5 empty] | = | 5.625 |  | kN/m²
[14 empty] | ∴ Total Wd2 | = | 5.623 |  | kN/m²
[12 empty] | ∴ Total Wd2 × α |  |  | = | 5.73 |  | kN/m²
5) 부상방지턱에 작용하는 고정하중 ( 지하수가 있을경우, α = 1.019 ≤ 1.15 )
|  | - ASPHALT 포장하중 | [5 empty] | : | 0.25 × 22.50 | [5 empty] | = | 5.625 |  | kN/m²
|  | - 흙(지하수위 이상) | [5 empty] | : | 0.75 × 19.00 | [5 empty] | = | 14.25 |  | kN/m²
|  | - 흙(지하수위 이하) | [5 empty] | : | 0.75 × 10.00 | [5 empty] | = | 7.5 |  | kN/m²
[14 empty] | ∴ Total We2 | = | 27.38 |  | kN/m²
[12 empty] | ∴ Total We2 × α |  |  | = | 27.9 |  | kN/m²
6) 활 하 중
- 측벽에 작용하는 하중
|  |  | - Wl2 |  | = | 10.000 × 0.500 |  |  |  | = | 5 |  | kN/m²
7) 상부슬래브에 작용하는 활하중 (주철근이 차량진행방향에 평행인 경우)
① 차량하중 (DB-24 하중 재하시)
- 설계유효 지간장 : 2.300 m
- 유효폭 산정
E = 1.2 + 0.06 × L = 1.2 + 0.06 × 2.300 = 1.338 < 2.100 m
∴ E = 1.338 m
- 충격계수
i = 15 / ( 40 + L ) = 15 / ( 40 + 2.300 ) = 0.355 > 0.300
∴ i = 0.300
- 설계차선수 산정
Wci < 6.0 ===> 1차선 재하
- 차선수에 따른 활하중 산정
(1) 1차선 재하시
Pn = 2 × P × ( 1 + i ) / L
Pr = 2 × 96.0 × ( 1 + 0.300 ) / 3.138 = 79.541 kN/m
Pf = 2 × 24.0 × ( 1 + 0.300 ) / 3.138 = 19.885 kN/m
(단위 : kN/m)
|  | 구분 |  | 1차선 재하 |  |  | 비고
|  | Pr |  | 79.541 |  |  | DB-24
|  | Pf |  | 19.885 |  |  | DB-24
∴ 1차선 재하시가 가장 불리하므로 1차선을 재하한다.
② 차량하중 (DL-24하중 재하시)
Wl = 12.700 × ( 1 + 0.300 ) × 1 / 3.00 = 5.503 kN/m²
Pm = 108.000 × ( 1 + 0.300 ) × 1 / 3.00 = 46.800 kN/m²
Ps = 156.000 × ( 1 + 0.300 ) × 1 / 3.00 = 67.600 kN/m²
8) 토 압 (지하수가 없을경우)
|  | - Wh1 |  | = | (0.250 × 22.500 + 0.150 × 19.000) × 0.500 | [11 empty] | = | 4.237 | kN/m²
|  | - Wh2 |  | = | 4.237 + 0.370 × 19.000 × 0.500 | [11 empty] | = | 7.748 | kN/m²
|  | - Wh3 |  | = | 7.748 + 0.760 × 19.000 × 0.500 | [11 empty] | = | 14.968 | kN/m²
|  | - Wh4 |  | = | 14.968 + 0.370 × 19.000 × 0.500 | [11 empty] | = | 18.488 | kN/m²
9) 토 압 (지하수가 있을경우)
|  | - Wh'1 |  | = | (0.250 × 22.500 + 0.150 × 19.000) × 0.500 | [11 empty] | = | 4.237 | kN/m²
|  | - Wh'2 |  | = | 4.237 + 0.370 × 19.000 × 0.500 | [11 empty] | = | 7.748 | kN/m²
|  | - Wh'3 |  | = | 7.748 + 0.230 × 19.000 × 0.500 | [11 empty] | = | 9.938 | kN/m²
|  | - Wh'4 |  | = | 9.938 + 0.530 × 10.000 × 0.500 | [11 empty] | = | 12.588 | kN/m²
|  | - Wh'5 |  | = | 12.588 + 0.370 × 10.000 × 0.500 | [11 empty] | = | 14.438 | kN/m²
10) 지하수압 ( 지하수위 : GL = -1.0 m )
① 측벽에 작용하는 하중
|  | - Ww1 |  | = | 0.530 × 10.000 | [11 empty] | = | 5.3 | kN/m²
|  | - Ww2 |  | = | 5.300 + 0.370 × 10.000 | [11 empty] | = | 9 | kN/m²
② 하부 슬래브에 작용하는 하중
|  | - Wo1 |  | = | ( 0.250 + 1.800 - 1.000 ) × 10.000 | [11 empty] | = | 10.5 | kN/m²
③ 부상방지턱 상부에 작용하는 하중
|  | - Wo'1 |  | = | ( 0.250 + 1.500 - 1.000 ) × 10.000 | [11 empty] | = | 7.5 | kN/m²

## 하중재하도
8. 하중 재하
1) CASE1 -
2) CASE2 - 고정하중(지하수 없는경우)
3) CASE3 - 고정하중(지하수 있는경우)
4) CASE4 - 활하중에 의한 수평토압
5) CASE5 - 차량하중 ( DB-24 재하시 )
6) CASE6 - 차량하중 ( DL-24 재하시 )
7) CASE7 - 수평토압 (양측, 지하수 없는경우)
8) CASE8 - 수평토압 (양측, 지하수 있는경우)
9) CASE9 - 연직수압
10) CASE10 - 수평수압

## 하중계수 및 하중조합
9. 하중계수 및 하중조합
αH : 토피의 두께에 따른 연직방향 하중Hv에 대한 보정계수
h ≤ 2.0 m 에 대해서, αH = 1.0
h ＞ 2.0 m 에 대해서, αH = 1.05 - 0.025h (≥ 0.875) = 1.000, h = 0.250 m
1) 극한하중 검토시
구분 |  |  | 고정하중 |  |  | 활하중 | 수평하중 | 토압 | 연직수압 | 수평수압
|  |  | 구체자중 | 지하수 無 | 지하수 有
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
일반적인 경우 (전토압) |  | 1 | 1.4 | 1.4
|  | 2 | 1.4 |  | 1.4 |  |  |  | 1.4
|  | 3 | 1.2 | 1.6 |  | 1.6 | 1.6 | 1.6
|  | 4 | 1.2 | 1.6 |  |  | 1.6 | 1.6
|  | 5 | 1.2 |  | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
|  | 6 | 1.2 |  | 1.6 |  | 1.6 | 1.6 | 1.6 | 1.6
|  | 7 | 1.2 |  |  | 1
|  | 8 | 1.2
상판 정모멘트 검토시 (반토압) |  | 9 | 1.2 | 1.6 |  | 1.6 | 0.8 | 0.8
|  | 10 | 1.2 | 1.6 |  |  | 0.8 | 0.8
|  | 11 | 1.2 |  | 1.6 | 1.6 | 0.8 | 0.8 | 1.6 | 0.8
|  | 12 | 1.2 |  | 1.6 |  | 0.8 | 0.8 | 1.6 | 0.8
2) 사용하중 검토시
구분 |  |  | 고정하중 |  |  | 활하중 | 수평하중 | 토압 | 연직수압 | 수평수압
|  |  | 구체자중 | 지하수 無 | 지하수 有
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
일반적인 경우 (전토압) |  | 1 | 1 | 1
|  | 2 | 1 |  | 1 |  |  |  | 1
|  | 3 | 1 | 1 |  | 1 | 1 | 1
|  | 4 | 1 | 1 |  |  | 1 | 1
|  | 5 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1
|  | 6 | 1 |  | 1 |  | 1 | 1 | 1 | 1
|  | 7 | 1 |  |  | 1
|  | 8 | 1
상판 정모멘트 검토시 (반토압) |  | 9 | 1 | 1 |  | 1 | 0.5 | 0.5
|  | 10 | 1 | 1 |  |  | 0.5 | 0.5
|  | 11 | 1 |  | 1 | 1 | 0.5 | 0.5 | 1 | 0.5
|  | 12 | 1 |  | 1 |  | 0.5 | 0.5 | 1 | 0.5

## INPUT
10. INPUT DATA
| SYSTEM | ADD=15 RD=0,1 UX=5,5
| DOF=UX,UZ,RY LENGTH=M FORCE=kN | ADD=16 RD=0,1 UX=5,5
NAME=NWSOFULL
| JOINT | TYPE=Distributed Span
| 1 X= 0.150 Y= 0.000 Z= 0.150 | ADD=7 RD=0,1 UX=-18.4875,-14.9675
| 2 X= 0.530 Y= 0.000 Z= 0.150 | ADD=8 RD=0,1 UX=-14.9675,-7.7575
| 3 X= 0.725 Y= 0.000 Z= 0.150 | ADD=9 RD=0,1 UX=-7.7575,-4.2375
| 4 X= 1.300 Y= 0.000 Z= 0.150 | ADD=14 RD=0,1 UX=4.2375,7.7475
| 5 X= 1.875 Y= 0.000 Z= 0.150 | ADD=15 RD=0,1 UX=7.7475,14.9675
| 6 X= 2.070 Y= 0.000 Z= 0.150 | ADD=16 RD=0,1 UX=14.9675,18.4875
| 7 X= 2.450 Y= 0.000 Z= 0.150 | NAME=SOILFULL
| 8 X= 2.450 Y= 0.000 Z= 0.520 | TYPE=Distributed Span
| 9 X= 2.450 Y= 0.000 Z= 1.280 | ADD=7 RD=0,1 UX=-14.4375,-12.5875
| 10 X= 2.450 Y= 0.000 Z= 1.650 | ADD=8 RD=0,0.69737 UX=-12.5875,-9.9375
| 11 X= 2.080 Y= 0.000 Z= 1.650 | ADD=8 RD=0.69737,1 UX=-9.9375,-7.7575
| 12 X= 1.300 Y= 0.000 Z= 1.650 | ADD=9 RD=0,1 UX=-7.7575,-4.2375
| 13 X= 0.520 Y= 0.000 Z= 1.650 | ADD=14 RD=0,1 UX=4.2375,7.7475
| 14 X= 0.150 Y= 0.000 Z= 1.650 | ADD=15 RD=0,0.30263 UX=7.7475,9.9375
| 15 X= 0.150 Y= 0.000 Z= 1.280 | ADD=15 RD=0.30263,1 UX=9.9375,12.5875
| 16 X= 0.150 Y= 0.000 Z= 0.520 | ADD=16 RD=0,1 UX=12.5875,14.4375
| 17 X= -0.200 Y= 0.000 Z= 0.150 | NAME=VERWATER
| 18 X= 2.800 Y= 0.000 Z= 0.150 | TYPE=Distributed Span
ADD=1 RD=0,1 UZ=10.5,10.5
| SPRING | ADD=2 RD=0,1 UZ=10.5,10.5
| ADD=1 U3=24457.1 | ADD=3 RD=0,1 UZ=10.5,10.5
| ADD=3 U3=30406.1 | ADD=4 RD=0,1 UZ=10.5,10.5
| ADD=4 U3=30406.1 | ADD=5 RD=0,1 UZ=10.5,10.5
| ADD=5 U3=30406.1 | ADD=6 RD=0,1 UZ=10.5,10.5
| ADD=7 U3=24457.1 | ADD=17 RD=0,1 UZ=-7.5,-7.5
| ADD=17 U1=1e+010 U3=9254.03 | ADD=17 RD=0,1 UZ=10.5,10.5
| ADD=18 U3=9254.03 | ADD=18 RD=0,1 UZ=-7.5,-7.5
ADD=18 RD=0,1 UZ=10.5,10.5
| MATERIAL | NAME=HORWATER
| NAME=CONC IDES=C M=0.0001 W=24.5 | TYPE=Distributed Span
| T=0 E=2.61147e+007 U=0.17 A=9.99e-006 | ADD=7 RD=0,1 UX=-9,-5.3
ADD=8 RD=0,0.69737 UX=-5.3,0
| FRAME SECTION | ADD=15 RD=0.30263,1 UX=0,5.3
| NAME=1 MAT=CONC SH=R T=0.3, 1 | ADD=16 RD=0,1 UX=5.3,9
| FRAME | LANE
| 1 J= 1, 2 SEC=1 IOFF=0.075 RIGID=1 NSEG=1 ANG=180 | NAME=LANE1
| 2 J= 2, 3 SEC=1 NSEG=1 ANG=180 | PATH=10
| 3 J= 3, 4 SEC=1 NSEG=2 ANG=180 | PATH=11
| 4 J= 4, 5 SEC=1 NSEG=2 ANG=180 | PATH=12
| 5 J= 5, 6 SEC=1 NSEG=1 ANG=180 | PATH=13
6 J= 6, 7 SEC=1 JOFF=0.075 RIGID=1 NSEG=1 ANG=180
| 7 J= 7, 8 SEC=1 IOFF=0.075 RIGID=1 NSEG=1 ANG=0 | VEHICLE
| 8 J= 8, 9 SEC=1 NSEG=2 ANG=0 | NAME=DB-24 TYPE=GEN
| 9 J= 9, 10 SEC=1 JOFF=0.075 RIGID=1 NSEG=1 ANG=0 | P=19.8853
| 10 J= 10, 11 SEC=1 IOFF=0.075 RIGID=1 NSEG=1 ANG=0 | D=4.2,4.2 P=79.5411
| 11 J= 11, 12 SEC=1 NSEG=2 ANG=0 | D=4.2,9 P=79.5411
| 12 J= 12, 13 SEC=1 NSEG=2 ANG=0 | NAME=DL-24 TYPE=GEN
| 13 J= 13, 14 SEC=1 JOFF=0.075 RIGID=1 NSEG=1 ANG=0 | W=5.50333 PM=46.8 PXM=67.6
14 J= 14, 15 SEC=1 IOFF=0.075 RIGID=1 NSEG=1 ANG=180
| 15 J= 15, 16 SEC=1 NSEG=2 ANG=180 | VEHICLE CLASS
| 16 J= 16, 1 SEC=1 JOFF=0.075 RIGID=1 NSEG=1 ANG=180 | NAME=GENERAL
| 17 J= 17, 1 SEC=1 NSEG=1 ANG=180 | VEHI=DB-24
| 18 J= 7, 18 SEC=1 NSEG=1 ANG=180 | VEHI=DL-24
| LOAD | BRIDGE RESPONSE
| NAME=SELFWGT SW=1 | ELEM=JOINT TYPE=REAC
| NAME=NWDEAD | ADD=*
| TYPE=Distributed Span | ELEM=FRAME
| ADD=10 RD=0,1 UZ=-5.73,-5.73 | ADD=*
ADD=11 RD=0,1 UZ=-5.73,-5.73
| ADD=12 RD=0,1 UZ=-5.73,-5.73 | MOVING LOAD
| ADD=13 RD=0,1 UZ=-5.73,-5.73 | QUICK=0 CORR=N TOL=0.0001
| ADD=17 RD=0,1 UZ=-34.77,-34.77 | NAME=GENERAL RF=1
| ADD=18 RD=0,1 UZ=-34.77,-34.77 | CLASS=GENERAL LANE=* LMIN=1 LMAX=1
NAME=DEAD
| TYPE=Distributed Span | COMBO
| ADD=10 RD=0,1 UZ=-5.73,-5.73 | NAME=BR1 TYPE=ENVE
| ADD=11 RD=0,1 UZ=-5.73,-5.73 | MOVE=GENERAL SF=1
| ADD=12 RD=0,1 UZ=-5.73,-5.73 | NAME=COMB1 TYPE=ADD
| ADD=13 RD=0,1 UZ=-5.73,-5.73 | LOAD=SELFWGT SF=1.4
| ADD=17 RD=0,1 UZ=-27.9,-27.9 | LOAD=NWDEAD SF=1.4
| ADD=18 RD=0,1 UZ=-27.9,-27.9 | NAME=COMB2 TYPE=ADD
| NAME=HORLIVE | LOAD=SELFWGT SF=1.4
| TYPE=Distributed Span | LOAD=DEAD SF=1.4
| ADD=7 RD=0,1 UX=-5,-5 | LOAD=VERWATER SF=1.4
| ADD=8 RD=0,1 UX=-5,-5 | NAME=COMB3 TYPE=ADD
| ADD=9 RD=0,1 UX=-5,-5 | LOAD=SELFWGT SF=1.2
| ADD=14 RD=0,1 UX=5,5 | LOAD=NWDEAD SF=1.6
| COMB=BR1 SF=1.6 | LOAD=HORWATER SF=1
| LOAD=HORLIVE SF=1.6 | NAME=COMB19 TYPE=ADD
| LOAD=NWSOFULL SF=1.6 | LOAD=SELFWGT SF=1
| NAME=COMB4 TYPE=ADD | COMB=BR1 SF=1
| LOAD=SELFWGT SF=1.2 | NAME=COMB20 TYPE=ADD
| LOAD=NWDEAD SF=1.6 | LOAD=SELFWGT SF=1
| LOAD=HORLIVE SF=1.6 | NAME=COMB21 TYPE=ADD
| LOAD=NWSOFULL SF=1.6 | LOAD=SELFWGT SF=1
| NAME=COMB5 TYPE=ADD | LOAD=NWDEAD SF=1
| LOAD=SELFWGT SF=1.2 | COMB=BR1 SF=1
| LOAD=DEAD SF=1.6 | LOAD=HORLIVE SF=0.5
| COMB=BR1 SF=1.6 | LOAD=NWSOFULL SF=0.5
| LOAD=HORLIVE SF=1.6 | NAME=COMB22 TYPE=ADD
| LOAD=SOILFULL SF=1.6 | LOAD=SELFWGT SF=1
| LOAD=VERWATER SF=1.6 | LOAD=NWDEAD SF=1
| LOAD=HORWATER SF=1.6 | LOAD=HORLIVE SF=0.5
| NAME=COMB6 TYPE=ADD | LOAD=NWSOFULL SF=0.5
| LOAD=SELFWGT SF=1.2 | NAME=COMB23 TYPE=ADD
| LOAD=DEAD SF=1.6 | LOAD=SELFWGT SF=1
| LOAD=HORLIVE SF=1.6 | LOAD=DEAD SF=1
| LOAD=SOILFULL SF=1.6 | COMB=BR1 SF=1
| LOAD=VERWATER SF=1.6 | LOAD=HORLIVE SF=0.5
| LOAD=HORWATER SF=1.6 | LOAD=SOILFULL SF=0.5
| NAME=COMB7 TYPE=ADD | LOAD=VERWATER SF=1
| LOAD=SELFWGT SF=1.2 | LOAD=HORWATER SF=0.5
| COMB=BR1 SF=1 | NAME=COMB24 TYPE=ADD
| NAME=COMB8 TYPE=ADD | LOAD=SELFWGT SF=1
| LOAD=SELFWGT SF=1.2 | LOAD=DEAD SF=1
| NAME=COMB9 TYPE=ADD | LOAD=HORLIVE SF=0.5
| LOAD=SELFWGT SF=1.2 | LOAD=SOILFULL SF=0.5
| LOAD=NWDEAD SF=1.6 | LOAD=VERWATER SF=1
| COMB=BR1 SF=1.6 | LOAD=HORWATER SF=0.5
| LOAD=HORLIVE SF=0.8 | NAME=ULTIMATE TYPE=ENVE
| LOAD=NWSOFULL SF=0.8 | COMB=COMB1 SF=1
| NAME=COMB10 TYPE=ADD | COMB=COMB2 SF=1
| LOAD=SELFWGT SF=1.2 | COMB=COMB3 SF=1
| LOAD=NWDEAD SF=1.6 | COMB=COMB4 SF=1
| LOAD=HORLIVE SF=0.8 | COMB=COMB5 SF=1
| LOAD=NWSOFULL SF=0.8 | COMB=COMB6 SF=1
| NAME=COMB11 TYPE=ADD | COMB=COMB7 SF=1
| LOAD=SELFWGT SF=1.2 | COMB=COMB8 SF=1
| LOAD=DEAD SF=1.6 | COMB=COMB9 SF=1
| COMB=BR1 SF=1.6 | COMB=COMB10 SF=1
| LOAD=HORLIVE SF=0.8 | COMB=COMB11 SF=1
| LOAD=SOILFULL SF=0.8 | COMB=COMB12 SF=1
| LOAD=VERWATER SF=1.6 | NAME=SERVICE TYPE=ENVE
| LOAD=HORWATER SF=0.8 | COMB=COMB13 SF=1
| NAME=COMB12 TYPE=ADD | COMB=COMB14 SF=1
| LOAD=SELFWGT SF=1.2 | COMB=COMB15 SF=1
| LOAD=DEAD SF=1.6 | COMB=COMB16 SF=1
| LOAD=HORLIVE SF=0.8 | COMB=COMB17 SF=1
| LOAD=SOILFULL SF=0.8 | COMB=COMB18 SF=1
| LOAD=VERWATER SF=1.6 | COMB=COMB19 SF=1
| LOAD=HORWATER SF=0.8 | COMB=COMB20 SF=1
| NAME=COMB13 TYPE=ADD | COMB=COMB21 SF=1
| LOAD=SELFWGT SF=1 | COMB=COMB22 SF=1
| LOAD=NWDEAD SF=1 | COMB=COMB23 SF=1
| NAME=COMB14 TYPE=ADD | COMB=COMB24 SF=1
LOAD=SELFWGT SF=1
| LOAD=DEAD SF=1 | OUTPUT
| LOAD=VERWATER SF=1 | ELEM=JOINT TYPE=REAC,DISP,APP LOAD=* COMB=* HIST=*
| NAME=COMB15 TYPE=ADD | ELEM=FRAME TYPE=FORCE LOAD=* COMB=* HIST=*
LOAD=SELFWGT SF=1
LOAD=NWDEAD SF=1
COMB=BR1 SF=1
LOAD=HORLIVE SF=1
LOAD=NWSOFULL SF=1
NAME=COMB16 TYPE=ADD
LOAD=SELFWGT SF=1
LOAD=NWDEAD SF=1
LOAD=HORLIVE SF=1
LOAD=NWSOFULL SF=1
NAME=COMB17 TYPE=ADD
LOAD=SELFWGT SF=1
LOAD=DEAD SF=1
COMB=BR1 SF=1
LOAD=HORLIVE SF=1
LOAD=SOILFULL SF=1
LOAD=VERWATER SF=1
LOAD=HORWATER SF=1
NAME=COMB18 TYPE=ADD
LOAD=SELFWGT SF=1
LOAD=DEAD SF=1
LOAD=HORLIVE SF=1
LOAD=SOILFULL SF=1
LOAD=VERWATER SF=1

## OUTPUT
11. OUTPUT DATA
1) 극한하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | ULTIMATE MAX | 0.19737 | 7.872 | -10.9262 | -3.5641 | 17 | ULTIMATE MIN | 0 | -0.00904 | -2.6943 | 0
| 1 | ULTIMATE MAX | 1 | 7.872 | -13.6163 | 5.1563 | 17 | ULTIMATE MIN | 1 | -0.00904 | -22.3541 | -7.3942
| 1 | ULTIMATE MIN | 0.19737 | -38.1577 | -81.0167 | -24.8968 | 18 | ULTIMATE MAX | 0 | 0 | 22.3562 | 3.9239
| 1 | ULTIMATE MIN | 1 | -38.1577 | -79.9317 | -1.3384 | 18 | ULTIMATE MAX | 1 | 0 | 2.6956 | 0
| 2 | ULTIMATE MAX | 0 | 7.872 | -13.6163 | 5.1563 | 18 | ULTIMATE MIN | 0 | 0 | -16.4655 | -7.3939
| 2 | ULTIMATE MAX | 1 | 7.872 | -15.3362 | 16.8879 | 18 | ULTIMATE MIN | 1 | 0 | -32.4044 | 0
| 2 | ULTIMATE MIN | 0 | -38.1577 | -79.9317 | -1.3384
| 2 | ULTIMATE MIN | 1 | -38.1577 | -81.6516 | 3.0015
| 3 | ULTIMATE MAX | 0 | 7.872 | -1.5986 | 16.8879
| 3 | ULTIMATE MAX | 0.5 | 7.872 | -4.1343 | 22.7158
| 3 | ULTIMATE MAX | 1 | 7.872 | -6.6701 | 28.6264
| 3 | ULTIMATE MIN | 0 | -38.1577 | -28.7974 | 3.0015
| 3 | ULTIMATE MIN | 0.5 | -38.1577 | -26.5032 | 3.8257
| 3 | ULTIMATE MIN | 1 | -38.1577 | -28.9703 | 5.3788
| 4 | ULTIMATE MAX | 0 | 7.872 | 28.9756 | 28.6264
| 4 | ULTIMATE MAX | 0.5 | 7.872 | 26.5063 | 22.7154
| 4 | ULTIMATE MAX | 1 | 7.872 | 28.8006 | 16.8863
| 4 | ULTIMATE MIN | 0 | -38.1577 | 6.6701 | 5.3788
| 4 | ULTIMATE MIN | 0.5 | -38.1577 | 4.1343 | 3.8257
| 4 | ULTIMATE MIN | 1 | -38.1577 | 1.5986 | 3.0015
| 5 | ULTIMATE MAX | 0 | 7.872 | 81.6547 | 16.8863
| 5 | ULTIMATE MAX | 1 | 7.872 | 79.9348 | 5.1552
| 5 | ULTIMATE MIN | 0 | -38.1577 | 15.3362 | 3.0015
| 5 | ULTIMATE MIN | 1 | -38.1577 | 13.6163 | -1.3421
| 6 | ULTIMATE MAX | 0 | 7.872 | 79.9348 | 5.1552
| 6 | ULTIMATE MAX | 0.80263 | 7.872 | 81.0184 | -3.5641
| 6 | ULTIMATE MIN | 0 | -38.1577 | 13.6163 | -1.3421
| 6 | ULTIMATE MIN | 0.80263 | -38.1577 | 10.9262 | -24.8995
| 7 | ULTIMATE MAX | 0.2027 | -22.7115 | 7.872 | -3.2725
| 7 | ULTIMATE MAX | 1 | -20.1096 | 7.872 | -3.0968
| 7 | ULTIMATE MIN | 0.2027 | -160.1635 | -34.8127 | -22.0165
| 7 | ULTIMATE MIN | 1 | -157.5616 | -22.9655 | -19.9257
| 8 | ULTIMATE MAX | 0 | -20.1096 | 7.872 | -3.0968
| 8 | ULTIMATE MAX | 0.5 | -16.758 | 11.0636 | -1.973
| 8 | ULTIMATE MAX | 1 | -13.4064 | 20.0145 | -2.6441
| 8 | ULTIMATE MIN | 0 | -157.5616 | -22.9655 | -19.9257
| 8 | ULTIMATE MIN | 0.5 | -154.21 | -11.6588 | -21.7357
| 8 | ULTIMATE MIN | 1 | -150.8584 | -7.1833 | -25.9232
| 9 | ULTIMATE MAX | 0 | -13.4064 | 20.0145 | -2.6441
| 9 | ULTIMATE MAX | 0.7973 | -10.8045 | 25.3737 | -1.5962
| 9 | ULTIMATE MIN | 0 | -150.8584 | -7.1833 | -25.9232
| 9 | ULTIMATE MIN | 0.7973 | -148.2565 | -5.7819 | -31.0944
| 10 | ULTIMATE MAX | 0.2027 | 5.7819 | -7.1049 | 3.1047
| 10 | ULTIMATE MAX | 1 | 5.7819 | 4.6961 | 25.4485
| 10 | ULTIMATE MIN | 0.2027 | -26.525 | -142.7998 | -26.7679
| 10 | ULTIMATE MIN | 1 | -26.525 | -122.7747 | -6.4909
| 11 | ULTIMATE MAX | 0 | 5.7819 | 4.6961 | 25.4485
| 11 | ULTIMATE MAX | 0.5 | 5.7819 | 33.3545 | 45.9034
| 11 | ULTIMATE MAX | 1 | 5.7819 | 63.6344 | 53.09
| 11 | ULTIMATE MIN | 0 | -26.525 | -122.7747 | -6.4909
| 11 | ULTIMATE MIN | 0.5 | -26.525 | -93.9123 | 2.7378
| 11 | ULTIMATE MIN | 1 | -26.525 | -63.6324 | 3.4085
| 12 | ULTIMATE MAX | 0 | 5.7819 | 63.6344 | 53.09
| 12 | ULTIMATE MAX | 0.5 | 5.7819 | 93.9143 | 45.9028
| 12 | ULTIMATE MAX | 1 | 5.7819 | 122.7768 | 25.4473
| 12 | ULTIMATE MIN | 0 | -26.525 | -63.6324 | 3.4085
| 12 | ULTIMATE MIN | 0.5 | -26.525 | -33.3524 | 2.7378
| 12 | ULTIMATE MIN | 1 | -26.525 | -4.6961 | -6.4925
| 13 | ULTIMATE MAX | 0 | 5.7819 | 122.7768 | 25.4473
| 13 | ULTIMATE MAX | 0.7973 | 5.7819 | 142.8018 | 3.103
| 13 | ULTIMATE MIN | 0 | -26.525 | -4.6961 | -6.4925
| 13 | ULTIMATE MIN | 0.7973 | -26.525 | 7.1049 | -26.7701
| 14 | ULTIMATE MAX | 0.2027 | -10.8045 | 5.7819 | -1.5962
| 14 | ULTIMATE MAX | 1 | -13.4064 | 7.1819 | -2.6441
| 14 | ULTIMATE MIN | 0.2027 | -148.2585 | -25.3738 | -31.0968
| 14 | ULTIMATE MIN | 1 | -150.8604 | -20.0175 | -25.9242
| 15 | ULTIMATE MAX | 0 | -13.4064 | 7.1819 | -2.6441
| 15 | ULTIMATE MAX | 0.5 | -16.758 | 11.6564 | -1.9733
| 15 | ULTIMATE MAX | 1 | -20.1096 | 22.9607 | -3.0968
| 15 | ULTIMATE MIN | 0 | -150.8604 | -20.0175 | -25.9242
| 15 | ULTIMATE MIN | 0.5 | -154.212 | -11.0684 | -21.7358
| 15 | ULTIMATE MIN | 1 | -157.5636 | -7.872 | -19.925
| 16 | ULTIMATE MAX | 0 | -20.1096 | 22.9607 | -3.0968
| 16 | ULTIMATE MAX | 0.7973 | -22.7115 | 34.8079 | -3.2725
| 16 | ULTIMATE MIN | 0 | -157.5636 | -7.872 | -19.925
| 16 | ULTIMATE MIN | 0.7973 | -160.1655 | -7.872 | -22.0136
| 17 | ULTIMATE MAX | 0 | 0 | 32.4054 | 0
| 17 | ULTIMATE MAX | 1 | 0 | 16.4655 | 3.9234
2) 사용하중
F R A M E E L E M E N T F O R C E S
| FRAME | LOAD | DIST | P | V2 | M3 | FRAME | LOAD | DIST | P | V2 | M3
| 1 | SERVICE MAX | 0.19737 | 7.9713 | -9.1052 | -2.97 | 18 | SERVICE MAX | 1 | 0 | 1.2626 | 0
| 1 | SERVICE MAX | 1 | 7.9713 | -11.3469 | 3.2599 | 18 | SERVICE MIN | 0 | 0 | -16.2268 | -6.1296
| 1 | SERVICE MIN | 0.19737 | -23.9727 | -52.9117 | -16.303 | 18 | SERVICE MIN | 1 | 0 | -21.1943 | 0
| 1 | SERVICE MIN | 1 | -23.9727 | -52.794 | -0.7993
| 2 | SERVICE MAX | 0 | 7.9713 | -11.3469 | 3.2599
| 2 | SERVICE MAX | 1 | 7.9713 | -12.7802 | 11.1802
| 2 | SERVICE MIN | 0 | -23.9727 | -52.794 | -0.7993
| 2 | SERVICE MIN | 1 | -23.9727 | -54.2273 | 2.5013
| 3 | SERVICE MAX | 0 | 7.9713 | -1.3321 | 11.1802
| 3 | SERVICE MAX | 0.5 | 7.9713 | -3.4453 | 14.9944
| 3 | SERVICE MAX | 1 | 7.9713 | -5.5584 | 19.0121
| 3 | SERVICE MIN | 0 | -23.9727 | -18.3314 | 2.5013
| 3 | SERVICE MIN | 0.5 | -23.9727 | -17.4258 | 3.188
| 3 | SERVICE MIN | 1 | -23.9727 | -19.496 | 4.4823
| 4 | SERVICE MAX | 0 | 7.9713 | 19.4993 | 19.0121
| 4 | SERVICE MAX | 0.5 | 7.9713 | 17.4278 | 14.9941
| 4 | SERVICE MAX | 1 | 7.9713 | 18.3334 | 11.1793
| 4 | SERVICE MIN | 0 | -23.9727 | 5.5584 | 4.4823
| 4 | SERVICE MIN | 0.5 | -23.9727 | 3.4453 | 3.188
| 4 | SERVICE MIN | 1 | -23.9727 | 1.3321 | 2.5013
| 5 | SERVICE MAX | 0 | 7.9713 | 54.2292 | 11.1793
| 5 | SERVICE MAX | 1 | 7.9713 | 52.796 | 3.2592
| 5 | SERVICE MIN | 0 | -23.9727 | 12.7802 | 2.5013
| 5 | SERVICE MIN | 1 | -23.9727 | 11.3469 | -0.80159
| 6 | SERVICE MAX | 0 | 7.9713 | 52.796 | 3.2592
| 6 | SERVICE MAX | 0.80263 | 7.9713 | 52.9128 | -2.97
| 6 | SERVICE MIN | 0 | -23.9727 | 11.3469 | -0.80159
| 6 | SERVICE MIN | 0.80263 | -23.9727 | 9.1052 | -16.3047
| 7 | SERVICE MAX | 0.2027 | -18.9262 | 7.9713 | -2.7271
| 7 | SERVICE MAX | 1 | -16.758 | 7.9713 | -2.5807
| 7 | SERVICE MIN | 0.2027 | -104.8337 | -21.8821 | -14.4421
| 7 | SERVICE MIN | 1 | -102.6655 | -14.4776 | -13.0987
| 8 | SERVICE MAX | 0 | -16.758 | 7.9713 | -2.5807
| 8 | SERVICE MAX | 0.5 | -13.965 | 7.9713 | -1.8311
| 8 | SERVICE MAX | 1 | -11.172 | 12.385 | -2.2034
| 8 | SERVICE MIN | 0 | -102.6655 | -14.4776 | -13.0987
| 8 | SERVICE MIN | 0.5 | -99.8725 | -7.4108 | -14.1828
| 8 | SERVICE MIN | 1 | -97.0795 | -5.6827 | -16.7529
| 9 | SERVICE MAX | 0 | -11.172 | 12.385 | -2.2034
| 9 | SERVICE MAX | 0.7973 | -9.0038 | 15.7345 | -1.1848
| 9 | SERVICE MIN | 0 | -97.0795 | -5.6827 | -16.7529
| 9 | SERVICE MIN | 0.7973 | -94.9112 | -5.6827 | -19.9482
| 10 | SERVICE MAX | 0.2027 | 5.6827 | -5.5246 | 2.9799
| 10 | SERVICE MAX | 1 | 5.6827 | 5.8427 | 16.0565
| 10 | SERVICE MIN | 0.2027 | -16.454 | -91.2252 | -17.0815
| 10 | SERVICE MIN | 1 | -16.454 | -78.1675 | -3.9057
| 11 | SERVICE MAX | 0 | 5.6827 | 5.8427 | 16.0565
| 11 | SERVICE MAX | 0.5 | 5.6827 | 22.3637 | 29.26
| 11 | SERVICE MAX | 1 | 5.6827 | 39.7715 | 33.8914
| 11 | SERVICE MIN | 0 | -16.454 | -78.1675 | -3.9057
| 11 | SERVICE MIN | 0.5 | -16.454 | -59.4118 | 2.2815
| 11 | SERVICE MIN | 1 | -16.454 | -39.7706 | 2.8404
| 12 | SERVICE MAX | 0 | 5.6827 | 39.7715 | 33.8914
| 12 | SERVICE MAX | 0.5 | 5.6827 | 59.4131 | 29.2596
| 12 | SERVICE MAX | 1 | 5.6827 | 78.1687 | 16.0557
| 12 | SERVICE MIN | 0 | -16.454 | -39.7706 | 2.8404
| 12 | SERVICE MIN | 0.5 | -16.454 | -22.3637 | 2.2815
| 12 | SERVICE MIN | 1 | -16.454 | -5.8427 | -3.9067
| 13 | SERVICE MAX | 0 | 5.6827 | 78.1687 | 16.0557
| 13 | SERVICE MAX | 0.7973 | 5.6827 | 91.2264 | 2.9799
| 13 | SERVICE MIN | 0 | -16.454 | -5.8427 | -3.9067
| 13 | SERVICE MIN | 0.7973 | -16.454 | 5.5246 | -17.0829
| 14 | SERVICE MAX | 0.2027 | -9.0038 | 5.6827 | -1.1848
| 14 | SERVICE MAX | 1 | -11.172 | 5.6827 | -2.2034
| 14 | SERVICE MIN | 0.2027 | -94.9125 | -15.7345 | -19.9497
| 14 | SERVICE MIN | 1 | -97.0808 | -12.3868 | -16.7535
| 15 | SERVICE MAX | 0 | -11.172 | 5.6827 | -2.2034
| 15 | SERVICE MAX | 0.5 | -13.965 | 7.4093 | -1.8313
| 15 | SERVICE MAX | 1 | -16.758 | 14.4746 | -2.5807
| 15 | SERVICE MIN | 0 | -97.0808 | -12.3868 | -16.7535
| 15 | SERVICE MIN | 0.5 | -99.8738 | -7.9713 | -14.1829
| 15 | SERVICE MIN | 1 | -102.6668 | -7.9713 | -13.0983
| 16 | SERVICE MAX | 0 | -16.758 | 14.4746 | -2.5807
| 16 | SERVICE MAX | 0.7973 | -18.9262 | 21.8791 | -2.7271
| 16 | SERVICE MIN | 0 | -102.6668 | -7.9713 | -13.0983
| 16 | SERVICE MIN | 0.7973 | -104.835 | -7.9713 | -14.4403
| 17 | SERVICE MAX | 0 | 0 | 21.1949 | 0
| 17 | SERVICE MAX | 1 | 0 | 16.2268 | 2.2352
| 17 | SERVICE MIN | 0 | -0.00565 | -1.2626 | 0
| 17 | SERVICE MIN | 1 | -0.00565 | -13.6729 | -6.1296
| 18 | SERVICE MAX | 0 | 0 | 13.6742 | 2.2354

## 단면력정리
12. 단면력정리
1) 극한하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
2) 극한하중 검토시 : 최대 전단력도(S.F.D) - Unit : kN
3) 극한하중 검토시 : 최대 축력도(A.F.D) - Unit : kN
4) 사용하중 검토시 : 최대 휨 모멘트도(B.M.D - Unit : kN.m)
5) 단면력 정리
| 구 분 | 위 치 | 극한하중 |  |  | 사용하중 모멘트 | B | H | 비고
|  |  | 모멘트 | 전단력 | 축력
|  |  | kN.m | kN | kN | kN.m | mm | mm
| 상부슬래브 | 단지점부(좌측) | 26.77 | 122.777 | 26.525 | 17.083 | 1000 | 300
|  | 중앙부 | 53.09 | - | 26.525 | 33.891 | 1000 | 300
|  | 단지점부(우측) | 26.768 | 122.775 | 26.525 | 17.082 | 1000 | 300
| 하부슬래브 | 단지점부(좌측) | 24.897 | 79.932 | 38.158 | 16.303 | 1000 | 300
|  | 중앙부 | 28.626 | - | 38.158 | 19.012 | 1000 | 300
|  | 단지점부(우측) | 24.9 | 79.935 | 38.158 | 16.305 | 1000 | 300
| 좌측벽체 | 상부 | 31.097 | 20.017 | 148.259 | 19.95 | 1000 | 300
|  | 중앙부 | 0 | - | 150.86 | 0 | 1000 | 300
|  | 중앙부(부모멘트) | -25.924 | - | 150.86 | -16.753 | 1000 | 300 | 부모멘트
|  | 하부 | 22.014 | 22.961 | 160.166 | 14.44 | 1000 | 300
| 우측벽체 | 상부 | 31.094 | 20.015 | 148.256 | 19.948 | 1000 | 300
|  | 중앙부 | 0 | - | 157.562 | 0 | 1000 | 300
|  | 중앙부(부모멘트) | -25.923 | - | 157.562 | -16.753 | 1000 | 300 | 부모멘트
|  | 하부 | 22.017 | 22.966 | 160.163 | 14.442 | 1000 | 300
| 부상방지턱 | 내측지점부 | 7.394 | 22.356 | 0.009 | 6.13 | 1000 | 300

## 단면검토 및 철근량 산정
13. 단면검토 및 철근량 산정
(1) 주철근 요약
부재,절점 |  |  |  | b |  | d | Mu | ΦMn |  | req'd As | BAR |  | use'd As | S.F
|  |  |  | mm |  | mm | kN.m | kN.m |  | mm² |  |  | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 220 | 26.77 | 54.661 |  | 486.215 | D13 - 8.0EA |  | 1013.6 | 2.042
상부슬래브 : 중앙부 |  |  |  | 1000 |  | 240 | 53.09 | 91.825 |  | 895.566 | D16 - 8.0EA |  | 1588.8 | 1.73
상부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 220 | 26.768 | 54.661 |  | 486.174 | D13 - 8.0EA |  | 1013.6 | 2.042
하부슬래브 : 단지점부(좌측) |  |  |  | 1000 |  | 230 | 24.897 | 57.246 |  | 431.295 | D13 - 8.0EA |  | 1013.6 | 2.299
하부슬래브 : 중앙부 |  |  |  | 1000 |  | 240 | 28.626 | 59.831 |  | 475.675 | D13 - 8.0EA |  | 1013.6 | 2.09
하부슬래브 : 단지점부(우측) |  |  |  | 1000 |  | 230 | 24.9 | 57.246 |  | 431.342 | D13 - 8.0EA |  | 1013.6 | 2.299
좌측벽체 : 상부 |  |  |  | 1000 |  | 220 | 31.097 | 54.661 |  | 566.571 | D13 - 8.0EA |  | 1013.6 | 1.758
좌측벽체 : 중앙부 |  |  |  | 1000 |  | 240 | - | 59.831 |  | - | D13 - 8.0EA |  | 1013.6 | -
좌측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 220 | 25.924 | 54.661 |  | 470.566 | D13 - 8.0EA |  | 1013.6 | 2.109
좌측벽체 : 하부 |  |  |  | 1000 |  | 220 | 22.014 | 54.661 |  | 398.464 | D13 - 8.0EA |  | 1013.6 | 2.483
우측벽체 : 상부 |  |  |  | 1000 |  | 220 | 31.094 | 54.661 |  | 566.527 | D13 - 8.0EA |  | 1013.6 | 1.758
우측벽체 : 중앙부 |  |  |  | 1000 |  | 240 | - | 59.831 |  | - | D13 - 8.0EA |  | 1013.6 | -
우측벽체 : 중앙부(부모멘트) |  |  |  | 1000 |  | 220 | 25.923 | 54.661 |  | 470.547 | D13 - 8.0EA |  | 1013.6 | 2.109
우측벽체 : 하부 |  |  |  | 1000 |  | 220 | 22.017 | 54.661 |  | 398.517 | D13 - 8.0EA |  | 1013.6 | 2.483
부상방지턱 : 내측 지점부 |  |  |  | 1000 |  | 230 | 7.394 | 57.246 |  | 126.66 | D13 - 8.0EA |  | 1013.6 | 7.742
(2) 전단철근 요약
부재,절점 |  |  |  | ΦVc |  | Vu | ΦVn | 다리수 |  | req'd As | BAR | s | use'd As | 비 고
|  |  |  | kN |  | kN | kN | EA |  | mm² |  | mm | mm²
상부슬래브 : 단지점부(좌측) |  |  |  | 126.021 |  | 122.777 | 326.714 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
상부슬래브 : 중앙부 |  |  |  | 137.477 |  | - | 246.946 | 2 |  | - | D13 | 125 | 253.4 | O.K
상부슬래브 : 단지점부(우측) |  |  |  | 126.021 |  | 122.775 | 326.714 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
하부슬래브 : 단지점부(좌측) |  |  |  | 131.749 |  | 79.932 | 341.564 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
하부슬래브 : 중앙부 |  |  |  | 137.477 |  | - | 246.946 | 2 |  | - | D13 | 125 | 253.4 | O.K
하부슬래브 : 단지점부(우측) |  |  |  | 131.749 |  | 79.935 | 341.564 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
좌측벽체 : 상부 |  |  |  | 126.021 |  | 20.017 | 326.714 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
좌측벽체 : 중앙부 |  |  |  | 137.477 |  | - | 246.946 | 2 |  | - | D13 | 125 | 253.4 | O.K
좌측벽체 : 하부 |  |  |  | 126.021 |  | 22.961 | 326.714 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
우측벽체 : 상부 |  |  |  | 126.021 |  | 20.015 | 326.714 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
우측벽체 : 중앙부 |  |  |  | 137.477 |  | - | 246.946 | 2 |  | - | D13 | 125 | 253.4 | O.K
우측벽체 : 하부 |  |  |  | 126.021 |  | 22.966 | 326.714 | 2 |  | - | D13 | 62.5 | 253.4 | O.K
부상방지턱 : 내측 지점부 |  |  |  | 131.749 |  | 22.356 | 236.657 | 4 |  | - | D13 | 250 | 506.8 | O.K
▣ TITLE : 상부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 26.77 |  | 122.777
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 486.215 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 26.770 kN.m) ∴ O.K [안전률 2.042]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
≥ Vu (= 122.777 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 중앙부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 240 |  | 60 |  | 53.09 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1588.800 x 300.00 = 476640.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 26.703 mm, c = 26.703 / β1 = 26.703 / 0.85 = 31.415 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (240.00 - 31.415) / 31.415 = 0.0199
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 895.566 mm²
Use As = 1588.800 mm² (철근도심 : 60.000 mm)
1단 : D16 - 8.0 EA (= 1588.800 mm²) , d1 = 60.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00662
ρmax ≥ ρuse ≥ρmin → 철근비 만족, ∴ O.K
＊ 휨에 대한 검토
ΦMn = 0.85 x 1588.800 x 300 x (240.00 - a/2) = 91.825 kN.m
; a = As x fy / (0.85 x fck x b) = 26.703 mm
≥ Mu (= 53.090 kN.m) ∴ O.K [안전률 1.730]
＊ 전단에 대한 검토 (d = 240.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 240.00 = 137.477 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 상부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 26.768 |  | 122.775
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 486.174 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 26.768 kN.m) ∴ O.K [안전률 2.042]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
≥ Vu (= 122.775 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(좌측)
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 230 |  | 70 |  | 24.897 |  | 79.932
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (230.00 - 20.042) / 20.042 = 0.0314
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 431.295 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00441
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (230.00 - a/2) = 57.246 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 24.897 kN.m) ∴ O.K [안전률 2.299]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 230.00 = 131.749 kN
≥ Vu (= 79.932 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 중앙부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 240 |  | 60 |  | 28.626 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (240.00 - 20.042) / 20.042 = 0.0329
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 475.675 mm²
Use As = 1013.600 mm² (철근도심 : 60.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 60.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00422
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (240.00 - a/2) = 59.831 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 28.626 kN.m) ∴ O.K [안전률 2.090]
＊ 전단에 대한 검토 (d = 240.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 240.00 = 137.477 kN
≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 하부슬래브 : 단지점부(우측)
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 230 |  | 70 |  | 24.9 |  | 79.935
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (230.00 - 20.042) / 20.042 = 0.0314
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 431.342 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00441
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (230.00 - a/2) = 57.246 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 24.900 kN.m) ∴ O.K [안전률 2.299]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 230.00 = 131.749 kN
≥ Vu (= 79.935 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 상부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 31.097 |  | 20.017
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 566.571 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 31.097 kN.m) ∴ O.K [안전률 1.758]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
ΦVc/2 ≥ Vu (= 20.017 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 25.924 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 470.566 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 25.924 kN.m) ∴ O.K [안전률 2.109]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 좌측벽체 : 하부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 22.014 |  | 22.961
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 398.464 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 22.014 kN.m) ∴ O.K [안전률 2.483]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
ΦVc/2 ≥ Vu (= 22.961 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 상부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 31.094 |  | 20.015
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 566.527 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 31.094 kN.m) ∴ O.K [안전률 1.758]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
ΦVc/2 ≥ Vu (= 20.015 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 25.923 |  | 0
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 470.547 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 25.923 kN.m) ∴ O.K [안전률 2.109]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
ΦVc/2 ≥ Vu (= 0.000 kN) , 전단보강 불필요.
▣ TITLE : 우측벽체 : 하부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 220 |  | 80 |  | 22.017 |  | 22.966
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (220.00 - 20.042) / 20.042 = 0.0299
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 398.517 mm²
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00461
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (220.00 - a/2) = 54.661 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 22.017 kN.m) ∴ O.K [안전률 2.483]
＊ 전단에 대한 검토 (d = 220.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 220.00 = 126.021 kN
ΦVc/2 ≥ Vu (= 22.966 kN) , 전단보강 불필요.
▣ TITLE : 부상방지턱 : 내측 지점부
＊ 단면제원 및 설계가정
fck=21MPa, fy=300MPa, k1=0.85, Φf=0.85, Φv=0.75
|  | B (mm) | H (mm) |  | d (mm) |  | 피복 (mm) |  | Mu (kN.m) |  | Vu (kN)
|  | 1000 | 300 |  | 230 |  | 70 |  | 7.394 |  | 22.356
＊ 강도감소계수(Φ) 산정
T = As x fy = 1013.600 x 300.00 = 304080.000
C = 0.85 x fck x a x b = 0.85 x 21.00 x a x 1000.000 = 17850.000 x a
T = C 이므로, a = 17.035 mm, c = 17.035 / β1 = 17.035 / 0.85 = 20.042 mm
εy = fy / Es = 300.00 / 200000.00 = 0.0015
εt = 0.0030 x (dt - c) / c = 0.0030 x (230.00 - 20.042) / 20.042 = 0.0314
εt ≥ 0.0050 이므로 인장지배단면이며, Φ = 0.85 를 적용한다.
＊ 필요철근량 산정
Mu / Φ = As x fy x (d - a/2) ---------------- (1)
a = As x fy / (0.85 x fck x b) ---------------- (2)
式(2)를 式(1)에 대입하여 이차방정식으로 As를 구한다
→ Req As = 126.660 mm²
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
＊ 철근비 검토
ρmin : 1.4 / fy = 0.00467
0.25 √fck / fy = 0.00382 , ρmin = 0.00467 적용
수축온도철근비 = 0.00200
ρmax = 0.64 x ρb = 0.64 x k1 x Φx (fck / fy) x {600 / (600 + fy)} = 0.02168
ρuse = As / bd = 0.00441
ρmax ≥ ρuse, As ≥ As(req) x 4/3 → 철근비 만족, ∴ O.K (콘.설 6.3.2)
＊ 휨에 대한 검토
ΦMn = 0.85 x 1013.600 x 300 x (230.00 - a/2) = 57.246 kN.m
; a = As x fy / (0.85 x fck x b) = 17.035 mm
≥ Mu (= 7.394 kN.m) ∴ O.K [안전률 7.742]
＊ 전단에 대한 검토 (d = 230.00 mm)
ΦVc = 0.75 x 1/6 x √fck x b x d
= 0.75 x 1/6 x √21 x 1000.00 x 230.00 = 131.749 kN
≥ Vu (= 22.356 kN) , 전단보강 불필요.

## 수평철근검토
14. 수평철근 검토
1) 상부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 16EA |  |  |  | = | 2027.2 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 36%
|  |  | = | 486.215 |  | × | 0.36 |  | = | 176.33 |  | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 176.330 ----------> O.K !!!
2) 상부슬래브 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 16EA |  |  |  | = | 2027.2 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 36%
|  |  | = | 895.566 |  | × | 0.36 |  | = | 324.785 |  | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 324.785 ----------> O.K !!!
3) 상부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 16EA |  |  |  | = | 2027.2 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 36%
|  |  | = | 486.174 |  | × | 0.36 |  | = | 176.316 |  | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 176.316 ----------> O.K !!!
4) 하부슬래브 : 단지점부(좌측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 16EA |  |  |  | = | 2027.2 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 431.295 |  | × | 0.2 |  | = | 86.259 |  | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 86.259 ----------> O.K !!!
5) 하부슬래브 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 16EA |  |  |  | = | 2027.2 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 475.675 |  | × | 0.2 |  | = | 95.135 |  | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 95.135 ----------> O.K !!!
6) 하부슬래브 : 단지점부(우측)
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 16EA |  |  |  | = | 2027.2 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 431.342 |  | × | 0.2 |  | = | 86.268 |  | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 86.268 ----------> O.K !!!
7) 좌측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 566.571 |  | × | 0.2 |  | = | 113.314 |  | mm²
|  | ∴ Used As | = | D13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 113.314 ----------> O.K !!!
8) 좌측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
9) 좌측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 470.566 |  | × | 0.2 |  | = | 94.113 |  | mm²
|  | ∴ Used As | = | D13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 94.113 ----------> O.K !!!
10) 좌측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 398.464 |  | × | 0.2 |  | = | 79.693 |  | mm²
|  | ∴ Used As | = | D13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 79.693 ----------> O.K !!!
11) 우측벽체 : 상부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 566.527 |  | × | 0.2 |  | = | 113.305 |  | mm²
|  | ∴ Used As | = | D13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 113.305 ----------> O.K !!!
12) 우측벽체 : 중앙부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
13) 우측벽체 : 중앙부(부모멘트)
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 470.547 |  | × | 0.2 |  | = | 94.109 |  | mm²
|  | ∴ Used As | = | D13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 94.109 ----------> O.K !!!
14) 우측벽체 : 하부
|  | ① Req's As | = | B | × | H |  | × | 0.0025 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.0025 |  | = | 750 | mm²
|  | ∴ Used As | = | D13 - 10EA |  |  |  | = | 1267 |  |  | mm² > 750.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 398.517 |  | × | 0.2 |  | = | 79.703 |  | mm²
|  | ∴ Used As | = | D13 - 5EA |  |  |  | = | 633.5 |  |  | mm² > 79.703 ----------> O.K !!!
15) 부상방지턱
|  | ① Req's As | = | B | × | H |  | × | 0.002 |  | ( ≤ 1800 mm²)
|  |  | = | 1000 |  | × | 300 |  | × | 0.002 |  | = | 600 | mm²
|  | ∴ Used As | = | D13 - 8EA |  |  |  | = | 1013.6 |  |  | mm² > 600.000 ----------> O.K !!!
|  | ② Req's As | = | 필요 철근량 |  |  | × | 20%
|  |  | = | 126.66 |  | × | 0.2 |  | = | 25.332 |  | mm²
|  | ∴ Used As | = | D13 - 4EA |  |  |  | = | 506.8 |  |  | mm² > 25.332 ----------> O.K !!!

## 절점부 검토
15. 절점부 검토
1) 절점 14
[8 empty] | - CON'C 설계기준강도 |  | : fck = 21 MPa
[8 empty] | - 철근 항복강도 |  | : fy = 300 MPa
[8 empty] | - 사용 모멘트 |  | : Mu = 19.950 kN.m
[8 empty] | - 절점부 휨모멘트 |  | : Mo = 19.950 kN.m
R = √(T1² × T2²) = 424.264 mm
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = | 5 × Mo |  | = | 5 × 19.95 × 10^6 | = | 0.554 MPa > 0.08√fck (=0.367)
|  |  | R²×W |  |  | 424.264²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = | 2 × Mo |  | = | 2 × 19.95 × 10^6 | = | 626.959 mm²
|  |  | R × fsa |  |  | 424.264 × 150
|  | Req'd As |  | = | As - Asb
|  |  |  | = | 626.959 mm² - 0.000 mm²
|  |  |  | = | 626.959 mm²
☞ 사용보강철근
|  | Use'd As = |  | D13 @125 - 8EA
∴ Total As = 1013.600 mm² > Req'd As (= 626.959 mm²) -------------> O.K !!!
2) 절점 1
[8 empty] | - CON'C 설계기준강도 |  | : fck = 21 MPa
[8 empty] | - 철근 항복강도 |  | : fy = 300 MPa
[8 empty] | - 사용 모멘트 |  | : Mu = 16.303 kN.m
[8 empty] | - 절점부 휨모멘트 |  | : Mo = 16.303 kN.m
R = √(T1² × T2²) = 424.264 mm
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = | 5 × Mo |  | = | 5 × 16.30 × 10^6 | = | 0.453 MPa > 0.08√fck (=0.367)
|  |  | R²×W |  |  | 424.264²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = | 2 × Mo |  | = | 2 × 16.30 × 10^6 | = | 512.355 mm²
|  |  | R × fsa |  |  | 424.264 × 150
|  | Req'd As |  | = | As - Asb
|  |  |  | = | 512.355 mm² - 0.000 mm²
|  |  |  | = | 512.355 mm²
☞ 사용보강철근
|  | Use'd As = |  | D13 @125 - 8EA
∴ Total As = 1013.600 mm² > Req'd As (= 512.355 mm²) -------------> O.K !!!
3) 절점 10
[8 empty] | - CON'C 설계기준강도 |  | : fck = 21 MPa
[8 empty] | - 철근 항복강도 |  | : fy = 300 MPa
[8 empty] | - 사용 모멘트 |  | : Mu = 19.948 kN.m
[8 empty] | - 절점부 휨모멘트 |  | : Mo = 19.948 kN.m
R = √(T1² × T2²) = 424.264 mm
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = | 5 × Mo |  | = | 5 × 19.95 × 10^6 | = | 0.554 MPa > 0.08√fck (=0.367)
|  |  | R²×W |  |  | 424.264²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = | 2 × Mo |  | = | 2 × 19.95 × 10^6 | = | 626.913 mm²
|  |  | R × fsa |  |  | 424.264 × 150
|  | Req'd As |  | = | As - Asb
|  |  |  | = | 626.913 mm² - 0.000 mm²
|  |  |  | = | 626.913 mm²
☞ 사용보강철근
|  | Use'd As = |  | D13 @125 - 8EA
∴ Total As = 1013.600 mm² > Req'd As (= 626.913 mm²) -------------> O.K !!!
4) 절점 7
[8 empty] | - CON'C 설계기준강도 |  | : fck = 21 MPa
[8 empty] | - 철근 항복강도 |  | : fy = 300 MPa
[8 empty] | - 사용 모멘트 |  | : Mu = 16.305 kN.m
[8 empty] | - 절점부 휨모멘트 |  | : Mo = 16.305 kN.m
R = √(T1² × T2²) = 424.264 mm
① 절점부 보강철근량 필요여부 판정
|  | Ftmax = | 5 × Mo |  | = | 5 × 16.30 × 10^6 | = | 0.453 MPa > 0.08√fck (=0.367)
|  |  | R²×W |  |  | 424.264²× 1000
∴ 절점부 보강철근 필요 !!!
② 소요철근량
외측 인장에 대한 보강철근량(As)
|  | As = | 2 × Mo |  | = | 2 × 16.30 × 10^6 | = | 512.408 mm²
|  |  | R × fsa |  |  | 424.264 × 150
|  | Req'd As |  | = | As - Asb
|  |  |  | = | 512.408 mm² - 0.000 mm²
|  |  |  | = | 512.408 mm²
☞ 사용보강철근
|  | Use'd As = |  | D13 @125 - 8EA
∴ Total As = 1013.600 mm² > Req'd As (= 512.408 mm²) -------------> O.K !!!

## 사용성 검토
16. 사용성 검토
(1) 균열 검토 (콘크리트 구조설계기준ㆍ해설 6.3.3(4))
( C.T.C. 125 mm )
No. | 부재 위치 |  | 유효높이 (mm) |  | 인장사용철근량 |  |  | 검토 환경 | 철근간격 (mm) | 최대간격 (mm) |  | 검토 결과 | 비율 (Sa/S)
1 | 상부슬래브 : 단지점부(좌측) |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 757.365 |  | O.K | 6.059
2 | 상부슬래브 : 중앙부 |  | 240 |  | D16 - 8.0EA |  |  | 습윤 환경 | 125 | 643.42 |  | O.K | 5.147
3 | 상부슬래브 : 단지점부(우측) |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 757.427 |  | O.K | 6.059
4 | 하부슬래브 : 단지점부(좌측) |  | 230 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 831.027 |  | O.K | 6.648
5 | 하부슬래브 : 중앙부 |  | 240 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 744.742 |  | O.K | 5.958
6 | 하부슬래브 : 단지점부(우측) |  | 230 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 830.941 |  | O.K | 6.648
7 | 좌측벽체 : 상부 |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 626.914 |  | O.K | 5.015
8 | 좌측벽체 : 중앙부 |  | 240 |  | D13 - 8.0EA |  |  | 습윤 환경 | - | - |  | -
9 | 좌측벽체 : 중앙부(부모멘트) |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 772.257 |  | O.K | 6.178
10 | 좌측벽체 : 하부 |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 895.968 |  | O.K | 7.168
11 | 우측벽체 : 상부 |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 626.974 |  | O.K | 5.016
12 | 우측벽체 : 중앙부 |  | 240 |  | D13 - 8.0EA |  |  | 습윤 환경 | - | - |  | -
13 | 우측벽체 : 중앙부(부모멘트) |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 772.286 |  | O.K | 6.178
14 | 우측벽체 : 하부 |  | 220 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 895.854 |  | O.K | 7.167
15 | 부상방지턱 : 내측 지점부 |  | 230 |  | D13 - 8.0EA |  |  | 습윤 환경 | 125 | 2210.311 |  | O.K | 17.682
▣ TITLE : 상부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 17.083 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 83.183 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 83.18) - 2.5 x 73.50 = 762.96 mm
300 x (210 / fs) = 300 x (210 / 83.18) = 757.37 mm
Sa는 작은 값인 757.37 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 757.37 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 33.891 x 1000000 / [1588.800 x (240.000 - 66.426/3)]
= 97.914 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1588.800/1000.0 + 8x1588.800/1000.0 x √[(1 + 2x1000.0x240.0/(8x1588.800)]
= 66.426 mm
Use As = 1588.800 mm² (철근도심 : 60.000 mm)
1단 : D16 - 8.0 EA (= 1588.800 mm²) , d1 = 60.00 mm
* 철근의 최대 중심간격
Cc = 60.00 - 16/2 = 52.00 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 97.91) - 2.5 x 52.00 = 674.27 mm
300 x (210 / fs) = 300 x (210 / 97.91) = 643.42 mm
Sa는 작은 값인 643.42 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 643.42 mm) ∴ O.K
▣ TITLE : 상부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 17.082 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 83.176 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 83.18) - 2.5 x 73.50 = 763.03 mm
300 x (210 / fs) = 300 x (210 / 83.18) = 757.43 mm
Sa는 작은 값인 757.43 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 757.43 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(좌측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 16.303 x 1000000 / [1013.600 x (230.000 - 53.501/3)]
= 75.810 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(8x1013.600)]
= 53.501 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 75.81) - 2.5 x 63.50 = 880.03 mm
300 x (210 / fs) = 300 x (210 / 75.81) = 831.03 mm
Sa는 작은 값인 831.03 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 831.03 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 중앙부
* 응력 산정
fs = M / [As x (d - χ/3)] = 19.012 x 1000000 / [1013.600 x (240.000 - 54.804/3)]
= 84.593 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x240.0/(8x1013.600)]
= 54.804 mm
Use As = 1013.600 mm² (철근도심 : 60.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 60.00 mm
* 철근의 최대 중심간격
Cc = 60.00 - 13/2 = 53.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 84.59) - 2.5 x 53.50 = 797.18 mm
300 x (210 / fs) = 300 x (210 / 84.59) = 744.74 mm
Sa는 작은 값인 744.74 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 744.74 mm) ∴ O.K
▣ TITLE : 하부슬래브 : 단지점부(우측)
* 응력 산정
fs = M / [As x (d - χ/3)] = 16.305 x 1000000 / [1013.600 x (230.000 - 53.501/3)]
= 75.818 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(8x1013.600)]
= 53.501 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 75.82) - 2.5 x 63.50 = 879.93 mm
300 x (210 / fs) = 300 x (210 / 75.82) = 830.94 mm
Sa는 작은 값인 830.94 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 830.94 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 19.950 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 97.143 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 97.14) - 2.5 x 73.50 = 626.91 mm
300 x (210 / fs) = 300 x (210 / 97.14) = 648.53 mm
Sa는 작은 값인 626.91 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 626.91 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 16.753 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 81.579 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 81.58) - 2.5 x 73.50 = 781.57 mm
300 x (210 / fs) = 300 x (210 / 81.58) = 772.26 mm
Sa는 작은 값인 772.26 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 772.26 mm) ∴ O.K
▣ TITLE : 좌측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 14.440 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 70.315 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 70.32) - 2.5 x 73.50 = 936.21 mm
300 x (210 / fs) = 300 x (210 / 70.32) = 895.97 mm
Sa는 작은 값인 895.97 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 895.97 mm) ∴ O.K
▣ TITLE : 우측벽체 : 상부
* 응력 산정
fs = M / [As x (d - χ/3)] = 19.948 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 97.135 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 97.14) - 2.5 x 73.50 = 626.97 mm
300 x (210 / fs) = 300 x (210 / 97.14) = 648.58 mm
Sa는 작은 값인 626.97 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 626.97 mm) ∴ O.K
▣ TITLE : 우측벽체 : 중앙부(부모멘트)
* 응력 산정
fs = M / [As x (d - χ/3)] = 16.753 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 81.576 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 81.58) - 2.5 x 73.50 = 781.61 mm
300 x (210 / fs) = 300 x (210 / 81.58) = 772.29 mm
Sa는 작은 값인 772.29 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 772.29 mm) ∴ O.K
▣ TITLE : 우측벽체 : 하부
* 응력 산정
fs = M / [As x (d - χ/3)] = 14.442 x 1000000 / [1013.600 x (220.000 - 52.171/3)]
= 70.324 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x220.0/(8x1013.600)]
= 52.171 mm
Use As = 1013.600 mm² (철근도심 : 80.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 80.00 mm
* 철근의 최대 중심간격
Cc = 80.00 - 13/2 = 73.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 70.32) - 2.5 x 73.50 = 936.07 mm
300 x (210 / fs) = 300 x (210 / 70.32) = 895.85 mm
Sa는 작은 값인 895.85 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 895.85 mm) ∴ O.K
▣ TITLE : 부상방지턱 : 내측 지점부
* 응력 산정
fs = M / [As x (d - χ/3)] = 6.130 x 1000000 / [1013.600 x (230.000 - 53.501/3)]
= 28.503 MPa
χ = -nAs/b + nAs/b√[1 + 2bd/(nAs)]
= -8x1013.600/1000.0 + 8x1013.600/1000.0 x √[(1 + 2x1000.0x230.0/(8x1013.600)]
= 53.501 mm
Use As = 1013.600 mm² (철근도심 : 70.000 mm)
1단 : D13 - 8.0 EA (= 1013.600 mm²) , d1 = 70.00 mm
* 철근의 최대 중심간격
Cc = 70.00 - 13/2 = 63.50 mm
여기서 Cc ; 인장철근이나 긴장재의 표면과 콘크리트 표면사이의 두께(mm)
Smin : 375 x (210 / fs) - 2.5 x Cc = 375 x (210 / 28.50) - 2.5 x 63.50 = 2604.14 mm
300 x (210 / fs) = 300 x (210 / 28.50) = 2210.31 mm
Sa는 작은 값인 2210.31 mm 를 적용
S = 1000.00 / 8.00 Ea = 125.00 ≤ Sa (= 2210.31 mm) ∴ O.K
(2) 처짐검토
▣ 철근콘크리트 부재의 처짐은 시방서에서 규정한 부재의 최소두께를 고려하여
간접적으로 제한한다.
|  | - 경계조건 | : | 1방향 슬래브, 양단연속
|  | - 지 간 | : | L = 2.300 m
- fy = 300 MPa
- 부재두께(T) = 0.30 m
▣ 처짐계산을 하지 않는 경우의 휨 부재의 최소두께 ( fy = 400 MPa 인 경우 )
| 부재 |  | 최소두께 또는 높이 (mm)
|  |  | 단 순 지 지 |  |  | 일 단 연 속 | 양 단 연 속 |  | 캔 틸 레 버
| 1방향 슬래브 |  | l / 20 |  |  | l / 24 | l / 28 |  | l / 10
| 1보 |  | l / 16 |  |  | l / 18.5 | l / 21 |  | l / 8
Tmin = L / 28 × (0.43 + fy / 700)
T = 2.300 / 28 × (0.43 + 300 / 700)
T = 0.071 m < 0.300 m -----------> O.K

## 기초 지지력 검토
17. 기초 지지력 검토
(1) 하중 산정
1) 고정하중
|  |  | - 구체자중 = (58.800 + 13.950) / 2.600 = | [9 empty] | 27.981 | kN/m²
|  |  | - 상부연직하중 |  |  |  | = | 5.73 |  | kN/m² (지하수위 미 고려시)
2) 활하중
|  |  | - 도로 노면 활하중 = 79.541 / 2.600 = | [8 empty] | 30.593 | kN/m²
(2) 허용 지지력 검토
1) 최대 지반 반력
|  |  | Qmax |  | = | 27.981 |  | + | 5.73 |  | + | 30.593
[5 empty] | = | 64.304 |  | kN/m²
2) 지반의 허용연직지지력 : Terzaghi식 사용
|  |  | Qu | = | α c Nc + q Nq + β r1 B' Nr
|  |  |  | Qu | : | 하중의 편심을 고려한 지반의 극한지지력(kN)
|  |  |  | c | : | 지반의 점착력 (kN/m²)
|  |  |  | q | : | 상재하중(kN/m²), q = r2 x Df
|  |  |  | r1,r2 | : | 지지지반 및 근입지반의 단위중량(kN/m³)
다만, 지하수위이하에서는 수중단위중량을 사용한다.
|  |  |  | B | : | 기초의 폭(m) = B'
|  |  |  | Df | : | 기초의 유효근입 깊이(m)
|  |  |  | α,β | : | 기초의 형상계수 (직사각형, α = 1 + 0.3 B'/ L, β = 0.5 - 0.1 B'/ L)
|  |  |  | Nc,Nq,Nr | : | 지지력 계수 (Nc=38.717, Nq=23.799, Nr=20.325)
|  |  |  | c | = | 0.000 kN/m² |  |  |  | r1 | = | 20.000 kN/m³ |  | r2 | = | 20.000 kN/m³
|  |  |  | Df | = | 1.000 m |  |  |  | B | = | 1.000 m |  | q | = | 20.000 kN/m²
|  |  |  | L | = | 2.600 m
|  |  |  | Φ | = | 15 + √12N = 30.492 , N = 20
|  |  |  | Nq | = | a²/ ( 2cos²(45+Φ/2) ) , a = e^[(0.75π-Φ/2) tanΦ]
|  |  |  | Nc | = | (Nq-1) cotΦ
|  |  |  | Nr | = | tanΦ/2 x (Kpr/cos²Φ - 1)
Qu = 1.115 × 0.000 × 38.717 + 20.000 × 23.799 + 0.462 × 20.000 × 2.600 × 20.325
= 963.764 kN/m²
Qa = Qu / 3 = 963.764 / 3 = 321.255 kN/m² > 150.000 kN/m²
Qa' = 150.000 kN/m²> Qmax = 64.304 kN/m²............. O.K !!!

## 주철근 조립도
18. 주철근 조립도